# Draft Report on grid event 220 kV Lower Sileru station Complete outage in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 01-05-2026 19:02

# Event Summary (घटना का सारांश):

The triggering incident was a flashover between the contacts of the R-phase breaker in the bus coupler at the 220 kV Lower Sileru Power House during the opening of the bus coupler. Due to this, the LBB protection operated and a DT signal was sent to the remote ends, tripping the lines connected to Bus 1 and Bus 2 of the Lower Sileru Power House at remote ends. This incident led to a complete outage of the Lower Sileru Power House.

- Time and Date of the Event (घटना का समय और दिनांक:  21-04-2026 22:08

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): TELANGANA , ANDHRA PRADESH

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Telangana State Demand (MW) | 9806 | 9780 |
| Telangana State Generation (MW) | 5472 | 5467 |
| Andhra Pradesh State Demand (MW) | 11356 | 11355 |
| Andhra Pradesh State Generation (MW) | 8074 | 8005 |
| Grid Frequency (Hz) | 50.0 | 50.05 |
| SR Demand (MW) | 60287 | 60253 |
| SR Generation (MW) | 52393 | 52343 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 100.0 MW | 0.0 MW |

- Duration of interruption (रुकावट की अवधि):  1 hours, 4 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण):

| Equipment Type | Equipment make |
| --- | --- |
| CB | ABB , Breaker type: ELF SL4-1 (R-phase limb) |

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 220KV-BOMMUR-LOWER_SILERU-1

      - 220KV-LOWER_SILERU-Chintur-1

      - 220KV-DONKARAYI-LOWER_SILERU-1

      - LOWER_SILERU - 220KV - Bus 1

      - LOWER_SILERU - 220KV - Bus 2

      - 220KV-ASUPAKA-LOWER_SILERU-1

      - 220KV-BOMMUR-LOWER_SILERU-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

220 kV Lower Sileru power house connected to 220 kV Chintoor, Donkarayi, Bommur station and Asupaka station as shown below.

As per the reports submitted, the triggering incident was a flashover between contacts of R phase breaker in Bus Coupler at Lower Sileru power house during opening of the Bus Coupler. Due to the flashover, LBB operated at the Lower Sileru end and opened all breakers on Bus 1 and Bus 2, and DT was sent to the remote ends. As per the SCADA SOE, the lines connected to Bus 1 and Bus 2 tripped at the remote ends; however, the Lower Sileru–Asupaka line did not trip at the Asupaka end. This led to complete outage of 220kV Lower Sileru PH of APGENCO.

- DR Analysis:

220KV-ASUPAKA-LOWER_SILERU-1

|  | ASUPAKA - 220KV | LOWER_SILERU - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR not uploaded.Line is holding. | DR Trigger Time:21-04-2026 22:07:59.622 DT SENT, DT SENT CB OPEN R18 SPARE Ir (max): 0.07 kA Iy (max): 0.16 kA Ib (max): 0.15 kA Vr (max): 130.09 kV Vy (max): 131.07 kV Vb (max): 130.78 kV |

LOWER_SILERU - 220KV

|  | LOWER_SILERU - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:21-04-2026 22:07:59.622 DT SENT, DT SENT CB OPEN R18 SPARE Ir (max): 0.07 kA Iy (max): 0.16 kA Ib (max): 0.15 kA Vr (max): 130.09 kV Vy (max): 131.07 kV Vb (max): 130.78 kV DR Trigger Time:21-04-2026 22:07:59.379 T1 DT Sent CB OPEN T1 R18 SYNCH CLS Ir (max): 0.45 kA Iy (max): 0.45 kA Ib (max): 0.43 kA Vr (max): 133.56 kV Vy (max): 131.47 kV Vb (max): 131.92 kV DR Trigger Time:21-04-2026 22:07:59.567 201_A_BFP_STR 201_RE_TR, 213_RE_TR Bay01 PROT TR 201_BACK_TR, 201B_BACK_TR ZA COMON TRIP, ZA BFP TRIP, ZB COMON TRIP, ZB BFP TRIP Ir (max): 0.46 kA Iy (max): 0.02 kA Ib (max): 0.13 kA DR Trigger Time:21-04-2026 22:07:59.624 SPARE CB OPEN R18 SPARE R18 SPARE Ir (max): 0.11 kA Iy (max): 0.15 kA Ib (max): 0.11 kA Vr (max): 138.09 kV Vy (max): 148.17 kV Vb (max): 138.59 kV DR Trigger Time:21-04-2026 22:07:59.382 Any Start, T1 DT SENT CB OPEN R18 SYNCH OK Ir (max): 0.12 kA Iy (max): 0.23 kA Ib (max): 0.20 kA Vr (max): 135.08 kV Vy (max): 135.66 kV Vb (max): 137.31 kV DR Trigger Time:21-04-2026 22:07:59.611 NTRL DIR OC1 FWD 0SCILL_TRIG On, CB HEALTHY On, MAIN CB OPEN On 0SCILL_TRIG On, CB HEALTHY On, MAIN CB OPEN On Ir (max): 0.12 kA Iy (max): 0.22 kA Ib (max): 0.20 kA Vr (max): 124.51 kV Vy (max): 138.78 kV Vb (max): 144.39 kV DR Trigger Time:21-04-2026 22:07:59.620 HV EF4 STR NS2PTOC STR, T2W BLKH GCB Opened, T2W NS SENS GUPPDUP STR GCB Opened, T2W NS SENS TSAPTOF STR STEFPHIZ STR, Not used OV2PTOV STR GEN SPVC BLKZ, GEN SPVC BLKU Ir (max): 5.76 kA Iy (max): 5.33 kA Ib (max): 5.92 kA Vr (max): 7.20 kV Vy (max): 7.16 kV Vb (max): 7.20 kV DR Trigger Time:21-04-2026 22:07:59.567 201_A_BFP_STR 201_RE_TR, 213_RE_TR Bay01 PROT TR 201_BACK_TR, 201B_BACK_TR ZA COMON TRIP, ZA BFP TRIP, ZB COMON TRIP, ZB BFP TRIP Ir (max): 0.46 kA Iy (max): 0.02 kA Ib (max): 0.13 kA |

- A) PMU Analysis:

From the PMU plot , fault was not observed during the event.

B) SCADA Analysis:

From the SCADA data tripping of the lines connectec to 220kV Lower Sileru PH can be observed.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| TGTRANSCO | 1. The non opening of breaker of Asupaka-Lower Sileru line at Asupaka end needs review. |
| APGENCO | 1.Non opening of Bus coupler breaker needs review. |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| APGENCO | Faulty R-phase breaker limb removed from the structure and awaiting for Bus LC for Limb replacement. |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

21/04/2026 23:12

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) |  |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 |  |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: