# Draft Report on grid event Complete Outage of 230kV JSW_Vilanthikulam of JSW_RE in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 19-05-2026 19:14

# Event Summary (घटना का सारांश):

# 230 kV JSW_Vilanthikulam generating station(wind) radially connected 230 kV TTGS station through 230KV-TTGS-JSW_Vilathikulam-1 line. Further all elements were connected to 230kV Bus-2 at JSW_Vilathikulam. The triggering incident was R-Y-B fault due to failure of 33kV bus supporting insulators in the Y and B phases near LV side of PTR. During which the ICT protection operated but the breaker failed to open leading to LBB operation and tripping all the elements connected to Bus-2 including 230KV-TTGS-JSW_Vilathikulam-1 line and DT was sent to remote end. Due to the tripping of the only connected line to JSW_Vilathikulam led to the complete outage of 230kV JSW_Vilanthikulam

- Time and Date of the Event (घटना का समय और दिनांक:  11-05-2026 09:00

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): TAMILNADU

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| TamilNadu State Demand (MW) | 15630 | 15766 |
| TamilNadu State Generation (MW) | 8254 | 8327 |
| Grid Frequency (Hz) | 49.97 | 50.02 |
| SR Demand (MW) | 56577 | 56610 |
| SR Generation (MW) | 47953 | 48077 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Cloudy |

All the elements were connected to Bus-2 at JSW_Vilanthikulam

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) |  | Load Loss (MW) |
| --- | --- | --- |
| Solar | 0.0 MW | 0.0 MW |
| Wind | 0.0 MW |  |
| Others | 0.0 MW |  |
| Total | 0.0 MW |  |

- Duration of interruption (रुकावट की अवधि):  1 hours, 41 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 230KV-TTGS-JSW_Vilathikulam-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

230 kV JSW_Vilanthikulam generating station(wind) radially connected 230 kV TTGS station through 230KV-TTGS-JSW_Vilathikulam-1 line. Further all elements were connected to 230kV Bus-2 at JSW_Vilathikulam.

The triggering incident was R-Y-B fault due to failure of 33kV bus supporting insulators in the Y and B phases at the LV side of the transformer. During which the LV side ICT REF protection operated (as per the SCADA EL) but the breaker failed (as the fault current can be seen in the DR) to open leading to LBB operation and tripping all the elements connected to Bus-2 including 230KV-TTGS-JSW_Vilathikulam-1 line and DT was sent to remote end. At TTGS end, the line tripped due to DT receipt.

Due to the tripping of the only connected line to JSW_Vilathikulam led to the complete outage of 230kV JSW_Vilanthikulam. There was no generation during the event and hence there was no generation loss.

- DR Analysis:

230KV-TTGS-JSW_Vilathikulam-1

|  | TTGS - 230KV | JSW_Vilathikulam - 230KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:11-05-2026 09:00:37.114 MAIN1 Z3 START MAIN1 TRIP, DT REC CH1/2 3PH GR A/B OPTD MAIN CB Y OPEN MAIN CB B OPEN MAIN CB R OPEN MAIN CB AR LO Ir (max): 2.33 kA Iy (max): 2.60 kA Ib (max): 2.37 kA Vr (max): 181.24 kV Vy (max): 135.70 kV Vb (max): 134.59 kV DR Trigger Time:11-05-2026 09:00:37.373 MAIN2 Z3 START MAIN1 TRIP, DT REC CH1/2 3PH GR A/B OPTD MAIN CB Y OPEN MAIN CB R OPEN, MAIN CB B OPEN, MAIN CB AR LO Ir (max): 2.37 kA Iy (max): 2.64 kA Ib (max): 2.40 kA Vr (max): 181.51 kV Vy (max): 137.18 kV Vb (max): 136.03 kV | DR Trigger Time:11-05-2026 09:00:37.113 PHE_ZONE_MEAS_EN, DIST_START_BPH, DIST_START_PHE, E/F[67N]_STRV PP_ZONE_MEAS_EN, DIST_START_YPH UV_VOLGE_ST_SOTF DT SEND CH-I M/TBC_LBB_OPTD MAIN 3P TRIP FROM_REM_LINE_DT E/F[67N]_STRV MAIN_CB_B_OPEN MAIN_CB_R_OPEN MAIN_CB_Y_OPEN MAIN_CB_OPEN Ir (max): 2.35 kA Iy (max): 2.61 kA Ib (max): 2.38 kA Vr (max): 177.30 kV Vy (max): 139.56 kV Vb (max): 134.65 kV DR Trigger Time:11-05-2026 09:00:37.131 V<1 Start DT SEND CH-2 PR3P TRIP MAIN CB OP BPH MAIN CB OP YPH Any Pole Dead All Poles Dead TOR Active Ir (max): 2.38 kA Iy (max): 2.66 kA Ib (max): 2.42 kA Vr (max): 177.14 kV Vy (max): 139.32 kV Vb (max): 136.14 kV |

JSW_Vilathikulam - 230KV

|  | JSW_Vilathikulam - 230KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:11-05-2026 09:00:37.113 PHE_ZONE_MEAS_EN, DIST_START_BPH, DIST_START_PHE, E/F[67N]_STRV PP_ZONE_MEAS_EN, DIST_START_YPH UV_VOLGE_ST_SOTF DT SEND CH-I M/TBC_LBB_OPTD MAIN 3P TRIP FROM_REM_LINE_DT E/F[67N]_STRV MAIN_CB_B_OPEN MAIN_CB_R_OPEN MAIN_CB_Y_OPEN MAIN_CB_OPEN Ir (max): 2.35 kA Iy (max): 2.61 kA Ib (max): 2.38 kA Vr (max): 177.30 kV Vy (max): 139.56 kV Vb (max): 134.65 kV DR Trigger Time:11-05-2026 09:00:37.131 V<1 Start DT SEND CH-2 PR3P TRIP MAIN CB OP BPH MAIN CB OP YPH Any Pole Dead All Poles Dead TOR Active Ir (max): 2.38 kA Iy (max): 2.66 kA Ib (max): 2.42 kA Vr (max): 177.14 kV Vy (max): 139.32 kV Vb (max): 136.14 kV |

- A) PMU Analysis:

From the PMU, 3ph fault can be observed with a delayed fault clearance

B) SCADA Analysis:

From the SCADA data, complete station outage can be observed with no generation loss during the event

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| JSW_RE | 1. Single bus operation (All elements connected to Bus-2) at JSW_Vilathikulam needs review 2. Non opening of Breaker for PTR for LV side fault needs review 3. Non availability of DR of PTR where in REF operated needs review |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| JSW_RE | The fault zone was isolated from the circuit at the 230/33kV power transformer from the pooling substation end. |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | JSW_RE |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | PGCIL SR-2, JSW_RE |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: