# Draft Report on grid event Complete Outage of 220kV Renew_Surya_Ojas_Koppal_W of Renew in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 22-05-2026 20:00

# Event Summary (घटना का सारांश):

# As per the reports submitted, the triggering incident was R-G fault in 220KV-Renew_Surya_Ojas_Koppal_W-KOPPAL-1 line and the line tripped. Tripping of the only connected line led to complete outage of 220kV Renew_Surya_Ojas_Koppal_W of Renew

- Time and Date of the Event (घटना का समय और दिनांक:  15-05-2026 05:20

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): KARNATAKA

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Karnataka State Demand (MW) | 11713 | 11673 |
| Karnataka State Generation (MW) | 6227 | 6214 |
| Grid Frequency (Hz) | 50.0 | 49.98 |
| SR Demand (MW) | 50783 | 50785 |
| SR Generation (MW) | 45290 | 45283 |

*Pre and post data of 1 minute before and after the event

| Elements under outage | - 220KV-Renew_Surya_Ojas_Koppal_W-KOPPAL-1 |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Cloudy |

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 33.0 MW | 0.0 MW |

- Duration of interruption (रुकावट की अवधि):  1 hours, 25 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 220KV-Renew_Surya_Ojas_Koppal_W-KOPPAL-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

As per the reports submitted, the triggering incident was R-G fault in 220KV-Renew_Surya_Ojas_Koppal_W-KOPPAL-1 line. At RSOPL end, the fault was sensed in Line differntial protection and the line tripped. At Koppal end, FIR, DR and EL are not uploaded. However, from the DR at RSOPL end and PMU plots, it is suspected that A/R operated at Koppal end and was succesful. Tripping of the only connected line led to complete outage of 220kV Renew_Surya_Ojas_Koppal_W of Renew.

- DR Analysis:

220KV-Renew_Surya_Ojas_Koppal_W-KOPPAL-1

|  | Renew_Surya_Ojas_Koppal_W - 220KV | KOPPAL - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:15-05-2026 05:20:56.400 CB TC-1 TRIP RPH, Trip Output A, Diff Trip CB OPN BPH Trip Output B, Trip Output C CB OPN RPH, CB OPN YPH Ir (max): 1.16 kA Iy (max): 0.32 kA Ib (max): 0.52 kA Vr (max): 132.21 kV Vy (max): 144.04 kV Vb (max): 147.76 kV | DR is not uploaded |

Renew_Surya_Ojas_Koppal_W - 220KV

|  | Renew_Surya_Ojas_Koppal_W - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | Loss of power supply |

- A) PMU Analysis:

From PMU, dip in R-phase is observed indicating R-G fault during the event with A/R succesful.

B) SCADA Analysis:

From SCADA plot, tripping of 220kV RSOPL Koppal line can be observed with a generation loss of around 33MW.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| INDIGRID | 1. Non furnishing of FIR, DR and EL at Koppal end |
| RENEW POWER PVT LTD | 1. Non operation of A/R at RSOPL end |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| RENEW POWER PVT LTD | we carried out line inspection but no any observation found. |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

Renew_Surya_Ojas_Koppal_W - 220KV tripped at 15-05-2026 05:20 and restored at 15-05-2026 06:45

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | RENEW POWER PVT LTD |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | INDIGRID, RENEW POWER PVT LTD |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: