# Draft Report on grid event Complete Outage of 220kV Green Infra_GadagPS of GIREL in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 04-05-2026 13:54

# Event Summary (घटना का सारांश):

# The 220 kV Green Infra–Gadag PS station is radially connected to the 220 kV Gadag PSS station. The triggering incident was an R–G fault on the line during inclement weather conditions. The line tripped at both ends, resulting in a complete outage of the Green Infra–Gadag PS station.

- Time and Date of the Event (घटना का समय और दिनांक:  29-04-2026 04:40

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): KARNATAKA

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Karnataka State Demand (MW) | 11667 | 11592 |
| Karnataka State Generation (MW) | 6365 | 6368 |
| Grid Frequency (Hz) | 49.98 | 49.99 |
| SR Demand (MW) | 54744 | 54690 |
| SR Generation (MW) | 44531 | 44420 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Thunders , Windy |

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 40.0 MW | 0.0 MW |

- Duration of interruption (रुकावट की अवधि):  4 hours, 25 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 220KV-GADAG_PSS-Green Infra_GadagPS-1

      - Green Infra_GadagPS - 220KV

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

220kV Green Infra_GadagPS station is radially connected to the 220 kV Gadag PSS station through 220KV-GADAG_PSS-Green Infra_GadagPS-1. As per the reports submitted, the triggering incident was an R–G fault on the 220 kV Gadag PSS–Green Infra PS-1 line during inclement weather conditions. At the Green Infra end, the fault was sensed in Z1, Auto-reclosure (A/R) did not operate, resulting in three-phase tripping. At the Gadag end, the fault was sensed in Zone-1; however, A/R did not operate, and three-phase tripping was observed. Due to the tripping of the only connected line led to the complete outage of 220 kV Green Infra_Gadag PS station and led to a generation loss of around 40MW.

- DR Analysis:

220KV-GADAG_PSS-Green Infra_GadagPS-1

|  | GADAG_PSS - 220KV | Green Infra_GadagPS - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:29-04-2026 04:40:40.781 MAIN1_Z1_OPTD MAIN1_TRIP, M1/2_CARR_SEND MAIN2_TRIP MAIN_CB_R_OPEN MAIN1/2_CARR_REC MAIN_CB_Y_OPEN MAIN_CB_B_OPEN Ir (max): 4.29 kA Iy (max): 0.45 kA Ib (max): 0.32 kA Vr (max): 130.43 kV Vy (max): 130.85 kV Vb (max): 130.18 kV DR Trigger Time:29-04-2026 04:40:40.781 MAIN1_Z1_OPTD MAIN1_TRIP, M1/2_CARR_SEND MAIN2_TRIP MAIN_CB_R_OPEN MAIN1/2_CARR_REC MAIN_CB_Y_OPEN MAIN_CB_B_OPEN Ir (max): 4.29 kA Iy (max): 0.45 kA Ib (max): 0.32 kA Vr (max): 130.43 kV Vy (max): 130.85 kV Vb (max): 130.18 kV | DR Trigger Time:29-04-2026 04:40:40.801 M1 PRTN OPT PMUN, R-PH TRIP, GENERAL TRIP, Diff Trip, Diff Trip A CARRIER REC CH-1 Aid 1 Dist Trip 3PH PRTN OPT 86A, 3PH PRTN OPT 86B CB OPEN B-PH CB OPEN R-PH CB OPEN Y-PH Ir (max): 0.76 kA Iy (max): 0.47 kA Ib (max): 0.33 kA Vr (max): 131.11 kV Vy (max): 141.63 kV Vb (max): 137.99 kV |

Green Infra_GadagPS - 220KV

|  | Green Infra_GadagPS - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:29-04-2026 04:40:40.801 M1 PRTN OPT PMUN, R-PH TRIP, GENERAL TRIP, Diff Trip, Diff Trip A CARRIER REC CH-1 Aid 1 Dist Trip 3PH PRTN OPT 86A, 3PH PRTN OPT 86B CB OPEN B-PH CB OPEN R-PH CB OPEN Y-PH Ir (max): 0.76 kA Iy (max): 0.47 kA Ib (max): 0.33 kA Vr (max): 131.11 kV Vy (max): 141.63 kV Vb (max): 137.99 kV DR Trigger Time:29-04-2026 05:40:40.781 21_STFWL1, 21_STFWPE, FAULT_LOOP_R 21_STZ3, 67N_START 21_STZ2 MAIN_TRIP, TRIP_L1, TRIP_L2, TRIP_L3, 21_TRZ1, 21_STZ1, ZCOM_CS, START_AR BLOCK_AR 86_OPTD BRC_START Ir (max): 0.76 kA Iy (max): 0.47 kA Ib (max): 0.33 kA Vr (max): 129.75 kV Vy (max): 140.20 kV Vb (max): 136.87 kV |

- A) PMU Analysis:

From the PMU plot, R-G fault can be observed without any delayed clearance.

B) SCADA Analysis:

From the SCADA data tripping in the line can be observed.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| GREENINFRA | 1. Non operation of A/R needs review. 2. Non availability of SCADA SOE at Green Infra_GadagPS needs review |
| GTL | 1. Non operation of A/R needs review. |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| GREENINFRA | Inspected the Fault Location approximately veried around 20 Towers, but there is no observations found. But During Trip event weather condition was Thunders & Rain along with Lightnings at Kushtagi area. |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

29/04/2026 09:05

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | GREENINFRA |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | GREENINFRA |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: