# Draft Report on grid event Complete outage of 400kV UDANGUDI of TNPGCL in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 12-05-2026 15:55

# Event Summary (घटना का सारांश):

# 400kV UDANGUDI SS is radially connected to 400kV OTTAPIDARAM through 400kV-OTTAPIDARAM-UDANGUDI-1&2 lines. Both the 400kV-OTTAPIDARAM-UDANGUDI-1&2 lines are in the same dia at 400kV Udangudi SS The triggering incident is the B-G fault in 400kV-OTTAPIDARAM-UDANGUDI-1, where in B pole opened. However due to logic issue implemented in the Tie Breaker led to Tie LBB operation and tripped the other main and led to the tripping of 400kV-OTTAPIDARAM-UDANGUDI-2 and DT was sent to remote. With the tripping of both the 400kV-OTTAPIDARAM-UDANGUDI-1&2 led to the Complete outage of 400kV UDANGUDI of TNPGCL.

- Time and Date of the Event (घटना का समय और दिनांक:  29-04-2026 12:57

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): TAMILNADU

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| TamilNadu State Demand (MW) | 18995 | 18910 |
| TamilNadu State Generation (MW) | 10055 | 10000 |
| Grid Frequency (Hz) | 49.95 | 49.97 |
| SR Demand (MW) | 66774 | 66512 |
| SR Generation (MW) | 55886 | 55619 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Windy |

At 400kV Udangudi SS:

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 0.0 MW | 26.0 MW |

- Duration of interruption (रुकावट की अवधि):  2 hours, 28 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 400KV-OTTAPIDARAM-UDANGUDI-1

      - 400KV-OTTAPIDARAM-UDANGUDI-2

      - 400KV/11KV UDANGUDI-ST-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

400kV UDANGUDI SS is radially connected to 400kV OTTAPIDARAM through 400kV-OTTAPIDARAM-UDANGUDI-1&2 lines. Both the 400kV-OTTAPIDARAM-UDANGUDI-1&2 lines are in the same dia at 400kV Udangudi SS The triggering incident is the B-G fault in 400kV-OTTAPIDARAM-UDANGUDI-1, where in at both ends, the fault was sensed in zone-1 and B pole opened. However due to logic issue implemented in the Tie Breaker led to Tie LBB operation and tripped the other main and led to the tripping of 400kV-OTTAPIDARAM-UDANGUDI-2 and DT was sent to remote. With the tripping of both the 400kV-OTTAPIDARAM-UDANGUDI-1&2 led to the Complete outage of 400kV UDANGUDI of TNPGCL.

- DR Analysis:

400KV-OTTAPIDARAM-UDANGUDI-1

|  | OTTAPIDARAM - 400KV | UDANGUDI - 400KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:29-04-2026 12:57:09.473 3PH_F UN_PU PU_ZIIG, PU_ZIIIG IN_RECEIPT_D TRIP, TRIP1, TRIP2, TX_D, TRIP_SCHM_D GEN Bph TRIP, DA3 LBB B TCB PU_ZIG, TRIP_Z1G DIA3 MCB B OP DIA6 TCB B OP DIC1 DT RCV 1, DIC1 DT RCV 1 BLK_CMD1 DIA2 MCB Y OP, DIA4 TCB R OP, DIA5 TCB Y OP DIA1 MCB R OP Ir (max): 0.14 kA Iy (max): 0.42 kA Ib (max): 3.52 kA Vr (max): 258.75 kV Vy (max): 254.10 kV Vb (max): 233.99 kV DR Trigger Time:29-04-2026 12:57:09.483 ANY START, ZONE-2/3/4 START ANY START, ZONE-2/3/4 START DI08 CR REC CH1, DI07 CR REC CH2 ANY START, DI13 21M1X B OP AR Start, ARIP, AR Blocked DI03 MCB B OPEN DI06 TCB B OPEN DI22 DT RECV CH2, DI22 DT RECV CH2 AR Start, CB1 AR Lockout DI01 MCB R OPEN, DI02 MCB Y OPEN, DI05 TCB Y OPEN DI04 TCB R OPEN Ir (max): 0.16 kA Iy (max): 0.44 kA Ib (max): 3.57 kA Vr (max): 259.09 kV Vy (max): 255.12 kV Vb (max): 236.55 kV | DR Trigger Time:29-04-2026 12:57:09.480 IN>1 Start Z1, Z2, Z3 A/R 1P In Prog L12.EXT BPH TRIP DIST. Chan Recv BAR V>1 Start Ir (max): 0.22 kA Iy (max): 0.54 kA Ib (max): 3.42 kA Vr (max): 284.39 kV Vy (max): 283.37 kV Vb (max): 237.26 kV |

400KV-OTTAPIDARAM-UDANGUDI-2

|  | OTTAPIDARAM - 400KV | UDANGUDI - 400KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:29-04-2026 12:57:09.482 ANY START, ZONE-2/3/4 START Power Swing DI06 TCB B OPEN DI22 DT RECV CH2 AR Start, AR Blocked, CB1 AR Lockout DI03 MCB B OPEN DI05 TCB Y OPEN DI04 TCB R OPEN DI01 MCB R OPEN DI02 MCB Y OPEN Ir (max): 0.27 kA Iy (max): 0.60 kA Ib (max): 6.03 kA Vr (max): 288.65 kV Vy (max): 246.67 kV Vb (max): 253.14 kV | DR Trigger Time:29-04-2026 12:57:09.483 IN>1 Start Z4 BAR V>1 Start Ir (max): 0.20 kA Iy (max): 0.34 kA Ib (max): 3.18 kA Vr (max): 303.01 kV Vy (max): 281.94 kV Vb (max): 267.79 kV |

UDANGUDI - 400KV

|  | UDANGUDI - 400KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:29-04-2026 12:57:09.480 IN>1 Start Z1, Z2, Z3 A/R 1P In Prog L12.EXT BPH TRIP DIST. Chan Recv BAR V>1 Start Ir (max): 0.22 kA Iy (max): 0.54 kA Ib (max): 3.42 kA Vr (max): 284.39 kV Vy (max): 283.37 kV Vb (max): 237.26 kV |

- A) PMU Analysis:

From PMU, dip in B-phase voltage is observed indicating B-G fault during the event with no delayed fault clearance.

B) SCADA Analysis:

From SCADA, tripping of 400kV Udangudi Bus-1 and Bus-2 can be observed.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| TNPGCL | 1. Tie CB LBB maloperation at Udangudi end |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| TNPGCL | Ottapidaram Line-1 Normailsed on 29.04.2026 at 17:07 hrs Ottapidaram Line-2 Normailsed on 29.04.2026 at 17:17 hrs and the Power restored back in the 400kV GIS. |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

Ottapidaram Line-1 Normailsed on 29.04.2026 at 17:07 hrs

Ottapidaram Line-2 Normailsed on 29.04.2026 at 17:17 hrs and the Power restored back in the 400kV GIS.

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | TNPGCL |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | TNPGCL |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: