# Draft Report on grid event Complete outage of 400kV UDANGUDI of TNPGCL in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 12-05-2026 15:56

# Event Summary (घटना का सारांश):

# 400kV UDANGUDI is radially connected to 400kV OTTAPIDARAM through 400kV-OTTAPIDARAM-UDANGUDI-1&2 lines. Both the 400kV-OTTAPIDARAM-UDANGUDI-1&2 lines are in the same dia at 400kV OTTAPIDARAM. The triggering incident is the B-G fault in 400kV-OTTAPIDARAM-UDANGUDI-1, where in B pole opened. However due to logic issue implemented in the Tie Breaker led to Tie LBB operation and tripped the other main and led to the tripping of 400kV-OTTAPIDARAM-UDANGUDI-2 and DT was sent to remote. With the tripping of both the 400kV-OTTAPIDARAM-UDANGUDI-1&2 led to the Complete outage of 400kV UDANGUDI of TNPGCL during which led to the tripping of running unit of Unit-1 UDANGUDI and led to a generation loss of 156MW.

- Time and Date of the Event (घटना का समय और दिनांक:  30-04-2026 14:24

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): TAMILNADU

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| TamilNadu State Demand (MW) | 19701 | 19863 |
| TamilNadu State Generation (MW) | 10340 | 10322 |
| Grid Frequency (Hz) | 49.97 | 49.97 |
| SR Demand (MW) | 67889 | 68170 |
| SR Generation (MW) | 55273 | 55384 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 156.0 MW | 63.0 MW |

- Duration of interruption (रुकावट की अवधि):  1 hours, 35 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 400KV-OTTAPIDARAM-UDANGUDI-2

      - 400KV/11KV UDANGUDI-ST-1

      - 400KV/21KV UDANGUDI-GT-1

      - UDANGUDI - UNIT 1

      - 400KV-OTTAPIDARAM-UDANGUDI-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

400kV UDANGUDI SS is radially connected to 400kV OTTAPIDARAM through 400kV-OTTAPIDARAM-UDANGUDI-1&2 lines. Both the 400kV-OTTAPIDARAM-UDANGUDI-1&2 lines are in the same dia at 400kV Udangudi SS The triggering incident is the B-G fault in 400kV-OTTAPIDARAM-UDANGUDI-1, where in at both ends, the fault was sensed in zone-1 and B pole opened. However due to logic issue implemented in the Tie Breaker led to Tie LBB operation and tripped the other main and led to the tripping of 400kV-OTTAPIDARAM-UDANGUDI-2 and DT was sent to remote. With the tripping of both the 400kV-OTTAPIDARAM-UDANGUDI-1&2 led to the Complete outage of 400kV UDANGUDI of TNPGCL.

- DR Analysis:

400KV-OTTAPIDARAM-UDANGUDI-2

|  | OTTAPIDARAM - 400KV | UDANGUDI - 400KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:30-04-2026 14:23:17.209 ANY START ZONE-2/3/4 START ANY START, ZONE-2/3/4 START DI06 TCB B OPEN DI22 DT RECV CH2 AR Start, AR Blocked, CB1 AR Lockout DI03 MCB B OPEN DI04 TCB R OPEN, DI05 TCB Y OPEN DI01 MCB R OPEN DI02 MCB Y OPEN Ir (max): 0.97 kA Iy (max): 0.88 kA Ib (max): 6.30 kA Vr (max): 286.38 kV Vy (max): 249.94 kV Vb (max): 248.78 kV | DR Trigger Time:30-04-2026 14:23:17.198 IN>1 Start Z4 Z4 Z4 Z4 IN>1 Start BAR V>1 Start Ir (max): 0.85 kA Iy (max): 0.80 kA Ib (max): 3.08 kA Vr (max): 302.05 kV Vy (max): 263.58 kV Vb (max): 262.27 kV |

UDANGUDI - 400KV

|  | UDANGUDI - 400KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:30-04-2026 14:23:17.191 IN>1 Start Z1, Z2, Z3 A/R 1P In Prog L12.EXT BPH TRIP DIST. Chan Recv BAR Ir (max): 0.83 kA Iy (max): 0.81 kA Ib (max): 6.93 kA Vr (max): 258.96 kV Vy (max): 258.88 kV Vb (max): 239.62 kV |

400KV-OTTAPIDARAM-UDANGUDI-1

|  | OTTAPIDARAM - 400KV | UDANGUDI - 400KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:30-04-2026 14:23:17.185 ANY START, ZONE-2/3/4 START DI08 CR REC CH1, DI07 CR REC CH2 Any Trip, CB1 Trip OutputC, CB2 Trip OutputC, Aid 1 Dist Trip AR Start, ARIP, AR Blocked DI13 21M1X B OP DI03 MCB B OPEN ZONE1 START, Zone 1 Trip, Aided 1 Send DI06 TCB B OPEN DI22 DT RECV CH2, DI22 DT RECV CH2 AR Start, CB1 AR Lockout DI01 MCB R OPEN, DI02 MCB Y OPEN, DI04 TCB R OPEN, DI05 TCB Y OPEN Ir (max): 0.64 kA Iy (max): 0.72 kA Ib (max): 3.94 kA Vr (max): 239.11 kV Vy (max): 244.67 kV Vb (max): 236.89 kV | DR Trigger Time:30-04-2026 14:23:17.191 IN>1 Start Z1, Z2, Z3 A/R 1P In Prog L12.EXT BPH TRIP DIST. Chan Recv BAR Ir (max): 0.83 kA Iy (max): 0.81 kA Ib (max): 6.93 kA Vr (max): 258.96 kV Vy (max): 258.88 kV Vb (max): 239.62 kV |

- A) PMU Analysis:

From PMU, dip in B-phase voltage is observed indicating B-G fault during the event.

B) SCADA Analysis:

From SCADA, loss of power supply to 220kv Bus-1 and Bus-2 is observed.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| TNPGCL | 1. Tie CB LBB maloperation at Udangudi end |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| TNPGCL | Configuration and Settings was verified and corrections were made in the LBB protection scheme and ensured it by testing the relay. LC applied and Ottapidaram Line-2 Tripped on 01.05.2026 at 11.06 hrs for Line Pattrolling and tree cutting was made, the line charged back on 01.05.2026 at 17.17 hrs Both the lines found to be normal. |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

Complete outage of 400kV UDANGUDI of TNPGCL @ 29-04-2026 12:57 and restored at 29-04-2026 15:25

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | TNPGCL |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | TANTRANSCO, TNPGCL |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: