# Draft Report on grid event Complete Outage of 230kV JSW_Vilanthikulam of JSW_RE in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 05-05-2026 17:26

# Event Summary (घटना का सारांश):

# 230 kV JSW_Vilanthikulam generating station(wind) radially connected 230 kV TTGS station through 230KV-TTGS-JSW_Vilathikulam_300MW-1 line. The triggering incident was R-G fault due to inclement weather. Although A/R operated at both ends but at TTGS end 3 phase tripping was observed without any fault and line is holding from JSW_Vilathikulam end. As the line is a radial feeder , the tripping of the line at TTGS station led to complete outage of 230kV JSW_Vilanthikulam station.

- Time and Date of the Event (घटना का समय और दिनांक:  02-05-2026 18:39

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): TAMILNADU

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| TamilNadu State Demand (MW) | 17989 | 17959 |
| TamilNadu State Generation (MW) | 6122 | 6069 |
| Grid Frequency (Hz) | 49.97 | 49.97 |
| SR Demand (MW) | 54029 | 54401 |
| SR Generation (MW) | 45548 | 45745 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Thunders |

JSW_Vilanthikulam station :

Bus Configuration Type : Double Bus with Bus coupler

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) |  | Load Loss (MW) |
| --- | --- | --- |
| Solar | 0.0 MW | 0.0 MW |
| Wind | 143.0 MW |  |
| Others | 0.0 MW |  |
| Total | 143.0 MW |  |

- Duration of interruption (रुकावट की अवधि):  1 hours, 52 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 230KV-TTGS-JSW_Vilathikulam_300MW-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

230 kV JSW_Vilathikulam generating station(wind) radially connected to 230 kV TTGS station through 230KV-TTGS-JSW_Vilathikulam_300MW-1 line. As per the reports submitted, the triggering incident was R-G fault in the line during inclement weather. At both the ends of the line differential protection triggered and differential protection operated; however A/R operated from both the ends but at TTGS end 3 phase tripping was observed without any fault and from JSW_Vilanthikulam line is holding as AR was successful at JSW_Vilanthikulam end. As the line is a radial feeder, the tripping of the line at TTGS station led to complete outage of 230kV JSW_Vilanthikulam station.

- DR Analysis:

230KV-TTGS-JSW_Vilathikulam_300MW-1

|  | TTGS - 230KV | JSW_Vilathikulam_300MW - 230KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:02-05-2026 18:39:19.894 MAIN1 Z2 START, MAIN1 Z3 START M1/2 CARR.SEND DIFF TRIP R MAIN1 TRIP, DIFF TRIP MAIN2 TRIP MAIN CB R OPEN MAIN CB AR LO 3PH GR A/B OPTD MAIN CB Y OPEN MAIN CB B OPEN MAIN CB R OPEN Ir (max): 14.06 kA Iy (max): 0.72 kA Ib (max): 0.57 kA Vr (max): 171.15 kV Vy (max): 174.61 kV Vb (max): 161.41 kV | DR Trigger Time:02-05-2026 18:39:20.933 V<1 Start V<1 Start Any Pole Dead Any Pole Dead All Poles Dead TOR Active Ir (max): 0.02 kA Iy (max): 0.02 kA Ib (max): 0.02 kA Vr (max): 167.46 kV Vy (max): 164.48 kV Vb (max): 161.70 kV DR Trigger Time:02-05-2026 18:39:19.894 LINE_DIFF_START, LINE_DIFF_ST_RPH, E/F[67N]_START, E/F[67N]_STFW, E/F[67N]_STIN1 PHE_ZONE_MEAS_EN, DIST_START_RPH, DIST_START_PHE, DIST_START_FWR LINE_DIFF_TRIP, LINE_DIFF_TR_RPH MAIN CB_TRL1 UV_VOLGE_ST_SOTF LINE_DIFF_UNRES, CARR RECV CH-I MAIN1/2_CAR_RECV, CARR REC CH-1 FROM_REM_LINE_DT CARR RECV CH-II MAIN2_TRIP MAIN_CB_R_OPEN E/F[67N]_STRV MAIN 3P TRIP Ir (max): 1.42 kA Iy (max): 0.73 kA Ib (max): 0.57 kA Vr (max): 166.20 kV Vy (max): 184.53 kV Vb (max): 167.51 kV |

JSW_Vilathikulam_300MW - 230KV

|  | JSW_Vilathikulam_300MW - 230KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:02-05-2026 18:39:20.933 V<1 Start V<1 Start Any Pole Dead Any Pole Dead All Poles Dead TOR Active Ir (max): 0.02 kA Iy (max): 0.02 kA Ib (max): 0.02 kA Vr (max): 167.46 kV Vy (max): 164.48 kV Vb (max): 161.70 kV |

- A) PMU Analysis:

From the PMU plot, R-G fault can be observed without any delayed clearance.

B) SCADA Analysis:

From the SCADA data, tripping in the line can be observed.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| PGCIL SR-2 | 1. The 3 phase tripping of the line without any fault during AR operation at TTGS end needs review. |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| JSW_RE | We carried out detailed line patrolling and found no abnormalities/observations. |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

02/05/2026 20:31

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | JSW_RE |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | JSW_RE |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: