# Draft Report on grid event Complete Outage of 220kV SAEL2 of SAEL in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 12-05-2026 17:02

# Event Summary (घटना का सारांश):

# 220kV SAEL2 is connected radially to Kurnool_III through 220kV SAEL2-Kurnool_III-1. The triggering incident is the 3ph fault in the 220kV SAEL2-Kurnool_III-1 and tripping of the line. Due to the tripping of the only connected line to SAEL2 led to the complete outage of 220kV SAEL2 of SAEL

- Time and Date of the Event (घटना का समय और दिनांक:  06-05-2026 19:42

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): ANDHRA PRADESH

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Andhra Pradesh State Demand (MW) | 9836 | 9802 |
| Andhra Pradesh State Generation (MW) | 7272 | 7233 |
| Grid Frequency (Hz) | 49.99 | 50.0 |
| SR Demand (MW) | 56446 | 56342 |
| SR Generation (MW) | 47436 | 47186 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Rainy , Thunders |

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) |  | Load Loss (MW) |
| --- | --- | --- |
| Solar | 0.0 MW | 0.0 MW |
| Wind | 0.0 MW |  |
| Others | 0.0 MW |  |
| Total | 0.0 MW |  |

- Duration of interruption (रुकावट की अवधि):  4 hours, 2 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 220KV-KURNOOL_PG_III-SAEL2-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

220kV SAEL2 is connected radially to Kurnool_III through 220kV SAEL2-Kurnool_III-1 as shown below.

The triggering incident is the 3ph fault in 220kV SAEL2-Kurnool_III-1 line due to inclement weather. At both ends differential protection operated and 3ph tripped. Due to the tripping of the only connected line to SAEL2 led to the complete outage of 220kV SAEL2 of SAEL. During the event, there was no generation at SAEL2.

- DR Analysis:

220KV-KURNOOL_PG_III-SAEL2-1

|  | KURNOOL_PG_III - 220KV | SAEL2 - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:06-05-2026 19:42:09.788 87L_STL3, 87L_BLK2H, 87L_BLK5H 87L_STARTRES, 87L_STL2 MAIN1_Z2_START, MAIN1_Z3_START, 21_STFWL1, 21_STFWL2, 21_STFWL3, ZCPSCH_CS MAIN2_TRIP, M1/2 CARR.SEND, 87L_STL1, PSD_ZOUT DIFF_OPTD, 87L_TRIP, 87L_TRL1, 87L_TRL2, 87L_TRL3 LDLPSCH_TRIP, LDLPSCH_TRL1, LDLPSCH_TRL2, LDLPSCH_TRL3, START_AR, PSD_ZIN MAIN1_TRIP CARF_CH1 BLOCK_AR, FAULT_LOOP_R, FAULT_LOOP_Y, FAULT_LOOP_B GRA_OP GRB_OP 3PH_GR_A/B_OPTD DTRE_CH2 PR3_TR_M DT_REC_CH1/2 PRE3_TR, LDLPSCH_TRREM MAIN_CB_R_OPEN, MAIN_CB_Y_OPEN MAIN_CB_B_OPEN M2CAR_RE 21_STFWPE DEF_ST, 67N_START CARR_CH1 DTRE_CH1 MAIN1/2_CARR_REC, CARR_AID_TRIP PSD_ZIN, PSD_ZOUT BRC START Ir (max): 12.06 kA Iy (max): 13.62 kA Ib (max): 9.80 kA Vr (max): 128.00 kV Vy (max): 128.92 kV Vb (max): 127.70 kV | DR Trigger Time:06-05-2026 19:42:09.780 DIFF_START_BPH, DIFF_BLK_2H, DIFF_BLK_2H_BPH, DIFF_BLK_5H, DIFF_BLK_5H_BPH DIFF_START_RPH, DIFF_START_YPH, DIFF_BLK_2H_RPH, DIFF_BLK_2H_YPH, DIFF_BLK_5H_RPH, DIFF_BLK_5H_YPH DIFF_START_RPH, DIFF_BLK_5H, DIFF_BLK_5H_RPH DIST_START_PP, DIST_START_ND_R, DIST_START_ND_Y, DIST_START_ND_B MAIN2_PROTN_OPTD CARR_RCV_CH-2 DT_SEND_CH-2 DT_SEND_CH-1 DIFF_START_RES DIFF_TRIP_RPH, DIFF_TRIP_YPH, DIFF_TRIP_BPH DIFF_L_TRIP, DIFF_L_TRIP_RPH, DIFF_L_TRIP_YPH, DIFF_L_TRIP_BPH, DIFF_TRIP_LOCAL, DIFF_TRIP_REMOTE 86A_TRP_RLY_OPTD 86B_TRP_RLY_OPTD PSB_ZIN, PSB_ZOUT, FUSE_FAIL_BLKU, FUSE_FAIL_BLKZ PREPARE_3PH_TRIP AR LOCKOUT OPTD DIFF_BLK_2H, DIFF_BLK_2H_BPH DEF_START_FW DIFF_BLK_2H_YPH DIFF_BLK_2H_RPH CB_YPH_OPEN CB_RPH_OPEN, CB_BPH_OPEN CARR_RCV_CH-1 MAIN_CB_OPEN DEF_START_RV, TEF_2ND_HARMONIC Ir (max): 0.31 kA Iy (max): 0.36 kA Ib (max): 0.34 kA Vr (max): 128.03 kV Vy (max): 128.90 kV Vb (max): 128.12 kV |

SAEL2 - 220KV

|  | SAEL2 - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:06-05-2026 19:42:09.780 DIFF_START_BPH, DIFF_BLK_2H, DIFF_BLK_2H_BPH, DIFF_BLK_5H, DIFF_BLK_5H_BPH DIFF_START_RPH, DIFF_START_YPH, DIFF_BLK_2H_RPH, DIFF_BLK_2H_YPH, DIFF_BLK_5H_RPH, DIFF_BLK_5H_YPH DIFF_START_RPH, DIFF_BLK_5H, DIFF_BLK_5H_RPH DIST_START_PP, DIST_START_ND_R, DIST_START_ND_Y, DIST_START_ND_B MAIN2_PROTN_OPTD CARR_RCV_CH-2 DT_SEND_CH-2 DT_SEND_CH-1 DIFF_START_RES DIFF_TRIP_RPH, DIFF_TRIP_YPH, DIFF_TRIP_BPH DIFF_L_TRIP, DIFF_L_TRIP_RPH, DIFF_L_TRIP_YPH, DIFF_L_TRIP_BPH, DIFF_TRIP_LOCAL, DIFF_TRIP_REMOTE 86A_TRP_RLY_OPTD 86B_TRP_RLY_OPTD PSB_ZIN, PSB_ZOUT, FUSE_FAIL_BLKU, FUSE_FAIL_BLKZ PREPARE_3PH_TRIP AR LOCKOUT OPTD DIFF_BLK_2H, DIFF_BLK_2H_BPH DEF_START_FW DIFF_BLK_2H_YPH DIFF_BLK_2H_RPH CB_YPH_OPEN CB_RPH_OPEN, CB_BPH_OPEN CARR_RCV_CH-1 MAIN_CB_OPEN DEF_START_RV, TEF_2ND_HARMONIC Ir (max): 0.31 kA Iy (max): 0.36 kA Ib (max): 0.34 kA Vr (max): 128.03 kV Vy (max): 128.90 kV Vb (max): 128.12 kV |

- A) PMU Analysis:

From the PMU data, 3ph fault can be observed during the event without any delayed fault clearance

B) SCADA Analysis:

From the SCADA data, complete outage of SAEL can be observed

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):  Nil

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| SAEL | Transmission line patrolling done |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | SAEL |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | PGCIL SR-1 |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: