# Draft Report on grid event Complete Outage of 230kV NCTPS Generating station, 230kV Kilpauk SS, 230kV Ganesh Nagar SS, 230kV Basin Bridge SS, 230kV Athipatu SS of TANTRANSCO in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 19-05-2026 21:40

# Event Summary (घटना का सारांश):

# As per the reports submitted, the triggering incident was Y-G fault in 230kV Basin Bridge Tondiarpet line at 03:29:49hrs . At Tondiarpet end, the fault was sensed in zone-1 and the line tripped as A/R lockout operated. At Basin Bridge end, the fault was sensed in zone-1 and Y-pole opened. A/R operated and YB fault is observed after Auto reclosure. However, the fault was not sensed at Basin Bride end. The fault was being continuously fed by 230kV Basin bridge connected lines and other source feeders on zone-3 protection. Subsequently, at 03:30hrs, Y-G fault was observed in 230kV NCTPS Sriperumbudur line. At both ends, the fault was sensed in zone-1. At NCTPS end, A/R did not operate and the line tripped. At Sriperumbudur end, Y-pole opened. B-G fault was sensed in A/R dead time and the line tripped.

Tripping of all source feeders led to complete outage of 230kV NCTPS Generting station and all radial cnnected stations which are 230kV Kilpauk SS, 230kV Ganesh Nagar SS, 230kV Basin Bridge SS, 230kV Athipatu SS.

- Time and Date of the Event (घटना का समय और दिनांक:  08-05-2026 03:30

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): TAMILNADU

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| TamilNadu State Demand (MW) | 15093 | 14602 |
| TamilNadu State Generation (MW) | 4571 | 4128 |
| Grid Frequency (Hz) | 49.98 | 50.0 |
| SR Demand (MW) | 50025 | 49493 |
| SR Generation (MW) | 41536 | 41029 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 505.0 MW | 100.0 MW |

- Duration of interruption (रुकावट की अवधि):  0 hours, 26 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 230KV-NCTPS-TONDIARPET-2

      - 230KV-NCTPS-TONDIARPET-1

      - 230KV-NCTPS-SRIPERUMBADUR_TN-1

      - 230KV-GUMMIDIPOONDI-NCTPS-1

      - 230KV-BASIN_BRIDGE-PULIYANTHOPE-1

      - 230KV-BASIN_BRIDGE-PULIYANTHOPE-2

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

As per the reports submitted, the triggering incident was Y-G fault in 230kV Basin Bridge Tondiarpet line at 03:29:49hrs . At Tondiarpet end, the fault was sensed in zone-1 and the line tripped as A/R lockout operated. At Basin Bridge end, the fault was sensed in zone-1 and Y-pole opened. A/R operated and YB fault is observed after Auto reclosure. However, the fault was not sensed at Basin Bride end. The fault was being continuously fed by 230kV Basin bridge connected lines and the lines tripped in following sequence.

| S.No | Name of the line | Tripping time | Remarks |
| --- | --- | --- | --- |
| 1 | 230KV-NCTPS-TONDIARPET-1 | 03:29:50.978 | Zone-3 Opd at NCTPS end |
| 2 | 230KV-NCTPS-TONDIARPET-2 | 03:29:50.975 | Zone-3 Opd at NCTPS end |
| 3 | 230KV-GUMMIDIPOONDI-NCTPS-1 | 03:29:50.972 | Zone-3 Opd at Gummidipoondi end |
| 4 | 230KV-BASIN_BRIDGE-PULIYANTHOPE-1 | 03:29:50.977 | Zone-3 Opd at Puliyanthope end |
| 5 | 230KV-BASIN_BRIDGE-PULIYANTHOPE-2 | 03:29:51.050 | Zone-3 Opd at Puliyanthope end |

Subsequently, at 03:30hrs, Y-G fault was observed in 230kV NCTPS Sriperumbudur line. At both ends, the fault was sensed in zone-1. At NCTPS end, A/R did not operate and the line tripped. At Sriperumbudur end, Y-pole opened. B-G fault was sensed in A/R dead time and the lline tripped.

Tripping of all source feeders led to complete outage of 230kV NCTPS Generting station and all radial cnnected stations which are 230kV Kilpauk SS, 230kV Ganesh Nagar SS, 230kV Basin Bridge SS, 230kV Athipatu SS.

- DR Analysis:

NCTPS - 230KV

|  | NCTPS - 230KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:08-05-2026 03:29:50.957 FR_DR TRIG On, PH DIST Z3 OP Ir (max): 0.65 kA Iy (max): 3.35 kA Ib (max): 3.07 kA Vr (max): 135.78 kV Vy (max): 135.38 kV Vb (max): 136.56 kV DR Trigger Time:07-05-2026 23:38:05.708 START N, Any Start START R-ph, DIST Start A Rph-MAIN BKR TRP, Yph-MAIN BKR TRP, Bph-MAIN BKR TRP, Rph-TFR BKR TRP, Yph-TFR BKR TRP, Bph-TFR BKR TRP, Z2TorZ3T-EXT AR, START AR, CARR SEND, Any Trip, Fault_REC_TRIG VTS Fast Ir (max): 5.04 kA Iy (max): 0.16 kA Ib (max): 0.16 kA Vr (max): 134.61 kV Vy (max): 135.25 kV Vb (max): 135.82 kV DR Trigger Time:08-05-2026 03:30:01.225 FR_DR TRIG On, GND DIST Z1 OP Ir (max): 0.66 kA Iy (max): 6.62 kA Ib (max): 1.43 kA Vr (max): 152.89 kV Vy (max): 132.93 kV Vb (max): 148.18 kV DR Trigger Time:08-05-2026 03:29:49.191 DIST Start B, Any Start DIST Start B, DIST Start C, Any Start RPh MAIN BKRTRIP, YPh MAIN BKRTRIP, BPh MAIN BKRTRIP, R-TRFR BKR TRIP, Y TRFR BKR TRIP, B TRFR BKR TRIP, 3 PH TRIP, Any Trip, Fault_REC_TRIG Ir (max): 0.93 kA Iy (max): 4.61 kA Ib (max): 3.09 kA Vr (max): 136.35 kV Vy (max): 135.93 kV Vb (max): 137.20 kV DR Trigger Time:08-05-2026 03:29:50.959 DEF BLOCK On GENERAL TRIP On, PH DIST Z3 OP, GENERAL TRIP On, BKA/R Z2 Z3T On Ir (max): 0.64 kA Iy (max): 3.38 kA Ib (max): 3.06 kA Vr (max): 136.29 kV Vy (max): 135.84 kV Vb (max): 137.12 kV |

230KV-BASIN_BRIDGE-TONDIARPET-1

|  | BASIN_BRIDGE - 230KV | TONDIARPET - 230KV |
| --- | --- | --- |
| Time Sync Issue | No | Yes |
| DR Analysis | DR Trigger Time:08-05-2026 03:26:19.550 GND DIST Z3 PKP B, DEF BK VO 60 On GND DIST Z2 PKP B TRIP LED On, GND DIST Z1 PKP B, GND DIST Z1 OP B 52 AR CLOSE On CB B PH CLS On GND DIST Z3 PKP B, DEF BK VO 60 On BUS-2 VT ON On BUS-2 VT ON On BUS-2 VT ON On BUS-2 VT ON On BUS-2 VT ON On BUS-2 VT ON On BUS-2 VT ON On BUS-2 VT ON On BUS-2 VT ON On BUS-2 VT ON On Ir (max): 1.28 kA Iy (max): 19.34 kA Ib (max): 19.29 kA Vr (max): 133.85 kV Vy (max): 133.61 kV Vb (max): 134.42 kV DR Trigger Time:08-05-2026 03:26:21.891 BUS-2 VT ON On M2 FAULTY On, CB A PH CLS On, CB B PH CLS On, CB C PH CLS On CB B PH CLS On, BUS-2 VT ON On M2 FAULTY On, CB A PH CLS On, CB C PH CLS On POWER SWING UN/BLOCK, DIST BLOCK On SOTF TRIP On, DEF BK VO 60 On TRIP LED On AR BLOCK On POWER SWING UN/BLOCK, DIST BLOCK On Ir (max): 0.01 kA Iy (max): 12.16 kA Ib (max): 12.15 kA Vr (max): 143.69 kV Vy (max): 144.20 kV Vb (max): 143.96 kV | DR Trigger Time:08-05-2026 03:29:49.188 Any Start, DIST Fwd Any Trip, DIST Trip B, Z1 Any Pole Dead, All Pole Dead Ir (max): 1.32 kA Iy (max): 16.99 kA Ib (max): 1.30 kA Vr (max): 136.65 kV Vy (max): 134.97 kV Vb (max): 138.37 kV |

230KV-NCTPS-TONDIARPET-1

|  | NCTPS - 230KV | TONDIARPET - 230KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:08-05-2026 03:29:50.957 FR_DR TRIG On, PH DIST Z3 OP Ir (max): 0.65 kA Iy (max): 3.35 kA Ib (max): 3.07 kA Vr (max): 135.78 kV Vy (max): 135.38 kV Vb (max): 136.56 kV DR Trigger Time:08-05-2026 02:30:53.985 Any Start Ir (max): 0.59 kA Iy (max): 1.42 kA Ib (max): 0.35 kA Vr (max): 132.87 kV Vy (max): 132.93 kV Vb (max): 133.34 kV DR Trigger Time:08-05-2026 02:30:55.281 Any Start Ir (max): 0.69 kA Iy (max): 1.76 kA Ib (max): 0.42 kA Vr (max): 132.63 kV Vy (max): 132.79 kV Vb (max): 132.89 kV DR Trigger Time:08-05-2026 02:49:20.028 Any Start Ir (max): 0.96 kA Iy (max): 0.39 kA Ib (max): 0.69 kA Vr (max): 133.09 kV Vy (max): 134.11 kV Vb (max): 133.74 kV DR Trigger Time:08-05-2026 03:33:05.482 VTS Fast VTS Fast VTS Fast Ir (max): 0.00 kA Iy (max): 0.00 kA Ib (max): 0.00 kA Vr (max): 136.25 kV Vy (max): 136.17 kV Vb (max): 137.50 kV | Line was holding |

230KV-NCTPS-TONDIARPET-2

|  | NCTPS - 230KV | TONDIARPET - 230KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:07-05-2026 23:38:05.708 START N, Any Start START R-ph, DIST Start A Rph-MAIN BKR TRP, Yph-MAIN BKR TRP, Bph-MAIN BKR TRP, Rph-TFR BKR TRP, Yph-TFR BKR TRP, Bph-TFR BKR TRP, Z2TorZ3T-EXT AR, START AR, CARR SEND, Any Trip, Fault_REC_TRIG VTS Fast Ir (max): 5.04 kA Iy (max): 0.16 kA Ib (max): 0.16 kA Vr (max): 134.61 kV Vy (max): 135.25 kV Vb (max): 135.82 kV DR Trigger Time:08-05-2026 03:29:50.959 DEF BLOCK On GENERAL TRIP On, PH DIST Z3 OP, GENERAL TRIP On, BKA/R Z2 Z3T On Ir (max): 0.64 kA Iy (max): 3.38 kA Ib (max): 3.06 kA Vr (max): 136.29 kV Vy (max): 135.84 kV Vb (max): 137.12 kV | Line was holding |

230KV-NCTPS-SRIPERUMBADUR_TN-1

|  | NCTPS - 230KV | SRIPERUMBADUR_TN - 230KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:08-05-2026 03:30:01.219 START Y PH, DIST Start B, Any Start RPh MAIN BKRTRIP, YPh MAIN BKRTRIP, BPh MAIN BKRTRIP, R-TRFR BKR TRIP, Y TRFR BKR TRIP, B TRFR BKR TRIP, 3 PH TRIP, START AR, CARRIER SEND, Any Trip, Fault_REC_TRIG START N CARRIER RECIEVE, DIST. Chan Recv VTS Fast CARRIER RECIEVE, DIST. Chan Recv Ir (max): 0.66 kA Iy (max): 6.64 kA Ib (max): 1.43 kA Vr (max): 153.80 kV Vy (max): 133.08 kV Vb (max): 147.24 kV DR Trigger Time:08-05-2026 02:49:20.029 START N, Any Start Ir (max): 0.36 kA Iy (max): 0.06 kA Ib (max): 0.12 kA Vr (max): 133.65 kV Vy (max): 134.14 kV Vb (max): 134.04 kV DR Trigger Time:08-05-2026 03:29:49.210 START N, Any Start Ir (max): 0.45 kA Iy (max): 1.24 kA Ib (max): 1.01 kA Vr (max): 133.63 kV Vy (max): 133.45 kV Vb (max): 134.66 kV DR Trigger Time:08-05-2026 03:30:01.225 FR_DR TRIG On, GND DIST Z1 OP Ir (max): 0.66 kA Iy (max): 6.62 kA Ib (max): 1.43 kA Vr (max): 152.89 kV Vy (max): 132.93 kV Vb (max): 148.18 kV | DR Trigger Time:08-05-2026 03:30:01.243 Started Phase B, Started Phase N Any Trip, Zone 1 Trip, RL7 FEEDBACK, RL10 CR1 SEND, RL11 CR2 SEND, Aided 1 Send, Aided 2 Send, Trip Output B L11 CR1 RECVD Aid 1 Dist Trip, Aided 1 Receive L2 CB OPN B Any Trip, Zone 1 Trip, Aid 1 Dist Trip, RL7 FEEDBACK, Started Phase C, Started Phase N, RL10 CR1 SEND, RL11 CR2 SEND, Aided 1 Send, Aided 2 Send, Trip Output A, Trip Output B, Trip Output C L1 CB OPN A L3 CB OPN C Ir (max): 0.66 kA Iy (max): 3.26 kA Ib (max): 3.06 kA Vr (max): 140.15 kV Vy (max): 134.86 kV Vb (max): 136.38 kV |

230KV-GUMMIDIPOONDI-NCTPS-1

|  | NCTPS - 230KV | GUMMIDIPOONDI - 230KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | Line was holding | DR Trigger Time:08-05-2026 03:29:49.185 T1 Z3 T1 Z3 T2 Any Trip, Any Trip A, Any Trip B, Any Trip C, 3P Trip, T3 Ir (max): 0.82 kA Iy (max): 2.29 kA Ib (max): 1.89 kA Vr (max): 135.97 kV Vy (max): 134.52 kV Vb (max): 134.43 kV |

230KV-BASIN_BRIDGE-PULIYANTHOPE-1

|  | BASIN_BRIDGE - 230KV | PULIYANTHOPE - 230KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | Line was holding | DR Trigger Time:08-05-2026 03:29:50.177 ZONE 3 START ON (VO41) LINE PICKUP RCL TRIP DR TRIGGER ON (VO17), DR TRIGGER ON (VO17) Z-3 TRIP ON (VO3) TRIP PHASE A, TRIP PHASE B, TRIP PHASE C, R36. GRP-A TRIP CLOSED (CO36), R37. GRP-B TRIP CLOSED (CO37), TRIP 3-POLE OPEN POLE OP, OPEN POLE OP A, OPEN POLE OP B, OPEN POLE OP C 1.M CB OPEN A PH ON (CI1), OPEN POLE BKR PHASE A OP 3. M CB OPEN C PH ON (CI3), OPEN POLE BKR PHASE C OP 2.M CB OPEN B PH ON (CI2), OPEN POLE BKR PHASE B OP OPEN POLE OP, OPEN POLE OP C Ir (max): 0.33 kA Iy (max): 10.76 kA Ib (max): 10.42 kA Vr (max): 146.46 kV Vy (max): 147.44 kV Vb (max): 140.44 kV |

230KV-BASIN_BRIDGE-PULIYANTHOPE-2

|  | BASIN_BRIDGE - 230KV | PULIYANTHOPE - 230KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | Line was holding | DR Trigger Time:08-05-2026 03:29:49.203 Virtual Output30, Zone 3 B Start, Zone 3 N Start Virtual Output30, Zone 3 B Start, Zone 3 C Start Virtual Output30, Zone 3 B Start, Zone 3 C Start Virtual Output30, Zone 3 B Start, Zone 3 C Start Any Trip, Trip Output A, Trip Output B, Trip Output C, Zone 3 Trip L3 M CB OPEN B P L1 M CB OPEN R P L2 M CB OPEN Y P Ir (max): 1.10 kA Iy (max): 12.22 kA Ib (max): 11.78 kA Vr (max): 146.52 kV Vy (max): 147.02 kV Vb (max): 137.85 kV |

230KV-NCTPS-ATHIPATU-2

|  | NCTPS - 230KV | ATHIPATU - 230KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | Loss of power supply | Loss of power supply |

230KV-NCTPS-KILPAUK-1

|  | NCTPS - 230KV | KILPAUK - 230KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | Loss of power supply | Loss of power supply |

230KV-NCTPS-ATHIPATU-1

|  | NCTPS - 230KV | ATHIPATU - 230KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | Loss of power supply | Loss of power supply |

- A) PMU Analysis:

From the PMU Y-G fault followed by YB fault is observed at 03:29:49hrs where a delayed fault clearance of 1600ms is observed for YB fault. At 03:30:01hrs, Y-G fault followed by B-G fault is observed.

B) SCADA Analysis:

From SCADA plots, tripping of 230kV NCTPS Tondiarpet Line-1&2 and 230kV NCTPS Athipatu line can be observed.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| TANTRANSCO | 1. Non operation of A/R at Tondiarpet end in 230kV Basin Bridge Tondiarpet line. 2. Zone-3 settings co-ordination in NCTPS and Basin bridge connected lines to be reviiewed. |
| TNPGCL | 1. Non operation of A/R at NCTPS end in 230kV NCTPS Sriperumbudur line. |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| TANTRANSCO | The above fault trip feeders line fault was attended. |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

230kV Nctps-1 to Gummdipoondi feeder normalized on 08.05.2025 at 03:58 Hrs.

230kV Nctps-1 to Station transformer-1 charged on 08.05.2025 at 04:00 Hrs.

230kV Nctps-1 to Station transformer-2 charged on 08.05.2025 at 04:01 Hrs.

230kV Nctps-1 to Kilpauk feeder normalized on 08.05.2025 at 04:24 Hrs.

230kV Nctps-1 to Tondairpet-2 feeder normalized on 08.05.2025 at 04:36 Hrs.

230kV Nctps-1 to Athipathu-1 feeder normalized on 08.05.2025 at 04:41 Hrs.

230kV Nctps-1 to Athipathu-2 feeder normalized on 08.05.2025 at 04:48 Hrs.

230kV Nctps-1 to Tondairpet-1 feeder normalized on 08.05.2025 at 05:07 Hrs.

Unit-I synchronized on 08.05.2025 at 09:51 Hrs.

Unit-II synchronized on 08.05.2025 at 13:14 Hrs.

Unit-III synchronized on 08.05.2025 at 13:25 Hrs.

230kV Nctps-1 to Sriperumbudur feeder normalized on 08.05.2025 at 14:30 Hrs.

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | TNPGCL |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | TNPGCL, TANTRANSCO |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: