# Draft Report on grid event Tripping of 220kV Bus-2 of Chilakallu of APTRANSCO in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 12-05-2026 15:47

# Event Summary (घटना का सारांश):

# The triggering incident is the B-G fault in 220KV-CHILLAKALLU-PULICHINTALA-1, during which B-ph breaker failed to open at CHILLAKALLU end and led to the LBB operation in Bus-2 and all elements connected to Bus-2 at CHILLAKALLU tripped and led to the Tripping of 220kV Bus-2 of Chilakallu of APTRANSCO

- Time and Date of the Event (घटना का समय और दिनांक:  30-04-2026 13:16

- Event Category (ग्रिड घटना का प्रकार):  GI-1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): ANDHRA PRADESH , TELANGANA

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Telangana State Demand (MW) | 11382 | 11414 |
| Telangana State Generation (MW) | 5847 | 5824 |
| Andhra Pradesh State Demand (MW) | 13037 | 13056 |
| Andhra Pradesh State Generation (MW) | 7459 | 7392 |
| Grid Frequency (Hz) | 49.98 | 50.04 |
| SR Demand (MW) | 65543 | 65576 |
| SR Generation (MW) | 55225 | 55085 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

At Chilakallu SS, elements were connected in the following manner.

Bus-1: Kondapalli-1,VTPS-1, Suryapeta, 100MVA PTR-1& 100MVA PTR-3.

Bus-2: Kondapalli-2,VTPS-2, Pulichintala, 100MVA PTR-2.

Bus coupler CB was in closed condition.

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 0.0 MW | 0.0 MW |

- Duration of interruption (रुकावट की अवधि):  0 hours, 13 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 220KV-KONDAPALLI-CHILLAKALLU-2

      - 220KV-VTPS-CHILLAKALLU-2

      - CHILLAKALLU - 220KV - Bus 2

      - 220KV-CHILLAKALLU-PULICHINTALA-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

In the antecedent condition, 220kV Chillakallu-VTS-2, 220kV Chillakallu-Kondapalli-2, 220/110kV 100MVA Chillakallu PTR-2 and 220kV Chillakallu-Pulichintala were connected to Bus-2 of 220kV Chillakallu.

The triggering incident is the B-G fault in 220KV-CHILLAKALLU-PULICHINTALA-1, at PULICHINTALA end, the fault was sensed in Z1 and AR operated and tripped to persistent fault. At CHILLAKALLU end, the fault was sensed in Z1 and B pole opened and AR operated after around 1 sec and Z1 was sensed due to persistent fault, however B-ph breaker failed to open at CHILLAKALLU end and led to the LBB operation in Bus-2 and all elements connected to Bus-2 (220kV Chillakallu-VTS-2, 220kV Chillakallu-Kondapalli-2, 220/110kV 100MVA Chillakallu PTR-2 and 220kV Chillakallu-Pulichintala) at CHILLAKALLU tripped and this led to the Tripping of 220kV Bus-2 of Chilakallu of APTRANSCO

- DR Analysis:

220KV-CHILLAKALLU-PULICHINTALA-1

|  | CHILLAKALLU - 220KV | PULICHINTALA - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | Yes |
| DR Analysis | DR Trigger Time:30-04-2026 13:16:53.345 1ph Fault Z2 L11 M2LBBINB/ARI Any Trip, A/R 1P In Prog, A/R 1st In Prog, 1P Trip DIST Trip C, Z1, DIST Sig. Send, R8 CARR SEND CH1, R7 CARR SEND CH2 A/R Trip 3P A/R Close, A/R Reclaim L3 M CB CLS-B A/R Lockout Any Trip, AR Lockout Shot>, SOTF/TOR Trip, 3P Trip, R12 86A TR-Z2_.., R18 86B TR-Z2_.. 1ph Fault Z1, DIST Sig. Send, R8 CARR SEND CH1, R7 CARR SEND CH2 L11 M2LBBINB/ARI L15 BB OPTD DIST. Chan Recv, L8 CARR REC CH1 Ir (max): 0.19 kA Iy (max): 0.43 kA Ib (max): 6.69 kA Vr (max): 150.71 kV Vy (max): 130.12 kV Vb (max): 129.04 kV | DR trigger time : 13:18:43.507 B-G fault Z1, AR operated ToR |

CHILLAKALLU - 220KV

|  | CHILLAKALLU - 220KV |
| --- | --- |
| Time Sync Issue | Yes |
| DR Analysis | DR Trigger Time:30-04-2026 14:16:53.350 ZA IIN ALM, ZB IIN ALM ZA IIN ALM, ZB IIN ALM BAY09 TR BAY09 LBB TR ZB EXT BAY TR, ZB COMMON TR BAY02 TR, BAY03A TR, BAY05 TR, BAY08 TR Ir (max): 1.03 kA Iy (max): 0.91 kA Ib (max): 4.61 kA DR Trigger Time:30-04-2026 13:16:53.345 1ph Fault Z2 L11 M2LBBINB/ARI Any Trip, A/R 1P In Prog, A/R 1st In Prog, 1P Trip DIST Trip C, Z1, DIST Sig. Send, R8 CARR SEND CH1, R7 CARR SEND CH2 A/R Trip 3P A/R Close, A/R Reclaim L3 M CB CLS-B A/R Lockout Any Trip, AR Lockout Shot>, SOTF/TOR Trip, 3P Trip, R12 86A TR-Z2_.., R18 86B TR-Z2_.. 1ph Fault Z1, DIST Sig. Send, R8 CARR SEND CH1, R7 CARR SEND CH2 L11 M2LBBINB/ARI L15 BB OPTD DIST. Chan Recv, L8 CARR REC CH1 Ir (max): 0.19 kA Iy (max): 0.43 kA Ib (max): 6.69 kA Vr (max): 150.71 kV Vy (max): 130.12 kV Vb (max): 129.04 kV |

- A) PMU Analysis:

From the PMU data, B-G fault was can be observed with AR operation and delayed fault clearance

B) SCADA Analysis:

From the SCADA data, tripping of the Bus-2 at Chilakallu can be observed

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| APTRANSCO | 1. Non opening of B-ph breaker of 220KV-CHILLAKALLU-PULICHINTALA-1 at CHILLAKALLU end needs review |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| APTRANSCO | 1. B-Pole CB limb of 220kV Pulichintala feeder bay was lubricated thoroughly and tested for closing and opening operations on the same day. On 01/05/2026 availed LC on the same feeder bay and carried out lubrication of all the pole limbs, CB timings test, DCRM test was carried and found satisfactory. 2. The time drift in Bus bar protection relay (REB670) and Main-2 relay (REL670) was attended by correcting time zone settings in respective relays. |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

220kV Chillakallu Bus coupler CB closed at 13:29 Hrs.

100MVA Chillakallu PTR-2 CB closed at 13:30 Hrs.

220kV Chillakallu-VTS-2 feeder CB closed at 13:33 Hrs.

220kV Chillakallu-Kondapalli-2 feeder CB closed at 13:34 Hrs.

220kV Chillakallu-Pulichintala feeder CB was closed at 19:13 Hrs.

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | APTRANSCO |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 |  |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) | APTRANSCO |
| 4 | Any other non-compliance | IEGC section 17.3 | TGGENCO, APTRANSCO |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: