## Summary
सुरक्षा प्रदर्शन सूचकांक/ Protection Performance Indices |  |  |  |  | 01-04-2026 | to | 30-04-2026
उपयोगिता का नाम/Name of the Utility | सुरक्षा अभियान के अनुसार ट्रिपिंग क्रम में/Trippings in order as per protection operation (Nc) | अनुचित परिचालनों की संख्या/No.of Unwarranted Operations (Nu) | विफल परिचालनों की संख्या/No.of failed operations (Nf) | (Ni=Nu+Nf) | सुरक्षा सूचकांक/Security Index [S=Nc/ (Nc+NU)] | निर्भरता सूचकांक/Dependability Index [D=Nc/ (Nc+Nf)] | विश्वसनीयता सूचकांक/Reliability Index [R=Nc/ (Nc+Ni)]
APGENCO | 41 | 0 | 2 | 2 | 1 | 0.95349 | 0.95349
APTRANSCO | 224 | 4 | 2 | 6 | 0.98246 | 0.99115 | 0.97391
GREENKO | 0 | 1 | 0 | 1 | 0 | NA | 0
HINDUJA | 2 | 0 | 0 | 0 | 1 | 1 | 1
JSW_RE | 0 | 0 | 0 | 0 | NA | NA | NA
JSW_THERMAL | 2 | 5 | 0 | 5 | 0.28571 | 1 | 0.28571
KPCL | 16 | 0 | 0 | 0 | 1 | 1 | 1
NPCIL_KAIGA | 3 | 0 | 0 | 0 | 1 | 1 | 1
NPCIL_KKNP | 3 | 0 | 0 | 0 | 1 | 1 | 1
NPCIL_MAPS | 2 | 0 | 0 | 0 | 1 | 1 | 1
NTECL | 1 | 0 | 0 | 0 | 1 | 1 | 1
NTPC | 1 | 0 | 0 | 0 | 1 | 1 | 1
NTPC_RSTPS | 0 | 0 | 0 | 0 | NA | NA | NA
NTPC_SIMHADRI | 1 | 0 | 0 | 0 | 1 | 1 | 1
PGCIL SR-1 | 48 | 2 | 0 | 2 | 0.96 | 1 | 0.96
PGCIL SR-2 | 41 | 0 | 2 | 2 | 1 | 0.95349 | 0.95349
TANTRANSCO | 329 | 4 | 9 | 13 | 0.98799 | 0.97337 | 0.96199
TGGENCO | 19 | 0 | 0 | 0 | 1 | 1 | 1
TGTRANSCO | 78 | 4 | 5 | 9 | 0.95122 | 0.93976 | 0.89655
Vena_GadagPS | 1 | 0 | 0 | 0 | 1 | 1 | 1
ADANI_APL | NA | NA | NA | NA | NA | NA | NA
BETAMWIND | NA | NA | NA | NA | NA | NA | NA
MEPL | NA | NA | NA | NA | NA | NA | NA
NTPC_KUDGI | NA | NA | NA | NA | NA | NA | NA
NTPC_TESTPP | NA | NA | NA | NA | NA | NA | NA
NTPL | NA | NA | NA | NA | NA | NA | NA
ORANGE | NA | NA | NA | NA | NA | NA | NA
OSTRO_KANNADA | NA | NA | NA | NA | NA | NA | NA
PONDICHERRY | NA | NA | NA | NA | NA | NA | NA
PVG_IRCON_S | NA | NA | NA | NA | NA | NA | NA
SEIL | NA | NA | NA | NA | NA | NA | NA
TATA | NA | NA | NA | NA | NA | NA | NA
TELENGANA | NA | NA | NA | NA | NA | NA | NA
ADANI_ATL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
AMGEPL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
APSPCL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
Ayana Renewable Power Six Pvt Ltd | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
BHAVINI | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
GREENINFRA | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
GRT | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
GTL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
HIRIYUR_ZREPL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
ILFS | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
INDIGRID | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
KLEIO_SOLAR | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
KPTCL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
KSEB | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
KSPDCL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
LKPPL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
MYTRAH | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
NLC | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
RENEW POWER PVT LTD | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
SAEL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
SCCL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
SEPC | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
SEPL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
SERENTICA_RI1PL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
Spring_Pugalur | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
TNGECL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
TNPGCL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified

## All
क्र. स. /S.NO. | एलमन्ट नाम/ ELEMENT NAME | एलमन्ट प्रकार/ELEMENT TYPE | वोल्टेज स्तर/Voltage Level | इंट्रा/इंटर स्टेट एलमन्ट/Intra/Inter state element | एलीमेंट का मालिक/Owner of the element | ट्रिपिंग की तारीख/ TRIPPING DATE | ट्रिपिंग का समय/ TRIPPING TIME | भेजनेवाला/Sending End |  |  |  |  | प्राप्त करनेवाला/Receiving End |  |  |  |  | ट्रिपिंग का कारण /REASON for Tripping
[8 empty] | मालिक/OWNER | वर्गीकरण/Classification | वर्गीकरण टिप्पणी/Classification Comment | कार्य योजना/Action Plan | कार्य योजना की स्थिति/Action Plan Status | मालिक/OWNER | वर्गीकरण/Classification | वर्गीकरण टिप्पणी/Classification Comment | कार्य योजना/Action Plan | कार्य योजना की स्थिति/Action Plan Status
1 | 230KV-TIRUNELVELI-VEERANAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-04-2026 | 03:22 | PGCIL SR-2 | Failure Operation | AR FAILED @ TIRUNELVELI END DUE TO CB UNHEALTHY DURING AR | ISSUE ATTENDED | Completed | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRIPPED AND REASON AWAITED
2 | 400KV-GOOTY-KURNOOL_PG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 01-04-2026 | 09:19 | PGCIL SR-1 | Correct Operation | Auto reclose attempted and tripped on persisting fault Y-G fault |  |  | PGCIL SR-1 | Correct Operation | Auto reclose attempted and tripped on persisting fault Y-G fault |  |  | TRIPPED ON Y-N FAULT
3 | 400KV-KALPAKKA-ASUPAKA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | APTRANSCO | 03-04-2026 | 12:03 | APTRANSCO | Failure Operation | fault tripping | The non-operation of SOTF/TOR during zone 2 pickup was addressed to OEM. With the support of OEM the problem will be resolved. The AR feature was enabled in Siemens BCU with dead time of 1 sec. while AR operations during the reclose of breaker the AR close command is being issued with 100 to 150 mS delay. The same was raised to M/s Siemens and is being pursued with M/s Siemens for proper operation of AR. | Pending | TGTRANSCO | Correct Operation | Correcet operation |  |  | tripped on RN fault
4 | 400KV/230KV PULIYANTHOPE-ICT-2 | TRANSFORMER | 400 | Intra | TANTRANSCO | 02-04-2026 | 20:29 | TANTRANSCO | Correct Operation | Differential trip & REF trip_Y phase LV side GIS ES champer faulty | [7 empty] | TRIPPED AND REASON AWAITED
5 | 400KV-DONI-GUTTUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 03-04-2026 | 12:20 | KPTCL | Correct Operation | RN fault TOR due to persistent fault |  |  | KPTCL | Correct Operation | RN fault TOR due to persistent fault |  |  | Rph - G fault
6 | 400KV-ALAMATHY-TIRUVALAM_TN-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 03-04-2026 | 12:36 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL & DUE TO SUBSEQUENT FAULT LOCKOUT TRIP INITIATED_Tree clearance done between Loc. No.155 & 156 |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL, DUE TO SUBSEQUENT FAULT WITHIN RECLAIM TIME LOCKOUT TRIP INITIATED_Tree clearance done between Loc. No.155 & 156 |  |  | Reason awaited
7 | 400KV-ALAMATHY-TIRUVALAM_TN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 03-04-2026 | 11:58 | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR_Tree clearance done between Loc. No.155 & 156 |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,TOR_Tree clearance done between Loc. No.155 & 156 |  |  | SOTF OPERATED
8 | 400KV-KURNOOL_PG-NAGARJUNASAGAR_PG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 02-04-2026 | 14:47 | PGCIL SR-1 | Correct Operation | Line tripped due to DT receipt from NSagar End. |  |  | PGCIL SR-1 | Unwanted Operation | Line tripped due to mal operation of Group relay at Nagarjunasagar End. | Group relay replaced | Completed | Tripped
9 | 400KV-SATTENPALLY-PODILI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 05-04-2026 | 12:44 | APTRANSCO | Correct Operation | No visible fault observed |  |  | APTRANSCO | Correct Operation | nil |  |  | TRIPPED ON B-N FAULT
10 | 400KV-MANALI-PULIYANTHOPE-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 06-04-2026 | 05:20 | TANTRANSCO | Correct Operation | LDP_R,Y_At loc.8 Rph insulation flashover\ |  |  | TANTRANSCO | Correct Operation | LDP_R,Y_At loc.8 Rph insulation flashover\ |  |  | Reason awaited
11 | 765KV-THIRUVALAM-ARIYALUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Intra | TANTRANSCO | 04-04-2026 | 19:36 | PGCIL SR-2 | Failure Operation | AR Failed to Operate |  | Pending | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRIPPED ON Y-N FAULT
12 | 230KV-KALVENDAPATTU-VEERAPURAM | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 05-04-2026 | 13:31 | PGCIL SR-2 | Correct Operation | AR Successful @ KALIVANTHAPATTU END. 14.2 KM / 10 KA |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | Veerapuram: DP, Z-1, Y-B-N, 1.1 kA, 1.4 kA, 7.9 Kms; PG: DP, Z-1, Y-B-N, 10.2 kA, 10.13 kA, 14.2 Kms
13 | 400KV-MANALI-PULIYANTHOPE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 06-04-2026 | 06:54 | TANTRANSCO | Correct Operation | LDP_Bphase_AR Lockout due to subsequent fault within reclaim time_At loc.24, Bph suspension insulator flashover |  |  | TANTRANSCO | Correct Operation | LDP_Bphase_AR Lockout due to subsequent fault within reclaim time_At loc.24, Bph suspension insulator flashover |  |  | SOTF, Cph fault
14 | 400KV-KURNOOL_PG-NAGARJUNASAGAR_PG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 05-04-2026 | 18:02 | PGCIL SR-1 | Correct Operation | Tripped on operation of OV-I at Kurnool SS and DT sent to remote end |  |  | PGCIL SR-1 | Correct Operation | Tripped on operation of OV-I at Kurnool SS and DT sent to remote end |  |  | Over Voltage stage-I operation at Kurnool
15 | 765KV-KURNOOL_PG-CUDDAPAH-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Intra | POWERGRID | 05-04-2026 | 18:00 | PGCIL SR-1 | Correct Operation | Tripped on operation of OV-I at Kadapa SS and DT sent to remote end |  |  | PGCIL SR-1 | Correct Operation | Tripped on operation of OV-I at Kadapa SS and DT sent to remote end |  |  | Over voltage stage -I operation at Kadapa end
16 | 400KV-KONASEEMA-VEMAGIRI_AP-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 06-04-2026 | 10:41 | APTRANSCO | Correct Operation | 400kV Vemagiri-Konaseema feeder is in idle charged from Vemagiri end and the line isolator was kept open at konaseema end |  |  | APTRANSCO | Correct Operation | Group trip was issued as all forward zone time delays were kept instataneous and 86A & 86B operated and three phase tripping occured. |  |  | R-N, 17.7 Kms, 11.7 kA
17 | 400KV-SRIPERUMBADUR-CHITTOOR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 07-04-2026 | 12:20 | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | APTRANSCO | Correct Operation | Tripping operation is in correct order. |  |  | TRIPPED ON R-N FAULT
18 | 230KV-ARNI-KANCHIPURAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 05-04-2026 | 23:39 | TANTRANSCO | Correct Operation | Holding |  |  | TANTRANSCO | Correct Operation | Zone.3,Y,N |  |  | Trip
19 | 230KV-ARNI-BHAVANI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 05-04-2026 | 23:39 | TANTRANSCO | Correct Operation | Holding |  |  | BHAVINI |  |  |  |  | Trip
20 | 400KV-SRIPERUMBADUR-CHITTOOR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 07-04-2026 | 11:03 | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | APTRANSCO | Correct Operation | Trip operation is in correct order. |  |  | RN fault with unsucessfull A/R
21 | 230KV-ARNI-SINGARPET | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 05-04-2026 | 23:39 | TANTRANSCO | Correct Operation | Holding |  |  | TANTRANSCO | Correct Operation | ZONE.3,R,Y,N |  |  | Trip
22 | 230KV-ARNI-ECHUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 05-04-2026 | 23:39 | TANTRANSCO | Correct Operation | Holding |  |  | TANTRANSCO | Correct Operation | Holding |  |  | Trip
23 | 400KV-GUDDIGUDEM-HINDUJA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 08-04-2026 | 14:21 | APTRANSCO | Correct Operation | AR operated and unsuccessful due to persistent fault. charged after line patrolling. feeder stood ok |  |  | HINDUJA | Correct Operation | Tripped on persistent fault |  |  | Tripped
24 | 400KV-DICHPALLY-NIRMAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 04-04-2026 | 22:26 | TGTRANSCO | Failure Operation | AR not operated | relays will be test by availing LC | Pending | TGTRANSCO | Correct Operation | Correcet operation |  |  | TRIPPED ON Y-N FAULT
25 | 400KV-CHOUTUPPAL-KHAMMAM_PG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 06-04-2026 | 15:59 | TGTRANSCO | Failure Operation | AR not operated | rectified the issue with single phase trip relay | Completed | PGCIL SR-1 | Correct Operation | AR attempted and tripped on persisting B-N fault. |  |  | TRIPPED ON R-N FAULT
26 | 400KV-DICHPALLY-NIZAMABAD-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 04-04-2026 | 22:31 | TGTRANSCO | Correct Operation | line is in service at Dichpally end |  |  | PGCIL SR-1 | Correct Operation | NIL |  |  | TRIPPED ON Y-N FAULT
27 | 400KV-SATTENPALLY-PODILI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 08-04-2026 | 13:39 | APTRANSCO | Correct Operation | Distance protection operated |  |  | APTRANSCO | Correct Operation | Distance protection operated |  |  | R N fault
28 | 400KV/220KV DICHPALLY-ICT-4 | TRANSFORMER | 400 | Intra | TGTRANSCO | 04-04-2026 | 22:26 | TGTRANSCO | Correct Operation | Correcet operation | [7 empty] | Bus bar protection operated
29 | 230KV-MAPS-ECHUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 05-04-2026 | 23:39 | NPCIL_MAPS | Correct Operation | operation of earth fault protection |  |  | TANTRANSCO | Correct Operation | Holding |  |  | Trip
30 | 220KV-GADAG_PSS-RSRPL_GadagPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | GADAG_RSRPL | 05-04-2026 | 08:55 | GTL | Unwanted Operation | Line was idle charged from GTL Gadag end and tripped from RSRPL end. |  |  | RENEW POWER PVT LTD |  |  |  |  | Tripped on Y-B Fault
31 | 230KV-ARNI-BHAVANI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | POWERGRID | 05-04-2026 | 23:39 | TANTRANSCO | Correct Operation | NIL |  |  | BHAVINI |  |  |  |  | Trip
32 | 400KV-GUTTUR-HIRIYUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 09-04-2026 | 11:22 | KPTCL | Unwanted Operation | Line tripped due to PD relay cable damage | Attended and the normalcy of the line was restored | Completed | PGCIL SR-2 | Correct Operation | No trip/ fault events @ Hiriyur end. |  |  | TRIPPED ON Y-N FAULT
33 | 220KV-KAIGA-KODASALLY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 10-04-2026 | 13:01 | NPCIL_KAIGA | Correct Operation | B phase fault in transmission line |  |  | KPCL | Correct Operation |  |  |  | TRIPPED ON B-N FAULT at 11.26 kms from Kodasalli end, Ic=3.991kA
34 | 220KV-MYSORE-K R PET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 10-04-2026 | 22:05 | PGCIL SR-2 | Correct Operation | AR Successful. 18.13 km / 6.57 kA |  |  | KPTCL | Correct Operation |  |  |  | KA: DP, Z-1, R-N, 1.85 kA, 24.45 Kms; PG: AR successful
35 | 400KV-KALABURAGI-YTPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 10-04-2026 | 15:25 | KPTCL | Correct Operation | Transient Fault |  |  | KPCL | Correct Operation | Correct operation |  |  | tree touched, y-n fault
36 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | TGTRANSCO | 12-04-2026 | 14:38 | APGENCO | Correct Operation | correct operation |  |  | TGGENCO | Correct Operation | Carrier Aided Protection Operated |  |  | Rph fault
37 | 220KV-NP_KUNTA PSS3-NP_KUNTA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APSPCL | 13-04-2026 | 14:02 | APSPCL | Unwanted Operation | tripped on differential protection on the B phase. |  |  | PGCIL SR-1 | Correct Operation | Auto reclose attempted on Bph-G fault but tripped on persisting fault |  |  | Line Differential, B-N
38 | 400KV-JINDAL-BPS-4 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 13-04-2026 | 15:52 | JSW_THERMAL | Unwanted Operation | others |  | Pending | KPTCL | Correct Operation | The line did not trip at BPS end | GPR issue to be resolved by JSWEL |  | No relay Indication. CB tripped when fault in YTPS-BPS-1
39 | 400KV-MARADAM-KALPAKKA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 13-04-2026 | 19:37 | APTRANSCO | Correct Operation | Protection in order as there was 'NO' zone detected in both Main-1 and Main-2 |  |  | APTRANSCO | Correct Operation | line tripped on fault in dead time |  |  | R-Y-B FAULT
40 | 230KV-ARASUR_PG-GOBI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 14-04-2026 | 14:03 | PGCIL SR-2 | Correct Operation | Line tripped on Persisting Fault in Line.- 15.7 km / 6.14 kA. |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | GOBI ¦ Tripped on C-N fault, 3.38kA, 33.8km
41 | 220KV-NP_KUNTA PSS3-NP_KUNTA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APSPCL | 14-04-2026 | 11:59 | APSPCL | Unwanted Operation | tripped on differential protection on the B phase. |  |  | PGCIL SR-1 | Correct Operation | Auto reclose attempted on Bph-G fault but tripped on persisting fault. Fault details: NPK End:FC/FD-4.48KA/4.71KM |  |  | Differential relay operated
42 | 220KV-KOTTAYAM-PALLOM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 14-04-2026 | 16:40 | KSEB | Correct Operation | Delayed tripping |  |  | KSEB | Correct Operation | Fault in the bus isolator connection of 220kV Pallom-New Pallom-1 at New Pallom. Bus fault (B-G). BB protection at New Pallom was not operated. Fault in the 'out of zone' of pilot wire differential protection and so, backup protection of the New Pallom-Pallom feeder was operated. 220kV Kottayam-Pallom-1 tripped from remote end. |  |  | Trip
43 | 220KV-PALLOM-NEW PALLOM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 14-04-2026 | 16:40 | KSEB | Correct Operation | Fault in the bus isolator connection of 220kV Pallom-New Pallom-1 at New Pallom. Bus fault (B-G). BB protection at New Pallom was not operated. Fault in the 'out of zone' of pilot wire differential protection and so, backup protection at Pallom operated. |  |  | KSEB | Failure Operation | Fault in the bus isolator connection of 220kV Pallom-New Pallom-1 at New Pallom. Bus fault (B-G). BB protection at New Pallom was not operated. Fault in the 'out of zone' of pilot wire differential protection and so, backup protection at Pallom and New Pallom was operated. | Corrected the logic in the check zone (B-phase) in the BB protection. | Completed | Trip
44 | 400KV-BPS-YTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 13-04-2026 | 15:52 | KPTCL | Correct Operation | Correct Operation |  |  | KPCL | Correct Operation | Correct operation |  |  | Tripped
45 | 400KV/6.9KV MANUGURU-ST-1 | TRANSFORMER | 400 | Intra | TGTRANSCO | 15-04-2026 | 09:41 | TGGENCO | Correct Operation | It was observed that there is difference in HV R(0A), Y(40A) and B(0A) phase currents & HV neutral current of 40 A is recorded in p643 relay. The E/F relay setting current was 15A with 2Secs. time delay. Thus it is concluded that the protection system operation was intact. | [7 empty] | HV E/F operated
46 | 220KV-RAICHUR_KA-UPPER_JURALA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | TGTRANSCO | 14-04-2026 | 05:32 | KPTCL | Correct Operation | 220kV Jurala-1 line not tripped at our end but tripped on jurala end due to bus coupler issue |  |  | TGGENCO | Correct Operation | MAIN-1 BUSBAR DIFFERENTIAL PROTECTION |  |  | Tripped due to Bus coupler tripping
47 | 220KV-SABARIGIRI-PALLOM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 14-04-2026 | 16:40 | KSEB | Correct Operation | Delayed tripping |  |  | KSEB | Correct Operation | Fault in the bus isolator connection of 220kV Pallom-New Pallom-1 at New Pallom. Bus fault (B-G). BB protection at New Pallom was not operated. Fault in the 'out of zone' of pilot wire differential protection and so, backup protection of the New Pallom-Pallom feeder was operated. 220kV Sabarigiri-Pallom-1 tripped from remote end. |  |  | Trip
48 | 400KV/230KV SRIPERUMBADUR_TN-ICT-3 | TRANSFORMER | 400 | Intra | TANTRANSCO | 15-04-2026 | 13:38 | TANTRANSCO | Correct Operation | Buch Trip_For a simultaneous close-up line fault in the 230 kV NCTPS STG-1 feeder and the 230 kV Ctrl-S feeder, ICT-3 tripped due to actuation of the Yphase Buccholz relay trip, caused by heavy oil turbulence. | [7 empty] | TRIPPED ON BUCHHOLZ RELAY OPERATION
49 | 400KV-TUMKUR-DHARMAPURI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 14-04-2026 | 14:04 | PGCIL SR-2 | Correct Operation | Line tripped on Y -G fault. Autoreclose unsucessfull. Tumkur end details:M1: FLR: 3.3KA, FC: 178.8KM, M2: FLR: 2.58 KA, FC: 122.5KM. |  |  | PGCIL SR-2 | Correct Operation | Line tripped on Y -G fault. Dharmapuri end details: M1: FLR: 2.3ka, FC: 154.1 KM, M2: FLR: 2.33 ka, FC: 98.68KM. |  |  | TRIPPED ON Y-N FAULT
50 | 400KV-SURYAPET-KETHIREDDYPALLY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 13-04-2026 | 18:06 | TGTRANSCO | Correct Operation | Correcet operation |  |  | TGTRANSCO | Failure Operation | AR not operated | Non operation of AR will be checked | Pending | TRIPPED ON C-N FAULT
51 | 400KV-GAJWEL-CHANDALAPUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 14-04-2026 | 13:41 | TGTRANSCO | Correct Operation | Line is in service at Gajwelend. |  |  | TGTRANSCO | Unwanted Operation | I>3 operated | Disabled I>3 SOTF function on 28-04-2026 | Completed | A/R lockout
52 | 400KV-GAJWEL-CHANDALAPUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 14-04-2026 | 13:41 | TGTRANSCO | Correct Operation | Correcet operation |  |  | TGTRANSCO | Failure Operation | AR not operated | Disabled I>3 SOTF function on 28-04-2026 | Completed | TRIPPED ON B-N FAULT
53 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | TGTRANSCO | 16-04-2026 | 12:15 | APGENCO | Correct Operation | correct operation |  |  | TGGENCO | Correct Operation | Zone-1 Distance Protection operated |  |  | tripped on R-N Fault
54 | 220KV-HIRIYUR-INFOSYS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 15-04-2026 | 13:38 | PGCIL SR-2 | Correct Operation | Line tripped on Persisting fault in Line. |  |  | KPTCL |  |  |  |  | TRIPPED ON R-N FAULT
55 | 230KV-MAPS-ECHUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 15-04-2026 | 16:36 | NPCIL_MAPS | Correct Operation | Zone-1 protection operated for B-N fault |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | tripped on B-N fault Zone-1 protection.
56 | 220KV-PUNNAPRA-NEW PALLOM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | POWERGRID | 14-04-2026 | 16:40 | KSEB | Correct Operation | fault tripping |  |  | KSEB | Correct Operation | Fault in the bus isolator connection of 220kV Pallom-New Pallom-1 at New Pallom. Bus fault (B-G). BB protection at New Pallom was not operated. Fault in the 'out of zone' of pilot wire differential protection and so, backup protection of the New Pallom-Pallom feeder was operated. 220kV Punnapra-New Pallom-1 tripped from remote end. |  |  | Trip
57 | 220KV-IDDUKI-NEW PALLOM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 14-04-2026 | 16:40 | KSEB | Correct Operation | Delayed tripping |  |  | KSEB | Correct Operation | Fault in the bus isolator connection of 220kV Pallom-New Pallom-1 at New Pallom. Bus fault (B-G). BB protection at New Pallom was not operated. Fault in the 'out of zone' of pilot wire differential protection and so, backup protection of the New Pallom-Pallom feeder was operated. 220kV Idukki-New Pallom-1 tripped from remote end. |  |  | Trip
58 | 220KV-RAICHUR_KA-UPPER_JURALA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | KPTCL | 14-04-2026 | 05:32 | KPTCL | Correct Operation | 220kV Jurala-2 line not tripped at our end but tripped on jurala end due to bus coupler issue |  |  | TGGENCO | Correct Operation | MAIN-1 BUSBAR DIFFERENTIAL PROTECTION |  |  | Tripped due to Bus coupler tripping
59 | 400KV-HINDUJA-KALPAKKA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 16-04-2026 | 17:49 | HINDUJA | Correct Operation | DT Received |  |  | APTRANSCO | Unwanted Operation | unwanted operation | On 16/04/2026 at 17:49 Hrs., closing code were issued to 63MVar Bus reactor-3 and 125MVar Bus reactor- 4 vide 2938 and 2939. While charging of Bus reactor, Shift operator selected a wrong window (i.e. 400kV Kalapaka-HNPCL-1). Hence, trip command extended to CB of HNPCL-2 (402) feeder and Direct trip sent to remote end. REMEDIAL ACTION TAKEN: Superintending Engineer/400kV/OMC/Kalapaka informed that, strict instructions were issued to shift Engineers to avoid unwanted human errors and line trippings. | Completed | While charging of Bus reactors spurious signal of trip and close commands were extended to HNPCL-2 Bay(402) breaker from SAS causing tripping
60 | 220KV-KAYAMKULAM-NEW PALLOM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | POWERGRID | 14-04-2026 | 16:40 | NTPC | Correct Operation | Fault current in L3 1980A |  |  | KSEB | Correct Operation | Fault in the bus isolator connection of 220kV Pallom-New Pallom-1 at New Pallom. Bus fault (B-G). BB protection at New Pallom was not operated. Fault in the 'out of zone' of pilot wire differential protection and so, backup protection of the New Pallom-Pallom feeder was operated. 220kV Kayamkulam-New Pallom-1 tripped from remote end. |  |  | Trip
61 | 400KV-JINDAL-BPS-3 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 16-04-2026 | 15:18 | JSW_THERMAL | Unwanted Operation | Due to GPR issue |  | Pending | KPTCL | Correct Operation | Line tripped only at JSW end |  |  | TRIPPED ON EARTH FAULT
62 | 400KV-JINDAL-BPS-4 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 16-04-2026 | 15:18 | JSW_THERMAL | Correct Operation | relay operated as per the protection logic |  |  | KPTCL | Correct Operation | Correct Operation |  |  | TRIPPED ON EARTH FAULT
63 | 230KV-KALVENDAPATTU-SIRUSERI | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 18-04-2026 | 11:04 | PGCIL SR-2 | Correct Operation | Tripped on persisting fault- 9.4 km / 12.73 kA |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | attending jumper cut at loc92
64 | 400KV-PALAVADI-TIRUVALAM_TN-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 18-04-2026 | 05:17 | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR_At Loc No. 67 Tarpaulin fell over the tower line |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR_At Loc No. 67 Tarpaulin fell over the tower line |  |  | TRIPPED AND REASON AWAITED
65 | 230KV-KALVENDAPATTU-THARAMANI | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-04-2026 | 02:45 | PGCIL SR-2 | Correct Operation | Tripped on Persisting fault- 26.5 km / 5.39 kA |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TRIPPED DUE TO R-N FAULT
66 | 400KV/230KV PULIYANTHOPE-ICT-1 | TRANSFORMER | 400 | Intra | TANTRANSCO | 19-04-2026 | 05:32 | TANTRANSCO | Unwanted Operation | OLTC PRV Trip_Y phase OLTC PRV switch contacts sluggish | Both NO contact of PRV made series for PRV tripping | Completed | [5 empty] | OLTC Y phase tripped
67 | 132KV-KODADA-CHILLAKALLU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | TGTRANSCO | 20-04-2026 | 00:12 | TGTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation |  |  |  | RN fault
68 | 230KV-KUDANKULAM-TTPS | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-04-2026 | 05:42 | NPCIL_KKNP |  |  |  |  | TNPGCL | Correct Operation | TTPS - Kudankulam got tripped for Y - N fault, both ends got tripped. |  |  | TRIPPED ON Y-N FAULT
69 | 230KV-TIRUNELVELI-UDAYATHOOR | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-04-2026 | 14:43 | PGCIL SR-2 | Correct Operation | Tripped on Persisting Fault - 17.5 km / 5.6 kA |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | Line patrol done & No visible fault
70 | 220KV-HASSAN-GOPALPURA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 20-04-2026 | 20:16 | PGCIL SR-2 | Correct Operation | Line was HT from Gopalpura end due to Current Discrepancy . No |  |  | KPTCL |  |  |  |  | Line Hand Tripped @ Gopalpuraa Suzzlon end
71 | 132KV-MADIRA-CHILLAKALLU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | APTRANSCO | 21-04-2026 | 07:17 | TGTRANSCO |  |  |  |  | APTRANSCO | Correct Operation |  |  |  | TRIPPED ON B-N FAULT
72 | 400KV/220KV GUTTUR-ICT-1 | TRANSFORMER | 400 | Intra | KPTCL | 19-04-2026 | 01:16 | KPTCL | Unwanted Operation | Nil | Damaged TCIV and air cell to be replaced, PO placed, supply of materials awaited | Pending | [5 empty] | Buchholz Relay Operated
73 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | TGTRANSCO | 18-04-2026 | 12:04 | APGENCO | Correct Operation | correct operation |  |  | TGGENCO | Correct Operation | Zone-1 Distance Protection operated |  |  | R_N Fault
74 | 765KV-KURNOOL_PG-CUDDAPAH-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Intra | POWERGRID | 19-04-2026 | 18:01 | PGCIL SR-1 | Correct Operation | Line Converter to LVRD |  |  | PGCIL SR-1 | Correct Operation | na |  |  | Tripped on Over Voltage
75 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | TGTRANSCO | 21-04-2026 | 14:19 | APGENCO | Correct Operation | cerrect operation |  |  | TGGENCO | Correct Operation | Zone-1 Distance Protection operated |  |  | AP: Z-1, B-N, 30.8 kms, 3.11 kA; TS:Z-1, B-N, 54.4 Kms, 2.8 kA
76 | 400KV-KURNOOL_PG-NAGARJUNASAGAR_PG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 18-04-2026 | 18:02 | PGCIL SR-1 | Correct Operation | NA |  |  | PGCIL SR-1 | Correct Operation | NA |  |  | Tripped on Over Voltage
77 | 220KV-RAICHUR_KA-UPPER_JURALA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | KPTCL | 21-04-2026 | 20:52 | KPTCL | Correct Operation | Main1: Tripped on DPR, Zone1, RYB, L=0.5273KMS, R-phase Main2: Tripped on DPR, Zone1, RYB, AR Lockout shot, Fault duration=86.58ms, Relay trip time=86.25ms, Fault location=1.064KM, Ia=13.84kA, Ib=19.38A, Ic=21.86A, Fault Resistance=1.808 ohms Generation is at Telangana side and breaker & isolator is at open condition at jurala end so no tripping at jurala end. |  |  | TGGENCO | Correct Operation | NA |  |  | TRIPPED ON R-N FAULT
78 | 400KV-KAIGA-GUTTUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 20-04-2026 | 20:25 | NPCIL_KAIGA | Correct Operation | 400KV, Kaiga-Guttur line-2 R-phase Zone-1(main-1)/Zone-2(main-2) Distance protection operated. |  |  | KPTCL | Correct Operation | AR lockout initiated |  |  | TRIPPED ON R-N FAULT
79 | 400KV-ENNORE SEZ-SUNGAVARACHATRAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 21-04-2026 | 16:36 | TANTRANSCO | Correct Operation | ZONE.1,R,N,DT RECEIVED |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | SVCHATRAM: B-N, Z-1, SOTF, 2.9 Kms, 20.8 kA; ESEZ: B-N, Z-3, 2.625 KA, 94.53 Kms
80 | 220KV-ASUPAKA-LOWER_SILERU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 21-04-2026 | 13:37 | TGTRANSCO | Correct Operation | Correcet operation |  |  | APGENCO | Failure Operation | Relay sensed the fault in Zone2 but AR not operated due to non receipt of carrier signal from remote end. | Sending and receiving from PLC panel to relay panel internally checked and found ok. End to end to be checked , the same was intimated to TGTRANSCO for end to end checks. | Pending | Tripped on r-n fault, 1.73kA
81 | 400KV-JINDAL-BPS-4 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 21-04-2026 | 15:14 | JSW_THERMAL | Unwanted Operation | unwanted tripping due to GPR |  | Pending | KPTCL | Correct Operation | Line was holding at BPS end |  |  | No relay indication, breaker in open condition
82 | 220KV-ASUPAKA-LOWER_SILERU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 21-04-2026 | 22:08 | TGTRANSCO | Correct Operation | Line is in service at Asupaka end. |  |  | APGENCO | Failure Operation | DUE TO FAILURE OF R- PHASE LIMB OF BUS COUPLER. | Bus Coupler Faulty R-phase breaker limb removed from the structure and Limb replaced | Completed | LBB operated at Lower Sileru
83 | 765KV/400KV RAICHUR_PG-ICT-2 | TRANSFORMER | 765 | Intra | PGCIL SR-1 | 21-04-2026 | 18:32 | PGCIL SR-1 | Unwanted Operation | HV Neutral OC operated | Firmware issue was rectified | Completed | [5 empty] | Tripped
84 | 400KV-BPS-YTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 21-04-2026 | 19:15 | KPTCL | Correct Operation | Correct Operation |  |  | KPCL | Correct Operation | Correct relay operation |  |  | BPS: Z-1, R-N, 152 Kms, 2.9 kA; YTPS: Z-1, R-N, 11.01 Kms, 11.7 kA
85 | 400KV-KAYATHAR-KANARPATTI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 20-04-2026 | 13:30 | TANTRANSCO | Unwanted Operation | LBB trip |  |  | TANTRANSCO | Correct Operation | DT received |  |  | Reason awaited
86 | 220KV-KOTHAGUDEM_TPS-TIRUVURU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 20-04-2026 | 15:04 | TGGENCO | Correct Operation | Trip A,N; zone-1; 18.11KM; AR Lockout optd |  |  | APTRANSCO | Correct Operation | AR Successful at Tiruvuru End |  |  | tripped on R-N Fault
87 | 400KV-TUMKUR-KUDGI_PG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KTL | 21-04-2026 | 17:02 | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | TRIPPED DUE TO R-N FAULT
88 | 400KV-CUDDAPAH-NAGARJUNASAGAR_PG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 22-04-2026 | 18:04 | PGCIL SR-1 | Correct Operation | AR attempted and tripped on persisting Y-Gnd fault. |  |  | PGCIL SR-1 | Correct Operation | AR attempted and tripped on persisting Y-Gnd fault. |  |  | TRIPPED ON Y-N FAULT
89 | 400KV/33KV GREENKO_PSS1-ICT-1 | TRANSFORMER | 400 | Intra | GREENKO | 22-04-2026 | 07:40 | GREENKO | Unwanted Operation | ICT-1 LV-2 REF Operated | Checked and found 33kv side Bay-310 feeder (P-6 B-5,6,7) Incomer CB got tripped due to Over current stage-2 fault due to monkey hit at Pole no-P-6 F#310 Same was rectified (Checked Pin Insulator healthiness megger done Insulators cleaning also carried out- Relay Settings checked found as per recommended. Test charged Stood Ok found all are normal | Completed | [5 empty] | TRIPPED ON EARTH FAULT
90 | 220KV-CHITTOOR_AP-THIRUVALAM_TN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | TANTRANSCO | 22-04-2026 | 13:43 | APTRANSCO | Correct Operation | correct operation |  |  | TANTRANSCO | Correct Operation | ZONE.1,AR Successful & Lock out due to subsequent fault |  |  | B-N, Z-1, 17.45 Kms, 2.569 kA
91 | 400KV-DONI-MUNIRABAD-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 22-04-2026 | 08:52 | KPTCL | Correct Operation | as per protection policy |  |  | PGCIL SR-1 | Correct Operation | A/R attempted and tripped on persisting fault |  |  | tripped on R-N Fault
92 | 220KV-MYSORE-TUBINAKERE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 23-04-2026 | 03:50 | PGCIL SR-2 | Correct Operation | Tripped on persisting fault- Bph-G. 39.4 km / 4.4 kA |  |  | KPTCL |  |  |  |  | TRIPPED ON DISTANCE PROTECTION
93 | 400KV-MANALI-PULIYANTHOPE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 24-04-2026 | 03:58 | TANTRANSCO | Correct Operation | ZONE.1,B,N,LOCKOUT_At loc.21, Yph and Bph suspension insulator flashover |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N LOCKOUT_At loc.21, Yph and Bph suspension insulator flashover |  |  | Tripped
94 | 400KV-KALPAKKA-ASUPAKA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | APTRANSCO | 23-04-2026 | 11:58 | APTRANSCO | Correct Operation | correct operation |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | TRIPPED ON B-N FAULT
95 | 400KV-GAJWEL-CHANDALAPUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 26-04-2026 | 13:22 | TGTRANSCO | Correct Operation | Line is in service at Gajwel end. |  |  | TGTRANSCO | Unwanted Operation | spurious tripping | Disabled I>3 SOTF function on 28-04-2026 | Completed | tripped on RYB fault
96 | 220KV-KOLAR_AC-CHINTAMANAI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 25-04-2026 | 06:54 | PGCIL SR-2 | Correct Operation | Tripped on Rph-Yph Fault - 5.6 km / 12.24 kA |  |  | KPTCL |  |  |  |  | tripped on RY fault
97 | 400KV-CUDDAPAH-CHITTOOR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 23-04-2026 | 14:15 | PGCIL SR-1 | Correct Operation | Tripped on Y-Gnd fault. |  |  | APTRANSCO | Correct Operation | Tripping is in correct order. AR not operated due to - Auto Reclose kept in OFF condition on 23.04.2026 at 10.45Hrs due to PGCIL work - Hotline stringing work. |  |  | tripped on YN fault
98 | 400KV-KHAMMAM_PG-WARANGAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 26-04-2026 | 11:55 | PGCIL SR-1 | Correct Operation | NIL |  |  | PGCIL SR-1 | Correct Operation | NIL |  |  | BN fault
99 | 400KV-GAZUWAKA-KALPAKKA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 26-04-2026 | 03:53 | PGCIL SR-1 | Correct Operation | A/R attempted and tripped on persisting R-N fault |  |  | APTRANSCO | Correct Operation | line tripped on fault in reclaim time |  |  | TRIPPED DUE TO R-N FAULT
100 | 400KV-CUDDAPAH-NAGARJUNASAGAR_PG-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 23-04-2026 | 14:15 | PGCIL SR-1 | Correct Operation | Tripped on B-Gnd fault. |  |  | PGCIL SR-1 | Correct Operation | Tripped on B-Gnd fault. |  |  | TRIPPED ON B-N FAULT
101 | 220KV-KOTHAGUDEM_TPS-TIRUVURU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 24-04-2026 | 10:49 | TGGENCO | Correct Operation | Trip A,N; Z1;60.71km; AR Lockout optd |  |  | APTRANSCO | Correct Operation | AR Successful at Tiruvuru end. |  |  | TRIPPED DUE TO R-N FAULT
102 | 220KV-CHIKKODI-TALANGADE | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | MAHATRANSCO | 23-04-2026 | 22:10 | KPTCL | Unwanted Operation | test charged stood ok | [7 empty] | B-PH FAULT
103 | 220KV-NARENDRA-GHATPRABHA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 24-04-2026 | 15:14 | PGCIL SR-2 | Correct Operation | AR Successful @ Narendra end 25.57 km / 5.14 KA |  |  | KPTCL |  |  |  |  | TRIPPED ON B-N FAULT
104 | 400KV/220KV TALGUPPA-ICT-2 | TRANSFORMER | 400 | Intra | KPTCL | 23-04-2026 | 17:37 | KPTCL | Unwanted Operation | unwanted operations | DC source mixing issue attended | Completed | [5 empty] | DC source-1 and source-2 mixed in PRV HV and PRV LV side which leads to false tripping
105 | 400KV-KOLAR_AC-MYLASANDRA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 25-04-2026 | 16:05 | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | KPTCL | Correct Operation | Tripped on DPR |  |  | TRIPPED AND REASON AWAITED
106 | 400KV-CUDDAPAH-NAGARJUNASAGAR_PG-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 24-04-2026 | 14:22 | PGCIL SR-1 | Correct Operation | nil |  |  | PGCIL SR-1 | Correct Operation | nil |  |  | TRIPPED ON Y-N FAULT
107 | 400KV-JINDAL-RAJAPURA_S-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 16-04-2026 | 15:18 | JSW_THERMAL | Correct Operation | others |  |  | JSW_RE |  |  |  |  | Trip
108 | 400KV-SIMHADRI-KALPAKKA-3 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 26-04-2026 | 03:54 | NTPC_SIMHADRI | Correct Operation | Correct operation |  |  | APTRANSCO | Correct Operation | correct operation |  |  | TRIPPED ON Y-N FAULT
109 | 400KV-GAJWEL-CHANDALAPUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 26-04-2026 | 13:22 | TGTRANSCO | Correct Operation | Line is in service at Gajwel end. |  |  | TGTRANSCO | Unwanted Operation | spurious tripping | Disabled I>3 SOTF function on 28-04-2026 | Completed | tripped on RYB fault
110 | 420KV/21KV NCTPS_STAGE_II-GT-5 | TRANSFORMER | 420 | Intra | TANGEDCO | 26-04-2026 | 08:11 | TNPGCL | Correct Operation | NIL | [7 empty] | TRIPPED ON EARTH FAULT
111 | 765KV-KURNOOL_PG-CUDDAPAH-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Intra | POWERGRID | 26-04-2026 | 18:00 | PGCIL SR-1 | Correct Operation | NIL |  |  | PGCIL SR-1 | Correct Operation | nil |  |  | Tripped on Over Voltage
112 | 765KV-NIZAMABAD-WARDHA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Inter | POWERGRID | 26-04-2026 | 18:01 | PGCIL SR-1 | Correct Operation | NIL | [7 empty] | Tripped on Over Voltage
113 | 220KV-SOMASAMUDRA-REGULAPADU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 26-04-2026 | 13:42 | KPTCL | Correct Operation | nill |  |  | APTRANSCO | Correct Operation | B-N fault, Zone-1. AR operated & again tripped on persistent fault |  |  | bph fault
114 | 400KV-MANALI-PULIYANTHOPE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 06-04-2026 | 05:20 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | Trip
115 | 220KV-IDDUKI-KALAMASSERY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 03-04-2026 | 18:09 | KSEB | Correct Operation | AR AND TRIPPED |  |  | KSEB | Correct Operation | AR AND TRIPPED |  |  | M1:Trip Phase A ,Phase C,Zone1 trip, N/G, PUTT trip, CARRIER SENT, carrier received M2:Zone 1 trip,14.5KM,Rph trip,Bph trip,start phase ACN, Tripped phase ABC Realy optd: 86LO
116 | 400KV-GAJWEL-NARSAPUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 26-04-2026 | 13:22 | TGTRANSCO | Correct Operation | Correcet operation |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | TRIPPED ON B-N FAULT
117 | 220KV-RAICHUR_KA-UPPER_JURALA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | KPTCL | 26-04-2026 | 16:22 | KPTCL | Correct Operation | Main-1: Tripped on Zone-1, ABC phase fault locator L=1.695KM, Fault resistance X=0.5469 ohms, A=1.451 ohms, phase B, phase C, Master trip relay 86. Main-2: Tripped on Y, B phase fault locator L=AR Lockout shot, Fault duration=86.61ms, Tripped time=79.95ms, Ia=175.6A, Ib=12.15kA, Ic=0A, Master trip 86. AR not operated as generation is at telangana side and the isolator is in open condition at jurala end. |  |  | TGGENCO | Correct Operation | L2-L3 fault, ZONE-1 |  |  | DPR, RYB Ph fault
118 | 400KV/33KV AMGEPL_SOLAR-ICT-2 | TRANSFORMER | 400 | Intra | AMGEPL | 27-04-2026 | 09:04 | AMGEPL | Correct Operation | Tripped on LBB | [7 empty] | LBB OPERATED
119 | 400KV-KHAMMAM_PG-ASUPAKA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 27-04-2026 | 13:17 | PGCIL SR-1 | Correct Operation | NIL |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | bph fault
120 | 220KV-IDDUKI-KALAMASSERY-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 03-04-2026 | 18:09 | KSEB | Correct Operation | MULTI PHASE FAULT.AR AND TRIPPED |  |  | KSEB | Correct Operation | MULTI PHASE FAULT.AR AND TRIPPED |  |  | M1: Phase A ,Phase C,Zone1 trip, N/G, PUTT trip CARRIER SENT M2:Zone 1 trip,14.11KM,Rph fault,Bph fault,start phase ACN, Tripped phase ABC Realy optd: 86LO
121 | 220KV-LOWER PERIYAR-IDDUKI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 03-04-2026 | 17:02 | KSEB | Correct Operation | AR OPTD |  |  | KSEB | Correct Operation | AR OPTD |  |  | AR OPERATED
122 | 220KV-ALUVA-Pallivasal-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 03-04-2026 | 17:19 | KSEB | Correct Operation | AR OPTD |  |  | KSEB | Correct Operation | AR OPTD |  |  | AR OPERATED
123 | 220KV-EDAMON-POTHENCODE-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 10-04-2026 | 12:39 | KSEB | Correct Operation | B Ph and C Ph tree felling and Tripped correctly with indication,Autoreclosure operated but not successful |  |  | KSEB | Correct Operation | B Ph and C Ph tree felling and Tripped correctly with indication,Autoreclosure operated but not successful |  |  | Ann: M1 M2 DP optd M1:DP:Y-B,Z1,16.34km,L2-L3 M2:DP:Y-B,Z1,16.37,L2-L3
124 | 220KV-WANAPARTHY-BRAMHANA_KOTKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 27-04-2026 | 18:18 | TGTRANSCO | Correct Operation | Correcet operation |  |  | APTRANSCO | Correct Operation | found ok |  |  | TRIPPED ON Y-N FAULT
125 | 220KV-ALUVA-KOTHAMANGALAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 19-04-2026 | 16:55 | KSEB | Correct Operation | "Ann: M1 M2 DP optd, Carrier send, carrier received M1:DP:A-N,Z1,19.8km M2:DP:A-N,Z1,23.8km".AR lockout. |  |  | KSEB | Correct Operation | "Ann: M1 M2 Diff protn optd, 86.1 & 86.2 relay optd M1 :Diff:R-N,Z1,10.7km M2:Diff:R-N,Z1,---"AR lockout. |  |  | Ann: M1 M2 Diff protn optd, 86.1 & 86.2 relay optd M1 :Diff:R-N,Z1,10.7km M2:Diff:R-N,Z1,---
126 | 220KV-BRAHMPURAM-LOWER PERIYAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 19-04-2026 | 16:21 | KSEB | Correct Operation | "Ann: M1 M2 DP optd M1:DP:C-N,Z1,51.16km M2:DP:B ph,Z1,45.6km,carrier aided trip, carrier send, carrier received".AR lockout. |  |  | KSEB | Correct Operation | "Ann: M1 M2 DP optd, SOTF, AR optd M1:DP:B ph,Z1,28.99km M2:DP:B ph,Z1,29.792km" |  |  | Ann: M1 M2 DP optd, SOTF, AR optd M1:DP:B ph,Z1,28.99km M2:DP:B ph,Z1,29.792km
127 | 220KV-BRAHMPURAM-LOWER PERIYAR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 19-04-2026 | 16:34 | KSEB | Correct Operation | "Ann: M1 M2 DP optd M1:DP:C-N,Z2,48.79km M2:DP:B ph,Z2,48.7km" Rlockout |  |  | KSEB | Correct Operation | "Ann: M1 M2 DP optd, AR optd M1:DP:B ph,Z1,8.49km M2:DP:B ph,Z1,8.96km" AR lockout. |  |  | Ann: M1 M2 DP optd, AR optd M1:DP:B ph,Z1,8.49km M2:DP:B ph,Z1,8.96km
128 | 400KV-TIRUNELVELI-KOTTAYAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | KSEB | 19-04-2026 | 18:10 | PGCIL SR-2 | Correct Operation | AR Successful. 1678km/2.4 kA |  |  | KSEB | Correct Operation | Z1, Y-phase fault |  |  | AR OPERATED
129 | 400KV-TUMKUR-KUDGI_PG-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KTL | 29-04-2026 | 01:26 | PGCIL SR-2 | Correct Operation | Protection scheme operated correct. |  |  | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | TRIPPED ON R-Y FAULT
130 | 220KV-THENI-SABARIGIRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | KSEB | 27-04-2026 | 13:44 | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR_Banana palm leaves charred out and fault cleared b/n loc 186-187 |  |  | KSEB | Correct Operation | fault tripping |  |  | tripped on R-N Fault
131 | 220KV-EDAMON-SABARIGIRI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 20-04-2026 | 17:13 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation | AR OPERATED,Z1 FAULT |  |  | AR OPERATED
132 | 220KV-EDAMON-SABARIGIRI-3 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 20-04-2026 | 17:19 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation | AR OPERATED,Z1 FAULT |  |  | AR OPERATED
133 | 220KV-KOTHAMANGALAM-Pallivasal-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 20-04-2026 | 15:55 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
134 | 220KV-SABARIGIRI-PALLOM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 21-04-2026 | 17:56 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
135 | 220KV-EDAMON-SABARIGIRI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 21-04-2026 | 15:59 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation | AR OPERTED,Z1 FAULT |  |  | AR OPERATED
136 | 220KV-EDAMON-SABARIGIRI-3 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 21-04-2026 | 15:59 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation | AR OPERATED,Z1 FAULT |  |  | AR OPERATED
137 | 220KV-EDAPPON-PATHANAMTHITTA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 21-04-2026 | 17:00 | KSEB | Failure Operation | Differential trip due to R-ph fault. The relay tripped correctly but didn't Autoreclose as the CB ready signal didnt recieved. | The Contactor in the CB has been rectified. | Completed | KSEB | Correct Operation | Differential trip due to R-ph fault. The relay tripped correctly and Autoreclosed successfully. |  |  | M1: DIFF: R ph trip, Diff inter trip, E/F trip, Z2-Z3, 20.1KM M2: Diff : R ph trip, Start ph A-N, Trip A-N, Z2-Z3, 21.1KM
138 | 220KV-LOWER PERIYAR-IDDUKI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 21-04-2026 | 17:45 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
139 | 220KV-LOWER PERIYAR-IDDUKI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 21-04-2026 | 17:45 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
140 | 220KV-LOWER PERIYAR-IDDUKI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 21-04-2026 | 17:39 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
141 | 220KV-LOWER PERIYAR-IDDUKI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 21-04-2026 | 17:39 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
142 | 220KV-LOWER PERIYAR-MADAKATHARA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 26-04-2026 | 17:27 | KSEB | Correct Operation | DISC FLASH AT LOC.155 |  |  | KSEB | Correct Operation | DISC FLASH AT LOC.155 |  |  | Conductor snapping, Ann: M1 DP & M2 DP optd, AR optd, PT Fuse fail M1: DP: Fault C-G, Z1, 76.133km, 74.633% M2: DP: P5 Bph, P4 SOTF/TOC, Z1, 40.06km, 39.270%
143 | 220KV-ASUPAKA-LOWER_SILERU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 28-04-2026 | 11:42 | TGTRANSCO | Failure Operation | AR not operated | Proposed to replace Main-1 D6o relay | Pending | APGENCO | Correct Operation | THE 220 KV LS-ASPK FEEDER GOT TRIPPED AT BOTH ENDS . |  |  | TRIPPED ON R-N FAULT
144 | 220KV-PUNNAPRA-NEW PALLOM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | POWERGRID | 28-04-2026 | 17:58 | KSEB | Correct Operation | The relay tripped in single ph R-N fault. Later an evolving fault was detected by the relay in Bph and went to lockout. |  |  | KSEB | Correct Operation | Autoreclose at New Pallom |  |  | tripped on R-N Fault
145 | 400KV-GOOTY-RAICHUR_PG-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 21-04-2026 | 18:36 | PGCIL SR-1 | Correct Operation | A/R sucessful R-N fault |  |  | PGCIL SR-1 | Correct Operation | A/R sucessful R-N fault |  |  | Trip
146 | 230KV-KUDANKULAM-TTPS | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 29-04-2026 | 06:44 | NPCIL_KKNP |  |  |  |  | TNPGCL |  |  |  |  | TRIPPED ON Y-N FAULT
147 | 400KV-JINDAL-BPS-3 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 29-04-2026 | 00:12 | JSW_THERMAL | Unwanted Operation | others |  |  | KPTCL | Unwanted Operation | The line did not trip at BPS end |  |  | Breaker Maloperation
148 | 765KV-KURNOOL_PG-MAHESHWARAM_PG-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Inter | POWERGRID | 28-04-2026 | 18:03 | PGCIL SR-1 | Correct Operation | Tripped on R-Y fault |  |  | PGCIL SR-1 | Correct Operation | Tripped on R-Y fault |  |  | r-y FAULT, If =14.5 kA
149 | 220KV-HASSAN-GOPALPURA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 28-04-2026 | 20:34 | PGCIL SR-2 | Correct Operation | AR Successful @ hassan end |  |  | KPTCL |  |  |  |  | TRIPPED ON Y-N FAULT
150 | 400KV-KAIGA-GUTTUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 28-04-2026 | 11:02 | NPCIL_KAIGA | Correct Operation | Kaiga Guttur Line-1 CB tripped due to receipt of D/T signal from PLCC |  |  | KPTCL | Correct Operation | Nil |  |  | DIRECT TRIP RECEIVED
151 | 220KV-GADAG_PSS-Green Infra_GadagPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | GADAG_II_A | 29-04-2026 | 04:40 | GTL | Correct Operation | The protection system was operated correctly, isolated the faulted section. |  |  | GREENINFRA | Correct Operation | No |  |  | RN fault
152 | 400KV-GOOTY-NPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 29-04-2026 | 10:51 | PGCIL SR-1 | Correct Operation | nil |  |  | PGCIL SR-1 | Correct Operation | nil |  |  | TRIPPED ON B-N FAULT
153 | 220KV-GADAG_PSS-Vena_GadagPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | Vena_GadagPS | 29-04-2026 | 05:24 | GTL | Correct Operation | Fault Tripping |  |  | Vena_GadagPS | Correct Operation | YN fault__Zone1 operated |  |  | tripped on YN fault
154 | 400KV-BPS-YTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 29-04-2026 | 02:11 | KPTCL | Correct Operation | Correct Operation |  |  | KPCL | Correct Operation | Correct relay operation |  |  | RN fault
155 | 400KV-TIRUNELVELI-KOTTAYAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 28-04-2026 | 17:15 | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct- AR Successful @ Tirunelveli end. |  |  | KSEB | Correct Operation | fault tripping |  |  | TRIPPED ON B-N FAULT
156 | 765KV-KURNOOL_PG-CUDDAPAH-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Intra | POWERGRID | 28-04-2026 | 18:02 | PGCIL SR-1 | Correct Operation | Tripped on Over Voltage |  |  | PGCIL SR-1 | Correct Operation | Tripped on Over Voltage Stage-I |  |  | Tripped on Over Voltage
157 | 400KV/110KV VELLALAVIDUTHI-ICT-1 | TRANSFORMER | 400 | Intra | TANTRANSCO | 29-04-2026 | 00:37 | TANTRANSCO | Correct Operation | Inst Earthfault protection operated | [7 empty] | Tripped along with 110 kV Karmbakudy feeder. Details awaited
158 | 400KV-OTTAPIDARAM-UDANGUDI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 29-04-2026 | 12:57 | TANTRANSCO | Correct Operation | DT recived from udangudi end due to Tie Bay LBB Acted. |  |  | TNPGCL | Correct Operation | Relay fault tripped due to Single line to Ground Fault. |  |  | TRIPPED ON B-N FAULT
159 | 400KV-OTTAPIDARAM-UDANGUDI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 29-04-2026 | 12:57 | TANTRANSCO | Correct Operation | DT recived from plant end due to Tie Bay LBB Acted. |  |  | TNPGCL | Failure Operation | Since there is No fault in Ottapidaram Line-2 feeder, 3 Phase unnecessary external trip has been initiated from LBB relay in Tie panel for a single phase to ground fault in Ottapidaram Line 1 Feeder. |  | Pending | TRIPPED ON B-N FAULT
160 | 400KV-OTTAPIDARAM-THENNAMPATTY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 29-04-2026 | 13:50 | TANTRANSCO | Failure Operation | ZONE.1,R,N LOCKOUT TRIP | M2 Relay Issued 3pole trip after 30 msec. AR scheme checked in next Lc. | Pending | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR Successful |  |  | TRIPPED ON R-N FAULT
161 | 220KV-IDDUKI-NEW PALLOM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 29-04-2026 | 15:43 | KSEB | Correct Operation | AR AND TRIPPED |  |  | KSEB | Correct Operation | Trip on reclose at New Pallom |  |  | M1: TRIP,PHASE C,NEUTRAL GROUND,ZONE 1 TRIP,B PHASE FAULT M2: ZONE 1 TRIP,B PHASE FAULT,carrier send,carrier receive,VTfuse fail alarm,CARR AID tripActive grp2,STARTED PHASE CN,TRIPPED PHASE ABC, Start element -distance,location-9.866km.
162 | 400KV-JINDAL-BPS-4 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 29-04-2026 | 00:12 | JSW_THERMAL | Unwanted Operation | others |  | Pending | KPTCL | Correct Operation | Line tripped only at JSW end |  |  | Breaker Maloperation
163 | HVDC 800KV RAIGARH HVDC Pole 4 | HVDC POLE | HVD | Intra | POWERGRID | 28-04-2026 | 18:04 | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. | [7 empty] | tripped on differential protection
164 | HVDC 800KV RAIGARH HVDC Pole 3 | HVDC POLE | HVD | Intra | POWERGRID | 28-04-2026 | 18:04 | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. | [7 empty] | tripped on differential protection
165 | 220KV-ASUPAKA-LOWER_SILERU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 17-04-2026 | 20:54 | TGTRANSCO | Correct Operation | AR OPERATED SUCESSFULLY |  |  | APGENCO | Correct Operation | Auto Reclosure successful |  |  | TRIPPED ON Y-N FAULT
166 | 400KV-NAGARJUNASAGAR_PG-MEHBOOBNAGAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 15-04-2026 | 00:02 | PGCIL SR-1 | Correct Operation |  |  |  | TGTRANSCO | Correct Operation | AR operated |  |  | TRIPPED ON R-N FAULT
167 | 400KV-KALPAKKA-ASUPAKA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | APTRANSCO | 30-04-2026 | 12:46 | APTRANSCO | Correct Operation | correct operation |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | TRIPPED ON R-Y FAULT
168 | 400KV-KALPAKKA-KHAMMAM_PG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | APTRANSCO | 30-04-2026 | 11:50 | APTRANSCO | Correct Operation | correct operation |  |  | PGCIL SR-1 | Correct Operation | Tripped on Y-B fault |  |  | Tripped on Y-B Fault
169 | 400KV-KOLAR_AC-HOODY-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 29-04-2026 | 20:07 | PGCIL SR-2 | Correct Operation | 400KV-KOLAR_AC-HOODY-2 tripped at 29-04-2026 20:07 due to B-G fault. Auto reclose attempted but tripped due to a persistent fault. |  |  | KPTCL | Failure Operation | Due to DTPC both the channel failure in Line-2 AR not attempted , the same was attended by Power grid on 30.04.2026 | Attended by Powergrid | Completed | bph fault
170 | 220KV-AMBALAMUGAL-SABARIGIRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 29-04-2026 | 15:36 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
171 | 220KV-MYSORE-K R PET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 30-04-2026 | 22:13 | PGCIL SR-2 | Correct Operation | AR Successful @ Mysore end. 12.04 kM / 9.43 kA |  |  | KPTCL |  |  |  |  | TRIPPED ON R-N FAULT
172 | 220KV-ETUMANOOR-KOTTAYAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 28-04-2026 | 09:06 | KSEB | Correct Operation | Support insulator flased (C-phase) in the yard of 220kV GIS ETTUMANOOR |  |  | KSEB | Correct Operation | Support insulator flased (C-phase) in the yard of 220kV GIS ETTUMANOOR |  |  | ANN: DP, Diff, SOTF M1: DP: Start ph BC-N, Trip ph C-N, Z2-Z3, 8.833KM
173 | 220KV-CHILLAKALLU-PULICHINTALA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | TGTRANSCO | 30-04-2026 | 13:16 | APTRANSCO | Correct Operation |  |  |  | TGGENCO | Correct Operation | Fault tripping |  |  | tripped on R-N Fault
174 | 220KV-EDAMON-SABARIGIRI-3 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 29-04-2026 | 14:29 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation | AR OPERTED,Z1 FAULT |  |  | AR OPERTED,Z1 FAULT
175 | 400KV-MALKARAM-SURYAPET-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 30-04-2026 | 21:54 | TGTRANSCO | Correct Operation | AR operated |  |  | TGTRANSCO | Correct Operation | AR operated |  |  | TRIPPED ON B-N FAULT
176 | 220KV-EDAMON-SABARIGIRI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 29-04-2026 | 14:29 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation | AR OPERTED |  |  | AR OPERATED
177 | 400KV-GAJWEL-NARSAPUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 23-04-2026 | 16:37 | TGTRANSCO | Correct Operation | AR operated |  |  | TGTRANSCO | Correct Operation | A/R operated |  |  | TRIPPED ON Y-N FAULT
178 | 400KV-URAVAKONDA-MEHBOOBNAGAR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | TGTRANSCO | 20-04-2026 | 02:49 | APTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation | AR operated |  |  | TRIPPED ON B-N FAULT
179 | 220KV-AMBALAMUGAL-SABARIGIRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 29-04-2026 | 14:33 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation | MULTI PHASE FAULT .CHECK SYNCH NOT OK. |  |  | M1: PICKUP R, PICKUP Y, PICKUP B, L1 L2 -E, 6.2KM M2: PICKUP R, PICKUP Y, PICKUP B, PICKUP E, L1 L2 -E, 6.3KM
180 | 220KV-AMBALAMUGAL-SABARIGIRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 29-04-2026 | 15:25 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
181 | 220KV-SABARIGIRI-PALLOM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 29-04-2026 | 15:25 | KSEB | Correct Operation | CHECK SYNCH NOT READY |  |  | KSEB | Correct Operation | Autoreclose at Pallom |  |  | M1: PICKUP R, PICKUP Y, PICKUP E, Z1, AIDED TRIP, L1-E, 22.4KM M2: PICKUP R, PICKUP Y, PICKUP E, Z1, 22.6KM
182 | 220KV-SABARIGIRI-PALLOM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 29-04-2026 | 15:36 | KSEB | Correct Operation | AR OPTD |  |  | KSEB | Correct Operation | Trip on reclose at Pallom |  |  | AR OPERATED
183 | 220KV-AMBALAMUGAL-SABARIGIRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 29-04-2026 | 16:26 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
184 | 220KV-SABARIGIRI-PALLOM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 29-04-2026 | 16:26 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
185 | 220KV-IDDUKI-KALAMASSERY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 29-04-2026 | 17:02 | KSEB | Correct Operation | AR AND LO.SOTF |  |  | KSEB | Correct Operation | SOTF |  |  | M1: TRIP,PHASE A,NEUTRAL GROUND,ZONE 1 TRIP,R PHASE FAULT M2: ZONE 1 TRIP,PUTT TRIP,R PHASE FAULT,carrier send,carrier receive,VTfuse fail alarm,CARR AID tripActive grp2,STARTED PHASE AN,TRIPPED PHASE A, Start element -distance,,location-31.62km.
186 | 400KV-OTTAPIDARAM-UDANGUDI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 30-04-2026 | 14:24 | TANTRANSCO | Correct Operation | ZONE.1,B,N_ DT received_Loc no 39,40,52,53,94 and 95 Tree clerance |  |  | TNPGCL | Correct Operation | Relay fault tripped due to Single line to Ground Fault. |  |  | TRIPPED ON B-N FAULT
187 | 400KV-VTPS_IV-THALLAYAPALEM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 30-04-2026 | 17:42 | APGENCO | Correct Operation | No tripping at VTPS end |  |  | APTRANSCO | Unwanted Operation | Mal operation due to DC disturbance | DC Contactor failed to operate during DC change over. Wiring modification done to avoid further trippings. | Completed | maloperation due to failure of DC set -1
188 | 400KV-OTTAPIDARAM-UDANGUDI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 30-04-2026 | 14:24 | TANTRANSCO | Correct Operation | DT RECEIVED |  |  | TNPGCL | Failure Operation | Since there is No fault in Ottapidaram Line-2 feeder, 3 Phase unnecessary external trip has been initiated from LBB relay in Tie panel for a single phase to ground fault in Ottapidaram Line 1 Feeder. |  | Pending | Tripped. No relay indication reported.
189 | 220KV-IDDUKI-NEW PALLOM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 29-04-2026 | 16:43 | KSEB | Correct Operation | AR AND TRIPPED |  |  | KSEB | Correct Operation |  |  |  | M1: TRIP,PHASE C,NEUTRAL GROUND,ZONE 1 TRIP,B PHASE FAULT M2: ZONE 1 TRIP,B PHASE FAULT,carrier send,carrier receive,VTfuse fail alarm,CARR AID tripActive grp2,STARTED PHASE CN,TRIPPED PHASE ABC, Start element -distance,location-37.8km
190 | 220KV-KOTHAMANGALAM-Pallivasal-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 29-04-2026 | 16:25 | KSEB | Correct Operation | DISC FLASH |  |  | KSEB | Correct Operation | DISC FLASH |  |  | ANN: Diff, SOTF, 87 L1 & 87L2 M1: B-E, ---, 53.4KM, M2: B-E,---, 52.8KM
191 | 220KV-BRAHMPURAM-LOWER PERIYAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 29-04-2026 | 16:50 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
192 | 220KV-BRAHMPURAM-LOWER PERIYAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 29-04-2026 | 17:00 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation | DISC FLASH |  |  | M1: DP: C-G, Z1, 26.987KM M2: DP: C-G, Z1, 24.693KM
193 | 220KV-MALAPARAMBA-NALLALAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 30-04-2026 | 19:10 | KSEB | Correct Operation | AR lockout at both end |  |  | KSEB | Correct Operation | AR lockout at both end after attempted |  |  | Ann: M1 M2 DP optd AR L/O M1:DP:A-N,Z1,32.32km M2:DP:R-G,Z1,32.164km
194 | 220KV-EDAMON-POTHENCODE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 30-04-2026 | 15:45 | KSEB | Correct Operation | CORRECT OPERATION,PHASES B AND C EARTH FAULT NOT AUTORECLOSED SUCCESFULLY |  |  | KSEB | Correct Operation | CORRECT OPERATION |  |  | Ann: M1 M2 DP optd M1:DP:Bph,Z1,--- M2:DP:Gen trip, Y-B,Z1, L2-L3, FUSE FAIL,11.47
195 | 220KV-EDAMON-POTHENCODE-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 30-04-2026 | 15:45 | KSEB | Failure Operation | Not reclosed due to CB ready issue |  | Completed | KSEB | Correct Operation | CORRECT OPERATION,SUCCESFUL AUTORECLOSURE @ POTHENCODE SS END |  |  | Ann:M1 M2 DP optd, fuse fail M1:DP: trip B PH,Z1,14.43km L3-N, AR optd M2:DP: B ph,Z1,14.45km, L3-N, AR optd
196 | 220KV-EDAMON-SABARIGIRI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 30-04-2026 | 15:57 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation | AR operated,Z1 fault |  |  | AR OPERATED
197 | 220KV-EDAMON-SABARIGIRI-3 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 30-04-2026 | 15:57 | KSEB | Correct Operation | CHECK SYNCH NOT READY |  |  | KSEB | Correct Operation | AR operated,Z1 fault |  |  | Ann: CB tripped M1:DP:L31-E,---,43km M2:DP:L31-E,---42.9km
198 | 220KV-IDDUKI-KALAMASSERY-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 30-04-2026 | 16:26 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | M1:PHASE A,ZONE 1 M2:start phase A CN,tripped phase AB C,fault location-13.22km
199 | 220KV-IDDUKI-NEW PALLOM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 30-04-2026 | 16:14 | KSEB | Correct Operation | AR AND TRIP |  |  | KSEB | Correct Operation | Trip on reclose at New Pallom |  |  | M1:PHASE C,ZONE 1 M2:start phase CN,tripped phase ABC,fault location-10.1km
200 | 220KV-LOWER PERIYAR-IDDUKI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 30-04-2026 | 16:29 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
201 | 220KV-LOWER PERIYAR-IDDUKI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 30-04-2026 | 16:26 | KSEB | Correct Operation | AR OPTD |  |  | KSEB | Failure Operation | AR RESET TIME NOT EXHAUSTED.HENCE FEEDER DID NOT RE CLOSE AT IDUKKI END |  | Completed | M1:PHASE C,ZONE 1 M2:start phase A CN,tripped phase BN,fault location-13.22km
202 | 220KV-IDDUKI-KOTHAMANGALAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 30-04-2026 | 16:17 | KSEB | Correct Operation | MULTI PHASE FAULT .CHECK SYNCH NOT READY |  |  | KSEB | Correct Operation | "Ann: M1 M2 DP optd M1:DP:RYB,Z1,32.2km M2:DP:RYB,Z1,,31.04km" |  |  | M1:PHASE C,ZONE 1 M2:start phase BCN,tripped phase ABC,fault location-9.497km
203 | 220KV-IDDUKI-PALLIVASAL_EXTN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 30-04-2026 | 15:52 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
204 | 220KV-BRAHMPURAM-LOWER PERIYAR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 30-04-2026 | 16:28 | KSEB | Correct Operation | "Ann: M1 M2 DP optd, 86A 86B optd M1:DP:R ph M2:C-G,Z1,48.7km,carrier send" |  |  | KSEB | Correct Operation | "M1:DP:ABC-N, Z1,13.41KM M2:DP:ABC-N, Z1,13.67KM" |  |  | AR OPERATED
205 | 400KV-TIRUNELVELI-KOTTAYAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 30-04-2026 | 16:01 | PGCIL SR-2 | Correct Operation | AR Successful Rph-G , 133.6 km / 3.29 kA. |  |  | KSEB | Correct Operation | Autoreclose. Z1, R-phase |  |  | AR OPERATED
206 | 400KV-TIRUNELVELI-KOTTAYAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 30-04-2026 | 16:19 | PGCIL SR-2 | Correct Operation | AR Successful Bph-G fault . 51.3 km / 7.54 kA |  |  | KSEB | Correct Operation | AR operated. Z1, C-phase |  |  | AR OPERATED
207 | 220KV-MADAKATHARA-ELANKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 30-04-2026 | 18:54 | KSEB | Correct Operation | "M1:DP:start ph AB-N, B-N,Z2-Z3,73.80KM M2:DIFF:B PH,---,-16.9km" |  |  | KSEB | Correct Operation |  |  |  | Transient fault.
208 | 220KV-IDDUKI-KALAMASSERY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 30-04-2026 | 16:11 | KSEB | Correct Operation | AR AND TRIP |  |  | KSEB | Correct Operation |  |  |  | M1:PHASE C,ZONE 1 M2:start phase CN,tripped phase C,fault location-4.6km,
209 | 220KV-BRAHMPURAM-LOWER PERIYAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 30-04-2026 | 16:28 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation | DISC FLASH |  |  | Ann: M1 M2 DP optd, 86A 86B optd M1:DP:RYB,Z1,44.89km,carrier send M2:C-G,---,44.5km,carrier send, carrier received, carrier aided trip
210 | 400KV-BPS-JAGALUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 29-04-2026 | 00:12 | KPTCL | Correct Operation | A/R Successful operation |  |  | KPTCL | Correct Operation |  |  |  | Trip
211 | 220KV-RTPS-SHAHAPUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 07-04-2026 | 23:24 | KPCL | Correct Operation |  |  |  | KPTCL | Correct Operation | BN fault, fault current 3.37kA, AR operated and TOR due to persistent fault |  |  | 220KV RTPS END:Zone-1, Fault loop Bph-GND, Distance:36.63 KM ,I=4.213 KA
212 | 220KV-LINGSUGUR-RTPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 10-04-2026 | 04:50 | KPTCL | Correct Operation |  |  |  | KPCL | Correct Operation |  |  |  | 220KV RTPS END:Zone-1, Fault loop Yph-GND, Distance:34.05 KM ,I=4.548 KA
213 | 220KV-RTPS-MALAT-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 11-04-2026 | 02:18 | KPCL | Correct Operation |  |  |  | KPTCL | Correct Operation |  |  |  | 220KV RTPS END:Zone-1, Fault loop Bph-GND
214 | 220KV-LINGSUGUR-RTPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 11-04-2026 | 23:25 | KPTCL | Correct Operation |  |  |  | KPCL | Correct Operation |  |  |  | 220KV RTPS END:Zone-1, Fault loop Bph-GND, Distance:30.42 KM ,I=5.094 KA
215 | 220KV-RTPS-SHAHAPUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 13-04-2026 | 04:09 | KPCL | Correct Operation |  |  |  | KPTCL | Correct Operation | BN fault in Zone-1, 3.73kA , AR successful at Shahpur end |  |  | 220KV RTPS END:Zone-1, Fault loop Bph-GND, Distance:43.89 KM ,I=3.807 KA
216 | 220KV-LINGSUGUR-RTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 19-04-2026 | 18:22 | KPTCL | Correct Operation | TOR due to persistent fault. Insulator decap at tower location 191 |  |  | KPCL | Correct Operation |  |  |  | 220KV RTPS END:Zone-1, Fault loop Yph-GND, Distance:62.12 KM ,I=2.551 KA
217 | 220KV-LINGSUGUR-RTPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 19-04-2026 | 18:44 | KPTCL | Correct Operation | BN fault in Zone-1, fault current - 8.218kA, Fault location 14.58km, AR blocked due to high fault current logic |  |  | KPCL | Correct Operation |  |  |  | 220KV RTPS END:Zone-1, Fault loop Bph-Yph, Distance:48.4 KM ,I=4.47 KA, PSB IN ZONE-1
218 | 220KV-LINGSUGUR-RTPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 19-04-2026 | 20:12 | KPTCL | Correct Operation |  |  |  | KPCL | Correct Operation |  |  |  | 220KV RTPS END:Zone-2, Fault loop Bph-GND, Distance:81.30KM ,I=2.139 KA, PUTT
219 | 220KV-LINGSUGUR-RTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 21-04-2026 | 13:15 | KPTCL | Correct Operation |  |  |  | KPCL | Correct Operation |  |  |  | 220KV RTPS END:Zone-1, Fault loop Rph-GND, Distance:48.3 KM ,I=2.8 KA
220 | 220KV-LINGSUGUR-RTPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 21-04-2026 | 18:52 | KPTCL | Correct Operation |  |  |  | KPCL | Correct Operation |  |  |  | 220KV RTPS END:Zone-1, Fault loop Bph-GND, Distance:49.78 KM ,I=3.149 KA
221 | 220KV-RTPS-RAICHUR_KA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 28-04-2026 | 05:25 | KPCL | Correct Operation |  |  |  | KPTCL | Correct Operation |  |  |  | 220KV RTPS END:Zone-1, Fault loop Rph-GND, Distance:14.99 KM ,I=8.550 KA
222 | 400KV-SHOLINGANALLUR-KALVENDAPATTU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 14-04-2026 | 10:42 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | PGCIL SR-2 | Correct Operation | AR Sucessfull Bph-G - 25.3 km / 8.06 kA |  |  | TRANSIENT FAULT
223 | 400KV-ALAMATHY-TIRUVALAM_TN-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 03-04-2026 | 12:05 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
224 | 400KV-SHOLINGANALLUR-KALVENDAPATTU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 14-04-2026 | 12:30 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | PGCIL SR-2 | Correct Operation | AR Successfull- 29.9 km / 4.23 kA |  |  | TRANSIENT FAULT
225 | 400KV-PALAVADI-RASIPALYAM-4 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 10-04-2026 | 00:07 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
226 | 400KV-NCTPS_STAGE_II-MANALI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 16-04-2026 | 02:15 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
227 | 400KV-ALAMATHY-MANALI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 19-04-2026 | 00:49 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
228 | 400KV-NCTPS_STAGE_II-MANALI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 20-04-2026 | 01:56 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
229 | 400KV-SHOLINGANALLUR-KALVENDAPATTU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 23-04-2026 | 02:26 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | PGCIL SR-2 | Correct Operation | AR successful - 3.3 km / 17.09 kA. |  |  | TRANSIENT FAULT Rpg-G
230 | 400KV-VALLUR-ALAMATHY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 23-04-2026 | 06:03 | NTECL | Correct Operation |  |  |  | TANTRANSCO | Correct Operation | CAT,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
231 | 220KV-VTPS-PODILI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 07-04-2026 | 10:35 | APGENCO | Correct Operation | Bph-G fault ,Z-Com protection operated. |  |  | APTRANSCO | Correct Operation |  |  |  | Distance protection operated
232 | 220KV-KONDAPALLI-CHILLAKALLU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 30-04-2026 | 17:38 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
233 | 230KV-KUDANKULAM-TTPS | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-04-2026 | 05:42 | NPCIL_KKNP | Correct Operation | Line tripped on carrier aid trip protection |  |  | TNPGCL |  |  |  |  | ADL31 TTPS line was tripped on carrier aid trip protection. Y-phase to earth fault, fault current: 1.37KA, Fault distance: 100.09KM
234 | 230KV-KUDANKULAM-TTPS | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 29-04-2026 | 06:44 | NPCIL_KKNP | Correct Operation | Line was tripped on carrier aid trip protection |  |  | TNPGCL |  |  |  |  | ADL31 line was tripped on carrier aid trip protection. R-phase to earth fault, fault distance: 108.15KM, Fault current: 1.422KA
235 | 400KV-KUDANKULAM-TIRUNELVELI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 29-04-2026 | 14:35 | NPCIL_KKNP | Correct Operation | ACL22 line got tripped on zone-1 distance protection, Auto re-closer successful |  |  | PGCIL SR-2 | Correct Operation | AR Successful Bph-G - 17.7 km / 13.4 kA |  |  | ACL22 Line was tripped on Zone-1 distance protection, Fault current : 5.686KA, Fault distance: 53.7KM, Auto re-closer happened successfully.
236 | 220KV-KONDAPALLI-CHILLAKALLU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 30-04-2026 | 17:42 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
237 | 230KV-TTPS-ANUPANKULAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 01-04-2026 | 11:24 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
238 | 230KV-KARAIKUDI-SEMBATTI | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 01-04-2026 | 20:17 | PGCIL SR-2 | Correct Operation | AR Successful |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
239 | 230KV-SINGARPET-VINNAMANGALAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-04-2026 | 07:48 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
240 | 230KV-KAYATHAR(TN)-TTPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-04-2026 | 13:46 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
241 | 230KV-KAVANUR-KAMUDHI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-04-2026 | 23:37 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
242 | 220KV-PULIVENDULA-MUTYALACHERU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 30-04-2026 | 21:45 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
243 | 220KV-JAMMALAMADUGU-BETAMCHERLA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 01-04-2026 | 12:17 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
244 | 220KV-KONDAPALLI-CHILLAKALLU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 02-04-2026 | 04:16 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
245 | 220KV-ATMAKUR-PODILI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 03-04-2026 | 13:43 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
246 | 220KV-VIJAYAWADA-GUDIVADA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 04-04-2026 | 00:29 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
247 | 220KV-PIDUGURALLA-INAPARAJUPALLI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 04-04-2026 | 15:01 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
248 | 220KV-ATMAKUR-PODILI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 05-04-2026 | 11:34 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
249 | 220KV-BOMMUR-JEGURUPADU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 06-04-2026 | 09:44 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
250 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 06-04-2026 | 11:35 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
251 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_AP-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 06-04-2026 | 13:24 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
252 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 06-04-2026 | 14:06 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
253 | 220KV-BOBBILI-MARADAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 06-04-2026 | 14:19 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
254 | 220KV-KV_KOTA_OLD-NUZVID-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 06-04-2026 | 15:40 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
255 | 220KV-VTPS-CHILLAKALLU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 06-04-2026 | 16:27 | APGENCO | Correct Operation | Rph-G fault , Zone-1 distance protection operated,1.27KA,AR disabled. |  |  | APTRANSCO | Correct Operation |  |  |  | distance protection operated
256 | 400KV-NELLORE_AP-VTPS_IV-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 06-04-2026 | 17:09 | APTRANSCO | Correct Operation |  |  |  | APGENCO | Correct Operation | No trip |  |  | No Trip On 06/04/2026
257 | 220KV-PULIVENDULA-MUTYALACHERU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 30-04-2026 | 21:45 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
258 | 220KV-KOTHAGUDEM_TPS-TIRUVURU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 07-04-2026 | 12:40 | TGGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
259 | 220KV-PENDURTHI-UPPER_SILERU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 07-04-2026 | 13:08 | APTRANSCO | Correct Operation |  |  |  | APGENCO | Correct Operation | Feeder tripped on R ph to Earth fault, AR operated |  |  | R-N fault
260 | 220KV-NANDYAL-SOMAYAJULAPALLI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 08-04-2026 | 12:13 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
261 | 220KV-CUDDAPAH-THIMAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 08-04-2026 | 12:41 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
262 | 220KV-NANDYAL-SOMAYAJULAPALLI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 08-04-2026 | 12:54 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
263 | 220KV-CUDDAPAH-THIMAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 08-04-2026 | 13:51 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
264 | 220KV-CUDDAPAH-THIMAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 08-04-2026 | 13:55 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
265 | 220KV-CUDDAPAH-RENIGUNTA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 08-04-2026 | 14:02 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
266 | 220KV-CUDDAPAH-RENIGUNTA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 08-04-2026 | 14:15 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
267 | 220KV-DHONE-NANSURALLA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 09-04-2026 | 03:33 | APTRANSCO | Failure Operation | Failure operation | Line tripped at both ends due to B-N fault. AR Successful, line was holding from Nansuralla end. AR not operated at Dhone end. In main-2 relay 7SA522, zone-2/1-phase trip configured to 86A & 86B. The same was rectified. | Completed | APTRANSCO | Correct Operation
268 | 220KV-TADIKONDA-VTPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 09-04-2026 | 06:29 | APTRANSCO | Correct Operation |  |  |  | APGENCO | Correct Operation | R-PH ,Neutral TOC2 operated,BRC. |  |  | Neutral TOC operated
269 | 220KV-KOTHAGUDEM_TPS-TIRUVURU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 10-04-2026 | 10:31 | TGGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
270 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_AP-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 10-04-2026 | 12:47 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
271 | 220KV-BD_PALEM-MARADAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 10-04-2026 | 14:01 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
272 | 220KV-KOTHAGUDEM_TPS-TIRUVURU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 10-04-2026 | 15:31 | TGGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
273 | 220KV-ATMAKUR-PODILI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 11-04-2026 | 09:02 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
274 | 220KV-PENDURTHI-UPPER_SILERU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 13-04-2026 | 12:54 | APTRANSCO | Correct Operation |  |  |  | APGENCO | Correct Operation | Feeder tripped on B ph to Earth fault |  |  | B-N fault
275 | 220KV-GAZUWAKA_AP-PENDURTHI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 13-04-2026 | 12:54 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
276 | 220KV-VIJAYAWADA-BHIMADOLE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 13-04-2026 | 13:00 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
277 | 220KV-PALAMANERU-PUNGANUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 13-04-2026 | 14:57 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Unwanted Operation |  | At Punganur end only line tripped on zone-1 indications due to Main-2 relay voltage deselection. Voltage selection relay replaced. | Completed
278 | 220KV-KOTHAGUDEM_TPS-TIRUVURU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 14-04-2026 | 12:57 | TGGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
279 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 14-04-2026 | 13:02 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
280 | 220KV-BOYAREDDYPALLI-TADIPATHRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 14-04-2026 | 17:30 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
281 | 220KV-URAVAKONDA-IPPERU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 15-04-2026 | 04:11 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
282 | 220KV-JAMMALAMADUGU-PORUMAMILA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 15-04-2026 | 12:23 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
283 | 220KV-CUDDAPAH-THIMAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 15-04-2026 | 12:31 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
284 | 220KV-CUDDAPAH-THIMAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 15-04-2026 | 12:49 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
285 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_AP-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 15-04-2026 | 13:13 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
286 | 220KV-JAMMALAMADUGU-MYLAVARAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 15-04-2026 | 13:23 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
287 | 220KV-CUDDAPAH-RAJAMPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 16-04-2026 | 08:38 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
288 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 18-04-2026 | 09:52 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
289 | 220KV-KONDAPALLI-CHILLAKALLU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 18-04-2026 | 12:33 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
290 | 220KV-URAVAKONDA-BELUGUPA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 18-04-2026 | 16:40 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
291 | 220KV-URAVAKONDA-BELUGUPA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 18-04-2026 | 23:05 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
292 | 220KV-CUDDAPAH-THIMAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 19-04-2026 | 12:52 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
293 | 220KV-CUDDAPAH-THIMAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 19-04-2026 | 13:20 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
294 | 220KV-ONGOLE-PODILI_OLD-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 19-04-2026 | 13:35 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
295 | 220KV-URAVAKONDA-BELUGUPA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 19-04-2026 | 21:58 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Unwanted Operation |  | Line tripped at Belaguppa end only on Main-1 (P444) distance relay with Y-N, zone-1 protection with out any line fault. It is informed that, bus PT supply was not avaialble to the relay. P444 relay issued 3-Phase trip after current change. The defective PT selection relay was replaced with spare relay. | Completed
296 | 220KV-URAVAKONDA-BELUGUPA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 20-04-2026 | 00:07 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
297 | 220KV-HINDUPUR2-BOKSAMPALLI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 20-04-2026 | 15:47 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
298 | 220KV-VTPS-CHILLAKALLU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 21-04-2026 | 12:25 | APGENCO | Correct Operation | Bph-G fault , Zone-1 distance protection operated,3.17,AR disabled. |  |  | APTRANSCO | Correct Operation |  |  |  | Distance protection operated
299 | 220KV-CHITTOOR-NAGIRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 20-04-2026 | 13:09 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
300 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_AP-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 20-04-2026 | 13:31 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
301 | 220KV-VTPS-PODILI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 21-04-2026 | 11:44 | APGENCO | Correct Operation | Bph-G fault ,Z-1 ,2.177KA ,AR Success. |  |  | APTRANSCO | Correct Operation |  |  |  | Distance protection operated
302 | 220KV-VIJAYAWADA-BHIMADOLE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 21-04-2026 | 13:11 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
303 | 220KV-CUDDAPAH-RENIGUNTA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 21-04-2026 | 14:36 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
304 | 220KV-KONDAPALLI-CHILLAKALLU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 21-04-2026 | 14:45 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
305 | 220KV-LOWER_SILERU-Chintur-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 21-04-2026 | 22:07 | APGENCO | Correct Operation | DUE TO FAILURE OF R- PHASE LIMB OF BUS COUPLER. |  |  | APTRANSCO | Correct Operation |  |  |  | LBB operated at Lower Sileru due to Bus-Coupler breaker failure
306 | 220KV-NELLORE_AP-RACHAGUNNERI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-04-2026 | 11:46 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
307 | 220KV-BOYAREDDYPALLI-TADIPATHRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-04-2026 | 12:09 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
308 | 220KV-GARIVIDI-MARADAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-04-2026 | 12:28 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
309 | 220KV-VTPS-NUZVID-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-04-2026 | 12:48 | APGENCO | Correct Operation | Yph-Bph fault ,Z-1 operated,8.305KA,AR unsuccess |  |  | APTRANSCO | Correct Operation |  |  |  | Distance protection
310 | 220KV-ANANTHAPUR-THIMAPRAM_LI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-04-2026 | 13:19 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
311 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 23-04-2026 | 11:51 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
312 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 24-04-2026 | 01:56 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
313 | 220KV-KONDAPALLI-CHILLAKALLU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 24-04-2026 | 03:27 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
314 | 400KV-KALPAKKA-VEMAGIRI_AP-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 24-04-2026 | 04:54 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
315 | 220KV-NIDADAVOLU-PALLANTLA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 24-04-2026 | 11:37 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
316 | 220KV-NANDYAL-SOMAYAJULAPALLI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 24-04-2026 | 12:44 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
317 | 220KV-DHONE-KAMBALPADU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 25-04-2026 | 08:40 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
318 | 220KV-KAKINADA-PARAVADA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 25-04-2026 | 09:10 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
319 | 400KV-KALPAKKA-VEMAGIRI_AP-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 25-04-2026 | 11:12 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
320 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 25-04-2026 | 12:54 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
321 | 220KV-KAKINADA-PARAVADA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 25-04-2026 | 15:47 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
322 | 400KV-GUDDIGUDEM-HINDUJA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 25-04-2026 | 17:49 | APTRANSCO | Correct Operation |  |  |  | HINDUJA
323 | 220KV-PIDUGURALLA-INAPARAJUPALLI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 26-04-2026 | 03:55 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
324 | 220KV-PIDUGURALLA-INAPARAJUPALLI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 26-04-2026 | 04:34 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
325 | 220KV-VTPS-PIDUGURALLA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 26-04-2026 | 05:05 | APGENCO | Correct Operation | Rph-G fault , Zone-3 distance protection operated,2.088KA. |  |  | APTRANSCO | Correct Operation |  |  |  | Distance protection operated
326 | 220KV-PIDUGURALLA-INAPARAJUPALLI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 26-04-2026 | 05:05 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
327 | 220KV-PIDUGURALLA-INAPARAJUPALLI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 26-04-2026 | 05:12 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
328 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 26-04-2026 | 11:37 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
329 | 220KV-ATMAKUR-PODILI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 27-04-2026 | 00:48 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
330 | 220KV-GARIVIDI-MARADAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 27-04-2026 | 12:21 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
331 | 400KV-MARADAM-KALPAKKA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 27-04-2026 | 12:38 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
332 | 220KV-CUDDAPAH-RENIGUNTA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 27-04-2026 | 12:44 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
333 | 220KV-ATMAKUR-PODILI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 27-04-2026 | 13:21 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
334 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 27-04-2026 | 22:15 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
335 | 220KV-WANAPARTHY-BRAMHANA_KOTKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 28-04-2026 | 05:26 | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | APTRANSCO | Correct Operation |  |  |  | C-phase to ground fault
336 | 220KV-SULURPET-NELLORE_AP-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 27-04-2026 | 13:40 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
337 | 220KV-PARAVADA-ANRAK-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 28-04-2026 | 13:05 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
338 | 220KV-PARAVADA-ANRAK-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 28-04-2026 | 13:59 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
339 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_AP-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 28-04-2026 | 16:54 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
340 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_AP-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 28-04-2026 | 16:54 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
341 | 220KV-KONDAPALLI-VTPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 30-04-2026 | 17:38 | APTRANSCO | Correct Operation |  |  |  | APGENCO | Correct Operation | R-Ph-G,Zone-1 operated ,6.583KA. |  |  | Distance protection operated
342 | 220KV-VTPS-RENTACHINTHALA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 30-04-2026 | 17:33 | APGENCO | Correct Operation | Rph-Yph-B-ph fault ,Z-1 operated,24.98KA,AR Unsuccess. |  |  | APTRANSCO | Correct Operation |  |  |  | Distance protection operated
343 | 220KV-VTPS-RENTACHINTHALA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 30-04-2026 | 17:33 | APGENCO | Correct Operation | Rph-Yph-Bph fault ,Z-1 operated,12.575KIA,AR unsuccess. |  |  | APTRANSCO | Correct Operation |  |  |  | Distance protection operated
344 | 220KV-VTPS-CHILLAKALLU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 30-04-2026 | 13:16 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
345 | 220KV-KONDAPALLI-CHILLAKALLU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 30-04-2026 | 13:16 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
346 | 220KV-PENDURTHI-UPPER_SILERU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 30-04-2026 | 06:51 | APTRANSCO | Correct Operation |  |  |  | APGENCO | Correct Operation | Feeder tripped on Y ph to Earth fault, AR operated |  |  | Y-N fault
347 | 220KV-HINDUPUR2-GOLLAPURAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 29-04-2026 | 20:36 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
348 | 220KV-GOLLAPURAM-HINDUPUR2-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 29-04-2026 | 18:49 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
349 | 220KV-SOMAYAJULAPALLI-DHONE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 28-04-2026 | 21:44 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
350 | 220KV-GOOTY-SWS-DHONE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 28-04-2026 | 21:05 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
351 | 220KV-GOOTY-SWS-DHONE-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 28-04-2026 | 20:10 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
352 | 220KV-DHONE-NANSURALLA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 28-04-2026 | 19:58 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
353 | 220KV-SOMAYAJULAPALLI-DHONE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 28-04-2026 | 19:51 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
354 | 220KV-NANDYAL-SOMAYAJULAPALLI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 28-04-2026 | 19:38 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
355 | 220KV-NANDYAL-SOMAYAJULAPALLI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 28-04-2026 | 19:38 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
356 | 220KV-SRISAILAM_RIGHT_BANK-SOMAYAJULAPALLI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 28-04-2026 | 17:50 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
357 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 28-04-2026 | 17:42 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
358 | 230KV-PUGALUR(TN)-RENGANATHAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 07-04-2026 | 05:56 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL
359 | 230KV-SAMAYAPURAM-TRICHY(TN)-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 07-04-2026 | 11:56 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
360 | 230KV-TIRUVALAM_TN-SINGARPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 07-04-2026 | 13:36 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
361 | 230KV-MYVADI-O.K.MANDAPAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 07-04-2026 | 14:12 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | CAT,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
362 | 220KV-THENI-SABARIGIRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | KSEB | 08-04-2026 | 11:26 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | KSEB | Correct Operation | AR operated |  |  | TRANSIENT FAULT
363 | 230KV-NEYVELI_TS_II-KADALANGUDI | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 03-04-2026 | 05:32 | NLC |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
364 | 230KV-KAYATHAR-SANGRAPERI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 03-04-2026 | 06:27 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | Idly charged from Kayathar |  |  | TRANSIENT FAULT
365 | 230KV-VEERAPURAM-CUDDALORE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 03-04-2026 | 10:35 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | Idly charged from Veerapuram |  |  | TRANSIENT FAULT
366 | 230KV-KARAIKUDI(TN)-KAVANUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 04-04-2026 | 05:17 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
367 | 230KV-Chekkanurani-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 04-04-2026 | 12:38 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
368 | 230KV-Chekkanurani-RENGANATHAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 04-04-2026 | 13:05 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | CAT,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
369 | 230KV-KAYATHAR(TN)-TTPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 04-04-2026 | 13:27 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
370 | 230KV-SAMAYAPURAM-POIYUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 04-04-2026 | 18:13 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
371 | 230KV-PASUMALAI-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 04-04-2026 | 19:55 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
372 | 230KV-NEYVELI_TS_II-KADALANGUDI | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 04-04-2026 | 20:21 | NLC |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
373 | 230KV-VILLUPURAM-CUDDALORE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 05-04-2026 | 13:59 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
374 | 230KV-KADAMPARAI-ALIYAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 06-04-2026 | 00:16 | TNGECL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
375 | 230KV-ALAMATHY-MOSUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 06-04-2026 | 11:29 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
376 | 230KV-AMUDHAPURAM-KODIKURCHI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-04-2026 | 11:44 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
377 | 230KV-KAYATHAR(TN)-TIRUNELVELI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-04-2026 | 12:52 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | PGCIL SR-2 | Correct Operation | AR ATTEMPTED AND TRIPPED ON PERSISTING FAULT- 17.11 KM / 4.97 KA |  |  | Bph-G fault in line
378 | 230KV-KAYATHAR(TN)-VEERANAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-04-2026 | 13:12 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,TOR |  |  | TRANSIENT FAULT
379 | 230KV-AMUDHAPURAM-KODIKURCHI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-04-2026 | 17:53 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
380 | 230KV-PUTHANSANTHAI-PUGALUR(TN)-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-04-2026 | 19:18 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
381 | 230KV-AMUDHAPURAM-KODIKURCHI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-04-2026 | 20:37 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | CAT,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
382 | 230KV-PASUMALAI-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 09-04-2026 | 12:58 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
383 | 230KV-ARNI-ECHUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 09-04-2026 | 14:34 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
384 | 230KV-KARAIKUDI-SEMBATTI | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 10-04-2026 | 03:27 | PGCIL SR-2 | Correct Operation | AR Successful. 66.37 KM / 3.2 kA |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | AR successful on Rph-G
385 | 230KV-Chekkanurani-THENI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 10-04-2026 | 13:56 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | CAT,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
386 | 230KV-KADAMPARAI-MYVADI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 10-04-2026 | 20:22 | TNGECL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
387 | 230KV-TTPS-KINNIMANGLAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-04-2026 | 05:40 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | CAT,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
388 | 230KV-O.K.MANDAPAM-ANAIKADAVU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 11-04-2026 | 18:31 | TANTRANSCO | Correct Operation | CAT,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
389 | 230KV-SALEM_230-SINGARPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 11-04-2026 | 14:25 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | CAT,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
390 | 230KV-KADAMPARAI-MYVADI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 11-04-2026 | 21:36 | TNGECL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
391 | 230KV-KADAMPARAI-MYVADI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 11-04-2026 | 21:53 | TNGECL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
392 | 230KV-THENI-SEMBATTI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 12-04-2026 | 03:29 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
393 | 230KV-KADAMPARAI-MYVADI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 12-04-2026 | 20:05 | TNGECL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
394 | 230KV-KARAIKUDI(TN)-KAVANUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 13-04-2026 | 02:16 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
395 | 230KV-ARNI-SINGARPET | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 13-04-2026 | 13:25 | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
396 | 230KV-ALAMATHY-OPG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 13-04-2026 | 17:35 | TANTRANSCO | Correct Operation | CAT,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE,1,B,N, AR Lockout due to subsequent fault |  |  | TRANSIENT FAULT
397 | 220KV-UDUMALPET-Pallivasal-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | KSEB | 14-04-2026 | 02:24 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | KSEB | Correct Operation | AR operated |  |  | TRANSIENT FAULT
398 | 230KV-KARAIKUDI(TN)-KAVANUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 15-04-2026 | 05:21 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
399 | 230KV-KARAIKUDI(TN)-VALATHUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 15-04-2026 | 19:42 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
400 | 230KV-TTPS-KINNIMANGLAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 17-04-2026 | 02:40 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
401 | 230KV-KAYATHAR(TN)-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 17-04-2026 | 03:32 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
402 | 230KV-MILAVITTAN-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 17-04-2026 | 04:25 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
403 | 230KV-KARAIKUDI(TN)-KAVANUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 17-04-2026 | 04:58 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
404 | 230KV-Chekkanurani-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 17-04-2026 | 05:22 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
405 | 230KV-MILAVITTAN-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 17-04-2026 | 05:25 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
406 | 230KV-MILAVITTAN-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 17-04-2026 | 06:46 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
407 | 230KV-KAVANUR-KAMUDHI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 18-04-2026 | 03:34 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
408 | 230KV-Chekkanurani-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 18-04-2026 | 05:44 | TANTRANSCO | Correct Operation | CAT,B,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
409 | 230KV-KARAIKUDI(TN)-KAVANUR-3 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 18-04-2026 | 05:47 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
410 | 230KV-TTPS-KINNIMANGLAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-04-2026 | 04:27 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | CAT,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
411 | 230KV-Chekkanurani-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-04-2026 | 04:40 | TANTRANSCO | Correct Operation | CAT,B,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
412 | 230KV-TTPS-ANUPANKULAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-04-2026 | 04:49 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | CAT,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
413 | 230KV-PASUMALAI-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-04-2026 | 04:53 | TANTRANSCO | Correct Operation | CAT,Y,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
414 | 230KV-TTPS-KINNIMANGLAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-04-2026 | 05:03 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | CAT,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
415 | 230KV-KAYATHAR(TN)-TTPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-04-2026 | 05:14 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
416 | 230KV-MILAVITTAN-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-04-2026 | 05:14 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
417 | 230KV-Chekkanurani-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-04-2026 | 05:18 | TANTRANSCO | Correct Operation | CAT,B,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
418 | 230KV-KAYATHAR(TN)-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-04-2026 | 05:37 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
419 | 230KV-KAYATHAR(TN)-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-04-2026 | 06:10 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
420 | 230KV-KAYATHAR(TN)-TTPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-04-2026 | 06:16 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
421 | 230KV-KARAIKUDI(TN)-KARAMBAYAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-04-2026 | 14:10 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TRANSIENT FAULT
422 | 230KV-TIRUNELVELI-UDAYATHOOR | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-04-2026 | 15:14 | PGCIL SR-2 | Correct Operation | AR Successful |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
423 | 230KV-KARAIKUDI(TN)-KAVANUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-04-2026 | 03:52 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
424 | 230KV-KARAIKUDI-PUDUKKOTTAI | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-04-2026 | 04:45 | PGCIL SR-2 | Correct Operation | AR Successful - Bph-G - 4.6 kM / 12.66 KA |  |  | TANTRANSCO | Correct Operation | CAT,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
425 | 230KV-TTPS-KINNIMANGLAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-04-2026 | 04:48 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | CAT,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
426 | 230KV-Chekkanurani-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-04-2026 | 05:44 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
427 | 230KV-TTPS-KINNIMANGLAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-04-2026 | 06:08 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | CAT,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
428 | 230KV-KUNDAH3-KARAMADAI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-04-2026 | 13:56 | TNGECL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
429 | 230KV-PUTHANSANTHAI-PUGALUR(TN)-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-04-2026 | 14:05 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
430 | 230KV-O.K.MANDAPAM-ANAIKADAVU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-04-2026 | 14:57 | TANTRANSCO | Correct Operation | CAT,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
431 | 230KV-PUTHANSANTHAI-PUGALUR(TN)-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-04-2026 | 23:16 | TANTRANSCO | Correct Operation | idly charged from Pugalur |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
432 | 230KV-AMUDHAPURAM-NALLAMANAICKENPATTI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 21-04-2026 | 05:51 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
433 | 230KV-KARAIKUDI(TN)-KARAMBAYAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 21-04-2026 | 12:09 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TRANSIENT FAULT
434 | 230KV-KAYATHAR(TN)-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 21-04-2026 | 23:55 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
435 | 230KV-KARAIKUDI-SEMBATTI | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 22-04-2026 | 00:27 | PGCIL SR-2 | Correct Operation | AR Successful - 107 km / 2.06 kA |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT Rph-G
436 | 230KV-Chekkanurani-SEMBATTI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 22-04-2026 | 14:16 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
437 | 230KV-Chekkanurani-IND_BHARATH_2-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 23-04-2026 | 00:22 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation |  |  |  | TRANSIENT FAULT
438 | 230KV-KARAIKUDI(TN)-KAVANUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 23-04-2026 | 03:06 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
439 | 230KV-Chekkanurani-SAVASPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 23-04-2026 | 23:46 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
440 | 230KV-PASUMALAI-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 24-04-2026 | 02:43 | TANTRANSCO | Correct Operation | CAT,Y,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
441 | 230KV-PASUMALAI-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 24-04-2026 | 03:42 | TANTRANSCO | Correct Operation | CAT,Y,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
442 | 230KV-KAYATHAR(TN)-TTPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 24-04-2026 | 04:49 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
443 | 230KV-PUGALUR(TN)-RENGANATHAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 24-04-2026 | 04:54 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
444 | 230KV-TTPS-ANUPANKULAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 25-04-2026 | 03:45 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
445 | 230KV-O.K.MANDAPAM-PALLADAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 25-04-2026 | 13:34 | TANTRANSCO | Correct Operation | CAT,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
446 | 230KV-ARASUR-GOBI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 27-04-2026 | 04:57 | TANTRANSCO | Correct Operation | idly charged from GOBI |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
447 | 230KV-TTPS-KINNIMANGLAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 27-04-2026 | 13:31 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
448 | 220KV-THENI-SABARIGIRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | KSEB | 27-04-2026 | 13:41 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | KSEB | Correct Operation | AR operated |  |  | TRANSIENT FAULT
449 | 230KV-SALEM_230-SINGARPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 27-04-2026 | 13:47 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
450 | 230KV-STCMS-PERAMBALUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 28-04-2026 | 12:47 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
451 | 230KV-UDUMALPET-ALIYAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 30-04-2026 | 05:38 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
452 | 230KV-ARNI-SINGARPET | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 30-04-2026 | 13:11 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
453 | 230KV-SALEM_230-SINGARPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 30-04-2026 | 13:27 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
454 | 230KV-VINNAMANGALAM-TIRUPATTUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 30-04-2026 | 16:17 | TANTRANSCO | Correct Operation | CAT,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
455 | 230KV-GOBI-ANTHIYUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 30-04-2026 | 19:58 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
456 | 230KV-GOBI-ANTHIYUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 30-04-2026 | 20:06 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
457 | 230KV-MANALI-CMRL_CENTRAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 03-04-2026 | 11:39 | TANTRANSCO | Correct Operation | ZONE.1,B,N LOCKOUT_AR OFF |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N LOCKOUT_AR OFF |  |  | TRANSIENT FAULT
458 | 230KV-VEERAPURAM-CUDDALORE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 04-04-2026 | 21:50 | TANTRANSCO | Correct Operation | ZONE.2,B,N,LOCKOUT |  |  | TANTRANSCO | Correct Operation | idly charged from Veerapuram |  |  | Y phase Disc flash over at location No.109
459 | 230KV-GUMMIDIPOONDI-THERVOI_KANDIGAI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 05-04-2026 | 13:19 | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | TANTRANSCO | Correct Operation | Idly charged from Gummidipoondi |  |  | TRANSIENT FAULT
460 | 230KV-NCTPS-TONDIARPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 21-04-2026 | 06:01 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR OFF _ DUE TO LINE CONSTRAINTS |  |  | TRANSIENT FAULT
461 | 230KV-GUMMIDIPOONDI-THERVOI_KANDIGAI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 05-04-2026 | 16:28 | TANTRANSCO | Correct Operation | DEF TRIP |  |  | TANTRANSCO | Correct Operation | Idly charged from Gummidipoondi |  |  | TRANSIENT FAULT
462 | 230KV-NCTPS-KILPAUK-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-04-2026 | 08:11 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR OFF_COMPOSITE FEEDER |  |  | TRANSIENT FAULT
463 | 230KV-GUMMIDIPOONDI-NCTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 16-04-2026 | 01:08 | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TNPGCL |  |  |  |  | R Phase insulator flash over at location 31
464 | 230KV-NCTPS-KILPAUK-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 16-04-2026 | 01:08 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N_AR OFF COMPOSITE FEEDER |  |  | A t loc.12, R ph jumper cut
465 | 230KV-MANALI-CMRL_CENTRAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 17-04-2026 | 01:51 | TANTRANSCO | Correct Operation | ZONE.1,R,N_AR OFF COMPOSITE FEEDER |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N_AR OFF COMPOSITE FEEDER |  |  | At loc.48,R ph suspension insulator flashover
466 | 230KV-NCTPS-TONDIARPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 23-04-2026 | 03:31 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR OFF _ DUE TO LINE CONSTRAINTS |  |  | TRANSIENT FAULT
467 | 230KV-GUMMIDIPOONDI-NCTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 24-04-2026 | 16:27 | TANTRANSCO | Failure Operation | ZONE.1,B,N,AR LOCKOUT_BREAKER ISSUE | Breaker issue attended | Completed | TNPGCL |  |  |  |  | TRANSIENT FAULT
468 | 230KV-KORATTUR-MANALI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 29-04-2026 | 04:10 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR OFF_COMPOSITE FEEDER |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR OFF_COMPOSITE FEEDER
469 | 230KV-KORATTUR-AMBATUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 29-04-2026 | 04:10 | TANTRANSCO | Correct Operation | Holding |  |  | TANTRANSCO | Unwanted Operation | ZONE.1,B,N,AR OFF_COMPOSITE FEEDER | Augmentation of differential relay proposed | Pending | Over reached Tripping for 230 kV Manali feeder cable fault
470 | 230KV-ALAMATHY-MOSUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 14-04-2026 | 14:28 | TANTRANSCO | Correct Operation | ZONE.1,R,Y |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,Y |  |  | TRANSIENT FAULT
471 | 220KV-KAKINADA-PARAVADA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 25-04-2026 | 09:56 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
472 | 220KV-SHAPURNAGAR-RAYADURG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 01-04-2026 | 13:30 | TGTRANSCO | Unwanted Operation | Pole descrepancy at shapurnagar end | Availed L/C and brekaker tested and rectified | Completed | TGTRANSCO | Correct Operation |  |  |  | Pole descrepancy
473 | 220KV-SHAPURNAGAR-JANAGAON-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 04-04-2026 | 13:23 | TGTRANSCO | Correct Operation | line is composite line |  |  | TGTRANSCO | Correct Operation | line is composite line |  |  | Line to ground fault
474 | 220KV-NAGARAM-MANTHANI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 04-04-2026 | 20:16 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
475 | 220KV-NIRMAL-RENJAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 06-04-2026 | 21:24 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
476 | 220KV-NIRMAL-UTNOOR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 06-04-2026 | 21:24 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
477 | 220KV-KOTHAGUDEM_TPS-MIRYALAGUDA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 07-04-2026 | 02:13 | TGGENCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | Line to ground fault
478 | 220KV-KOTHAGUDEM_TPS-MIRYALAGUDA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 08-04-2026 | 03:46 | TGGENCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
479 | 220KV-WARANGAL_TG-MAHABUBABAD-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 08-04-2026 | 11:50 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
480 | 220KV-MALLARAM-DURSHED-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 10-04-2026 | 11:20 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | phase to phase fault
481 | 220KV-NIRMAL_OLD-JAGITIYAL-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 10-04-2026 | 13:00 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | phase to phase fault
482 | 220KV-BONGULUR-MAHESHWARAM_TG-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 10-04-2026 | 13:56 | TGTRANSCO | Correct Operation | A/R operated and tripped again on persistent fault |  |  | TGTRANSCO | Correct Operation | A/R operated and tripped again on persistent fault |  |  | Line to ground fault
483 | 220KV-MALYALAPALLI-VEMNOOR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 11-04-2026 | 14:10 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | phase to phase fault
484 | 220KV-SHAPURNAGAR-JANAGAON-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 12-04-2026 | 14:34 | TGTRANSCO | Correct Operation | line is composite line |  |  | TGTRANSCO | Correct Operation | line is composite line |  |  | Line to ground fault
485 | 400KV-KETHIREDDYPALLY-SHANKARAPALLY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 14-04-2026 | 00:28 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
486 | 220KV-NIRMAL_OLD-JAGITIYAL-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 16-04-2026 | 12:23 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
487 | 220KV-SHAPURNAGAR-JANAGAON-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 16-04-2026 | 13:21 | TGTRANSCO | Correct Operation | line is composite |  |  | TGTRANSCO | Correct Operation | line patrole done |  |  | Line to ground fault
488 | 220KV-DICHPALLY-RENEW_DICHPALLY-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 16-04-2026 | 13:58 | TGTRANSCO | Correct Operation | A/R operated and tripped again on persistent fault |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
489 | 220KV-KOTHAGUDEM_TPS-MIRYALAGUDA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 17-04-2026 | 02:23 | TGGENCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | Line to ground fault
490 | 220KV-JULURUPADU-KALLUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 17-04-2026 | 03:08 | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | Line to ground fault
491 | 220KV-GACHIBOWLI-SIVARAMPALLI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 20-04-2026 | 12:12 | TGTRANSCO | Correct Operation | line is composite line |  |  | TGTRANSCO | Correct Operation | line is composite line |  |  | Line to ground fault
492 | 220KV-WARANGAL-BOMMAKAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 21-04-2026 | 17:20 | PGCIL SR-1 | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
493 | 220KV-GAJWEL-KAMAREDDY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 22-04-2026 | 02:13 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
494 | 220KV-MALYALAPALLI-MEDARAM_TG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 23-04-2026 | 14:00 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | phase to phase fault
495 | 220KV-JAGITIYAL-VEMNOOR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 23-04-2026 | 21:17 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
496 | 220KV-SHAPURNAGAR-RAYADURG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 24-04-2026 | 12:37 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | phase to phase fault
497 | 220KV-GACHIBOWLI-SIVARAMPALLI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 27-04-2026 | 09:50 | TGTRANSCO | Correct Operation | line is composite line |  |  | TGTRANSCO | Correct Operation | line is composite line |  |  | Line to ground fault
498 | 220KV-SHAPURNAGAR-RAYADURG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 27-04-2026 | 13:16 | TGTRANSCO | Correct Operation | line is composite line |  |  | TGTRANSCO | Correct Operation | line is composite line |  |  | Line to ground fault
499 | 220KV-SRISAILAM_RIGHT_BANK-DINDI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | TGTRANSCO | 28-04-2026 | 17:55 | APGENCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
500 | 220KV-KALWAKURTHY-THIMAJIPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 28-04-2026 | 17:50 | TGTRANSCO | Correct Operation | A/R operated and tripped again on persistent fault,discs replaced in the line |  |  | TGTRANSCO | Correct Operation | A/R operated and tripped again on persistent fault,discs replaced in the line |  |  | Line to ground fault
501 | 230KV-MANALI-CMRL_CENTRAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 29-04-2026 | 14:31 | TANTRANSCO | Correct Operation | ZONE.1,B,N,LOCKOUT_AR OFF_ CABLE FEEDER |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,LOCKOUT_AR OFF_ CABLE FEEDER |  |  | TRANSIENT FAULT
502 | 230KV-KARAIKUDI(TN)-KARAMBAYAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 30-04-2026 | 12:50 | TANTRANSCO | Correct Operation | ZONE.2,B,N,LOCKOUT_DR DOWNLOADED AND VERYFIED EVOLVING FAULT. DURING CARRIER RECEIVE AT KKDI END FEEDER LOAD CURRENT WAS NORMAL AND DISTANCE NOT STARTED. AFTER THAT DISTANCE Z3 & Z2 STARTS THEN TRIPPED IN ZONE-2 TIME. |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR
503 | 230KV-NCTPS-TONDIARPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 30-04-2026 | 18:32 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR OFF _ DUE TO LINE CONSTRAINTS |  |  | At loc.15,Y ph suspension insulator flashover
504 | 230KV-ORAGADAM-SUNGAVARACHATRAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 03-04-2026 | 11:21 | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | TRANSIENT FAULT
505 | 230KV-NLC-TNEB-CUDDALORE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 03-04-2026 | 12:16 | TANTRANSCO | Correct Operation | ZONE.1,B,R |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,R |  |  | TRANSIENT FAULT
506 | 230KV-KAYATHAR(TN)-SANGANERI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 03-04-2026 | 13:15 | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | TANTRANSCO | Failure Operation | ZONE.2,Y,B | carrier aided scheme has to be checked | Pending | Line patrol done & No visible fault
507 | 230KV-VEERAPURAM-CUDDALORE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-04-2026 | 13:33 | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | TANTRANSCO | Correct Operation | Idly charged from Cuddalore |  |  | TRANSIENT FAULT
508 | 230KV-KARAMBAYAM-VELLALAVIDUTHI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 21-04-2026 | 11:18 | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | TRANSIENT FAULT
509 | 230KV-VEERAPURAM-CUDDALORE-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 23-04-2026 | 13:56 | TANTRANSCO | Correct Operation | idly charged from Cuddalore |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | TRANSIENT FAULT
510 | 230KV-KARAIKUDI(TN)-KAVANUR-4 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 23-04-2026 | 14:00 | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | TRANSIENT FAULT
511 | 230KV-ALAMATHY-MOSUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 27-04-2026 | 11:47 | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | Tree clearance work between location No.288 and 289
512 | 230KV-ACHARAPAKAM-VILLUPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 29-04-2026 | 11:09 | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | TRANSIENT FAULT
513 | 230KV-SALEM_230-SINGARPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 29-04-2026 | 16:13 | TANTRANSCO | Correct Operation | ZONE.1,R,Y |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,Y |  |  | TRANSIENT FAULT
514 | 230KV-KAYATHAR(TN)-VEERANAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 30-04-2026 | 16:02 | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | Y phase line decap at Loc. 73
515 | 230KV-ARNI-KANCHIPURAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 04-04-2026 | 15:00 | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TRANSIENT FAULT
516 | 230KV-ARNI-KANCHIPURAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 05-04-2026 | 12:41 | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | Location No: 756-757 tree fell on the line
517 | 230KV-KARAIKUDI(TN)-KARAMBAYAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 05-04-2026 | 13:11 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,TOR |  |  | TRANSIENT FAULT
518 | 230KV-SALEM_TN-THINGALUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 10-04-2026 | 07:08 | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | B phase conductor cut at Loc. in between loc. 47 & 48
519 | 230KV-KUNDAH3-KARAMADAI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 10-04-2026 | 12:54 | TNGECL |  |  |  |  | TANTRANSCO | Correct Operation | CAT,R,N,TOR |  |  | TRANSIENT FAULT
520 | 230KV-MYVADI-O.K.MANDAPAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 11-04-2026 | 10:53 | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | tree clearance between Loc.145 & 146
521 | 230KV-SALEM_230-SINGARPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 11-04-2026 | 14:52 | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TRANSIENT FAULT_Line Patrol done & No visible fault
522 | 230KV-THANJAVUR-THIRUVARUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 13-04-2026 | 02:18 | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | Location No:223 R-Phase disc flash over attended
523 | 230KV-TRICHY(TN)-JAMBUNATHAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 14-04-2026 | 05:38 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,TOR | AR SCHEME HAS TO BE CHECKED |  | TANTRANSCO | Correct Operation | CAT,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
524 | 230KV-NCTPS-SRIPERUMBADUR_TN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 15-04-2026 | 13:38 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | Fire under the tower. AR acted for first CG fault, then it converted to BC fault within relcaim time
525 | 230KV-SRIPERUMBADUR_TN-L&T_DATA_CENTRE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 17-04-2026 | 13:48 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1YR,N,TOR |  |  | TRANSIENT FAULT_Line Patrol done & No visible fault
526 | 230KV-SHOLINGANALLUR-SIRUSERI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 18-04-2026 | 11:04 | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | replacing the R ph insulator at loc 22
527 | 230KV-KARAIKUDI(TN)-KARAMBAYAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 18-04-2026 | 15:58 | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TRANSIENT FAULT
528 | 230KV-PUTHANSANTHAI-PUGALUR(TN)-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-04-2026 | 23:22 | TANTRANSCO | Correct Operation | Idly charged from Pugalur |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | Line patrol done & No visible fault
529 | 230KV-ARASUR-GOBI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 22-04-2026 | 13:42 | TANTRANSCO | Correct Operation | Idly charged from Gobi |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | Banana Tree falling between loc 196&197
530 | 230KV-O.K.MANDAPAM-PALLADAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 25-04-2026 | 13:58 | TANTRANSCO | Correct Operation | CAT,B,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | tree clearance between location 8 and 9
531 | 230KV-MYVADI-SEMBATTI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 30-04-2026 | 11:51 | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | Fire observed at Loc 129 & 130
532 | 230KV-METTUR2-SINGARPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 04-04-2026 | 13:36 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TRANSIENT FAULT
533 | 230KV-ARNI-KANCHIPURAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 04-04-2026 | 18:03 | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TRANSIENT FAULT
534 | 230KV-KAVANUR-MILAVITTAN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 06-04-2026 | 08:42 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,TOR |  |  | Loc no 369 Y ph Disc replaced
535 | 230KV-ALAMATHY-OPG-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 13-04-2026 | 17:35 | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | Line patrol done & No visible fault
536 | 230KV-KAYATHAR(TN)-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-04-2026 | 06:21 | TANTRANSCO | Correct Operation | CAT,Y,N,TOR |  |  | TNPGCL |  |  |  |  | LBB operated at TTPS end. After replacement of Y ph limb at TTPS end
537 | 230KV-Chekkanurani-SEMBATTI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-04-2026 | 11:54 | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TRANSIENT FAULT
538 | 230KV-TTPS-AUTO-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 21-04-2026 | 23:55 | TANTRANSCO | Unwanted Operation | ZONE.1,R,N,SOTF | The defective TNC switch has to be replaced | Pending | TNPGCL |  |  |  |  | Main 1 relay ( Micom P442) relay has issued SOTF trip during fault trip of 230kV Kayathar_ TTPS line ,due to Manual close opto input of the relay is continuously energised
539 | 230KV-SALEM_TN-PALKAPALYAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 22-04-2026 | 14:10 | TANTRANSCO | Correct Operation | CAT,R,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TRANSIENT FAULT
540 | 230KV-TRICHY-THANJAVUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 23-04-2026 | 07:03 | TANTRANSCO | Correct Operation | Idly charged from Thanjavur |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | Location No:101 R-Phase Jumber Cut
541 | 230KV-SALEM_230-SINGARPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 27-04-2026 | 15:07 | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | At Location 189 Polythene cover wounded at feeder and removed
542 | 230KV-KAYATHAR(TN)-TTPS-AUTO-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 30-04-2026 | 13:29 | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TRANSIENT FAULT
543 | 230KV-SALEM_TN-UNJANAI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 30-04-2026 | 16:29 | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
544 | 230KV-PUGALUR(TN)-PARATHIYUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 12-04-2026 | 13:56 | TANTRANSCO | Correct Operation | DEF TRIP |  |  | TANTRANSCO | Correct Operation | DT RECEIVED |  |  | clearing teak tree branches @location numbers 34 and 35
545 | 230KV-ALAGAR_KOVIL-VALATHUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 06-04-2026 | 23:30 | TANTRANSCO | Failure Operation | ZONE.1,R,N,AR LOCKOUT_ Due to carrier fail | OLTE defect at Alagarkoil end has to be attended | Pending | TANTRANSCO | Failure Operation | ZONE.1,R,N,AR LOCKOUT_ Due to carrier fail | OLTE defect at Alagarkoil end has to be attended | Pending | LOC.No.258 'R' PHASSE, LOC.No. 259 'R' PHASE, 247 'Y' PHASE AND 247 'R' PHASE FLASHED POLYMER REPLACED
546 | 230KV-SRIPERUMBADUR_TN-CONTROL_DATA_CENTRE_TN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 09-04-2026 | 12:25 | TANTRANSCO | Correct Operation | ZONE..1,Y,N,AR OFF _COMPOSITE FEEDER |  |  | TANTRANSCO | Correct Operation | ZONE..1,Y,N,AR OFF _COMPOSITE FEEDER |  |  | TRANSIENT FAULT
547 | 230KV-SRIPERUMBADUR_TN-CONTROL_DATA_CENTRE_TN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 15-04-2026 | 13:38 | TANTRANSCO | Correct Operation | ZONE.1,R,Y |  |  | TANTRANSCO | Correct Operation | CAT,R,Y |  |  | Fault due to fire under the tower
548 | 230KV-MILAVITTAN-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-04-2026 | 06:33 | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | TNPGCL |  |  |  |  | Loc no 1 & 2 Jumber cut
549 | 230KV-Chekkanurani-RENGANATHAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-04-2026 | 13:57 | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TANTRANSCO | Failure Operation | CAT,B,N _PD OPERATED due to main.2 relay issue | It is programmed to replace the main.2 relay. Line clear awaited | Pending | TRANSIENT FAULT
550 | 230KV-Chekkanurani-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 24-04-2026 | 01:08 | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TNPGCL |  |  |  |  | Loc no 1 to 7 Disc replaced
551 | 230KV-ALAGAR_KOVIL-VALATHUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 26-04-2026 | 05:18 | TANTRANSCO | Failure Operation | ZONE.1,Y,N,AR LOCKOUT due to carrier fail | OLTE defect at Alagarkoil end has to be attended | Pending | TANTRANSCO | Failure Operation | ZONE.1,Y,N,AR LOCKOUT due to carrier fail | OLTE defect at Alagarkoil end has to be attended | Pending | TRANSIENT FAULT
552 | 230KV-TARAMANI-SHOLINGANALLUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 27-04-2026 | 10:54 | TANTRANSCO | Correct Operation | LDP_BPHASE_ AR OFF COMPOSITE FEEDER |  |  | TANTRANSCO | Correct Operation | LDP_BPHASE_ AR OFF COMPOSITE FEEDER |  |  | TRANSIENT FAULT
553 | 230KV-SRIPERUMBADUR_TN-CONTROL_DATA_CENTRE_TN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 27-04-2026 | 17:09 | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | TANTRANSCO | Correct Operation | CAT,Y,B |  |  | TRANSIENT FAULT
554 | 230KV-TRICHY-TRICHY(TN)-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 07-04-2026 | 06:01 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
555 | 230KV-ARNI-KANCHIPURAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 11-04-2026 | 12:48 | TANTRANSCO | Failure Operation | ZONE.1,R,N,AR LOCKOUT | AR scheme has to be checked | Pending | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
556 | 230KV-TTPS-KINNIMANGLAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 17-04-2026 | 03:52 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | Loc 482 R Ph line decapped and disc flash over
557 | 230KV-MILAVITTAN-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-04-2026 | 06:01 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
558 | 400KV-GHANAPUR-RAMAGUNDAM-4 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 05-04-2026 | 04:58 | PGCIL SR-1 | Correct Operation |  |  |  | NTPC_RSTPS |  |  |  |  | AR successful on B-N fault at both ends
559 | 400KV-KHAMMAM_PG-VIJAYAWADA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 10-04-2026 | 05:05 | PGCIL SR-1 | Correct Operation |  |  |  | PGCIL SR-1 | Correct Operation |  |  |  | AR successful on B-N fault
560 | 400KV-GOOTY-RAICHUR_PG-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 21-04-2026 | 18:36 | PGCIL SR-1 | Correct Operation |  |  |  | PGCIL SR-1 | Correct Operation |  |  |  | AR successful on R-N fault
561 | 400KV-CUDDAPAH-NP_KUNTA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 30-04-2026 | 23:28 | PGCIL SR-1 | Correct Operation |  |  |  | PGCIL SR-1 | Correct Operation |  |  |  | AR successful on B-G fault