## P-Rec (Pending)
Status of Pending Implementation of PCSC Recommendations
Meeting Index | Details of Event | Date & Time | Reason | PCSC Recommendations | Utility Responsible for Implementation | Consolidated Status of Implementation | Individual Compliance Status | Consolidated Compliance Status
MULTI-UTILITIES
140/I/3 | Complete Outage of 765kV NCPS of TANTRANSCO and NCTPS ST3 of TANGEDCO | 24-01-2026 16:32 | 765kV NCTPS is connected radially to 765kV NCPS through 765kV NCPS-NCTPS-1&2 which is in turn radially connected to Ariyalur with 765kV Ariyalur NCPS-1&2. In the antecedent condition, 765kV Ariyalur NCPS-1 was under outage and 765kV NCPS and NCTPS ST3 were only radially connected through 765kV Ariyalur NCPS-2. The triggering incident is the Y-ph fault in the line leading to the tripping of the line. Tripping of the only connected line led to the Complete Outage of 765kV NCPS of TANTRANSCO and NCTPS ST3 of TANGEDCO and the running unit of NCTPS ST3 tripped and led to a generation loss of around 800MW | TANTRANSCO to verify the A/R reclaim time of all feeders at Ariyalur SS. | TANTRANSCO | cepc:TANTRANSCO: 30/03/2026 16:06:26: reclaim time revised in all feeders on 18.02.2026. Complied | Pending | Pending
140/I/3 | Complete Outage of 765kV NCPS of TANTRANSCO and NCTPS ST3 of TANGEDCO | 24-01-2026 16:32 | 765kV NCTPS is connected radially to 765kV NCPS through 765kV NCPS-NCTPS-1&2 which is in turn radially connected to Ariyalur with 765kV Ariyalur NCPS-1&2. In the antecedent condition, 765kV Ariyalur NCPS-1 was under outage and 765kV NCPS and NCTPS ST3 were only radially connected through 765kV Ariyalur NCPS-2. The triggering incident is the Y-ph fault in the line leading to the tripping of the line. Tripping of the only connected line led to the Complete Outage of 765kV NCPS of TANTRANSCO and NCTPS ST3 of TANGEDCO and the running unit of NCTPS ST3 tripped and led to a generation loss of around 800MW | TNPGCL to submit detailed report on Tripping of generator during the event | TNPGCL |  | Pending | Pending
140/I/4 | Complete outage of 230kV Betam and NTPC Ettayapuram | 30-01-2026 14:47 | 230kV NTPC Ettayapuram and Betam is connected to TTGS radially. The triggering incident is the Y-B fault in the 230kV TTGS-NTPC Ettayapuram line due to conductor snapping leading to the tripping the line on line differential protection. During the same time, the fault was sensed in Z1 at Betam end only and 3ph tripped. Tripping of the radial lines led to the complete outage of 230kV Betam and NTPC Ettayapuram | 1. PGCIL SR-II to periodic maintaince activities at TTGS SS. 2. PGCIL SR-II to report equipment failure to CEA. | PGCIL SR-II |  | Pending | Pending
140/I/4 | Complete outage of 230kV Betam and NTPC Ettayapuram | 30-01-2026 14:47 | 230kV NTPC Ettayapuram and Betam is connected to TTGS radially. The triggering incident is the Y-B fault in the 230kV TTGS-NTPC Ettayapuram line due to conductor snapping leading to the tripping the line on line differential protection. During the same time, the fault was sensed in Z1 at Betam end only and 3ph tripped. Tripping of the radial lines led to the complete outage of 230kV Betam and NTPC Ettayapuram | M/s Betam Wind to consult OEM and submit report regarding the over reach observed during the event. | M/s Betam Wind |  | Pending | Pending
140/I/9 | Complete outage of 220kV Chintur of APTRANSCO and Tripping of Bus-2 at Lower Sileru of APGENCO | 11-02-2026 14:08 | In the antecedent conditions, at 220kV Lower Sileru is under Bus split condition where in 220kV Lower Sileru-Bommuru, 220kV Lower Sileru-Donkarayi is in Bus-1 and 220kV Lower Sileru-Asupaka and 220kV Lower Sileru-Chintur is in Bus-2 and 220kV Lower Sileru-Asupaka was under planned outage due to Tree Cutting works leading to Bus-2 being radially connected through 220kV Lower Sileru-Chintur which was inturn connected through 220kV Lower Sileru-Chintur-BG Kothur segment. The triggering incident is the R-B fault in 220kV Chintur-BG Kothur line and tripping of the line led to the Complete outage of 220kV Chintur of APTRANSCO and Tripping of Bus-2 at Lower Sileru of APGENCO. | APGENCO to provide the detailed report on the genarator frequency/speed variations during the incident and generator tripping values for over frequency protection. | APGENCO |  | Pending | Pending
140/I/9 | Complete outage of 220kV Chintur of APTRANSCO and Tripping of Bus-2 at Lower Sileru of APGENCO | 11-02-2026 14:08 | In the antecedent conditions, at 220kV Lower Sileru is under Bus split condition where in 220kV Lower Sileru-Bommuru, 220kV Lower Sileru-Donkarayi is in Bus-1 and 220kV Lower Sileru-Asupaka and 220kV Lower Sileru-Chintur is in Bus-2 and 220kV Lower Sileru-Asupaka was under planned outage due to Tree Cutting works leading to Bus-2 being radially connected through 220kV Lower Sileru-Chintur which was inturn connected through 220kV Lower Sileru-Chintur-BG Kothur segment. The triggering incident is the R-B fault in 220kV Chintur-BG Kothur line and tripping of the line led to the Complete outage of 220kV Chintur of APTRANSCO and Tripping of Bus-2 at Lower Sileru of APGENCO. | APTRANSCO to validate the relay settings of Chintur SS in the PDMS portal. | APTRANSCO | dee2sp:APTRANSCO: 07/04/2026 14:53:22: On 25/03/26, settings calculations were emailed to SRPC along with the following information, Zone-3 element in P444 relay act as Zone-4 protection and Zone-4 element in P444 relay act as Zone-5 element. Hence, the calculated settings are inline with the protection philosophy. At Chinturu end, Main-2 relay (ABB make REL670) settings are communicated to PRDC by MRT wing/Rajamahendravaram and same was confirmed with PRDC. | Complied | Pending
140/I/9 | Complete outage of 220kV Chintur of APTRANSCO and Tripping of Bus-2 at Lower Sileru of APGENCO | 11-02-2026 14:08 | In the antecedent conditions, at 220kV Lower Sileru is under Bus split condition where in 220kV Lower Sileru-Bommuru, 220kV Lower Sileru-Donkarayi is in Bus-1 and 220kV Lower Sileru-Asupaka and 220kV Lower Sileru-Chintur is in Bus-2 and 220kV Lower Sileru-Asupaka was under planned outage due to Tree Cutting works leading to Bus-2 being radially connected through 220kV Lower Sileru-Chintur which was inturn connected through 220kV Lower Sileru-Chintur-BG Kothur segment. The triggering incident is the R-B fault in 220kV Chintur-BG Kothur line and tripping of the line led to the Complete outage of 220kV Chintur of APTRANSCO and Tripping of Bus-2 at Lower Sileru of APGENCO. | TGTRANSCO to validate the relay settings of BG Kothuru SS in the PDMS portal. | TGTRANSCO | deprotection1:TGTRANSCO: 04/04/2026 14:36:00: Already verified and the settings are found to be in order. The same is mailed to SRPC on 04-04-2026. The point may be dropped. | Complied | Pending
140/I/10 | Complete outage of 220kV Chintur of APTRANSCO and Tripping of Bus-2 at Lower Sileru of APGENCO | 13-02-2026 12:20 | In the antecedent conditions, at 220kV Lower Sileru is under Bus split condition where in 220kV Lower Sileru-Bommuru, 220kV Lower Sileru-Donkarayi is in Bus-1 and 220kV Lower Sileru-Asupaka and 220kV Lower Sileru-Chintur is in Bus-2 and 220kV Chintur-BG Kothur was under planned outage due to Tree Cutting works leading to Bus-2 being radially connected through 220kV Lower Sileru-Asupaka. The triggering incident is the Y-G fault in 220kV Lower Sileru-Asupaka and tripping of the line led to the Complete outage of 220kV Chintur of APTRANSCO and Tripping of Bus-2 at Lower Sileru of APGENCO. | APGENCO to review the A/R logic at Lower Sileru. | APGENCO |  | Pending | Pending
140/I/10 | Complete outage of 220kV Chintur of APTRANSCO and Tripping of Bus-2 at Lower Sileru of APGENCO | 13-02-2026 12:20 | In the antecedent conditions, at 220kV Lower Sileru is under Bus split condition where in 220kV Lower Sileru-Bommuru, 220kV Lower Sileru-Donkarayi is in Bus-1 and 220kV Lower Sileru-Asupaka and 220kV Lower Sileru-Chintur is in Bus-2 and 220kV Chintur-BG Kothur was under planned outage due to Tree Cutting works leading to Bus-2 being radially connected through 220kV Lower Sileru-Asupaka. The triggering incident is the Y-G fault in 220kV Lower Sileru-Asupaka and tripping of the line led to the Complete outage of 220kV Chintur of APTRANSCO and Tripping of Bus-2 at Lower Sileru of APGENCO. | TGTRANSCO to configure the DR at Asupaka SS asper the FOLD recommendations. | TGTRANSCO |  | Pending | Pending
140/ii/2 | Tripping of 400kV Bus-1 of Simhadri TPS of NTPC | 30-01-2026 11:08 | The triggering incident is the Y-ph CT failure of 412Bay (Main Bay connected to 400kV Simhadri-Kalpakka-3) at Simhadri leading to Bus Bar protection operation and tripping of all the breakers connected to 400kV Bus-1 of Simhadri TPS. During which due to the delay in tripping of TEED protection led to the delay in clearing of the fault and also Z2 was sensed in remote end. During the same time 400kV Khammam-Kalpakka tripped only at Khammam end on Z2 due to the delay in clearing of fault. Subsequently 400kV Simhadri-Kalpakka-3 line tripped on Z2 at Kalpakka end. After which due to OPGW cable cut 400kV Simhadri-Kalpakka-4 and 400kV Gazuwaka-Kalpakka tripped. During the event Hinduja unit 2 tripped due to flame failure. | 1.APTRANSCO to indentify all such locations of towers, where separate earth wire is not layed. and to immediately start laying earth wire in such locations. Specifically on tower spans numbered 5 &6, 6&7, and 7&8, works for laying of separate earth wire on the tower should be taken up on immediate basis. 2.APTRANSCO to take appropriate actions in avoiding the interruptions in power communication through OPGW for known and rectifiable issues. | APTRANSCO | dee2sp:APTRANSCO: 07/04/2026 14:53:22: 1. 400kV/O&M wing informed that , laying of earth wire between loc.5-6 in line-3 was done on 10/03/26,laying of earth wire between loc 3-4 of Kalapaka- Vemagiri line completed on 13/03/26, in between loc 7-8 earth wire is existing. 2. To avoid OPGW/Earth wire failures on the existing EHT lines, alternative Optical route path was established with ADSS cable and is in service for both voice/protection. | Pending | Pending
140/ii/2 | Tripping of 400kV Bus-1 of Simhadri TPS of NTPC | 30-01-2026 11:08 | The triggering incident is the Y-ph CT failure of 412Bay (Main Bay connected to 400kV Simhadri-Kalpakka-3) at Simhadri leading to Bus Bar protection operation and tripping of all the breakers connected to 400kV Bus-1 of Simhadri TPS. During which due to the delay in tripping of TEED protection led to the delay in clearing of the fault and also Z2 was sensed in remote end. During the same time 400kV Khammam-Kalpakka tripped only at Khammam end on Z2 due to the delay in clearing of fault. Subsequently 400kV Simhadri-Kalpakka-3 line tripped on Z2 at Kalpakka end. After which due to OPGW cable cut 400kV Simhadri-Kalpakka-4 and 400kV Gazuwaka-Kalpakka tripped. During the event Hinduja unit 2 tripped due to flame failure. | 1.NTPC Simhadri to pursue the root cause analysis report with the OEM (GE) for recurring surface tracking failures of GE ICTs and share with SRPC/SRLDC and NTPC is suggested all the procedures need to be strictly followed while performing hotline washing. 2.NTPC Simhadri to conduct comprehensive testing of TEED protection for Simhadri-Kalpakka lines 2, 3, and 4 and confirm actual operating time and behaviour in coordination with APTRNASCO. 3.NTPC simhadri to verify and ensure that TEED protection is configured to transmit Direct Transfer Trip (DT) to remote end, in addition to the existing tie-breaker based DT logic. 4.NTPC may explore planned offline cleaning (with line shutdown) as an alternative to hotline washing for the Kalpakka lines. 5.NTPC Simhadri to share final third-party protection audit report (ERDS) with SRPC and SRLDC upon receipt. | NTPC Simhadri |  | Pending | Pending
140/ii/2 | Tripping of 400kV Bus-1 of Simhadri TPS of NTPC | 30-01-2026 11:08 | The triggering incident is the Y-ph CT failure of 412Bay (Main Bay connected to 400kV Simhadri-Kalpakka-3) at Simhadri leading to Bus Bar protection operation and tripping of all the breakers connected to 400kV Bus-1 of Simhadri TPS. During which due to the delay in tripping of TEED protection led to the delay in clearing of the fault and also Z2 was sensed in remote end. During the same time 400kV Khammam-Kalpakka tripped only at Khammam end on Z2 due to the delay in clearing of fault. Subsequently 400kV Simhadri-Kalpakka-3 line tripped on Z2 at Kalpakka end. After which due to OPGW cable cut 400kV Simhadri-Kalpakka-4 and 400kV Gazuwaka-Kalpakka tripped. During the event Hinduja unit 2 tripped due to flame failure. | SRLDC agreed to carry out a fresh short circuit modelling study (single-phase and three-phase fault levels) for the Simhadri/Kalpakka region incorporating the current network, to determine whether equipment ratings require upgrading and for further review of protection settings. | SRLDC | ArthiV~1776856274:SRLDC: 04/04/2026 17:48:05: The same has been communicated to the concerned team. A meeting may be scheduled with NTPC Simhadri in this regards for the requirements and the same will be updated further | Pending | Pending
141/I/1 | Complete outage of 230kV SR Pudur SS of TANTRANSCO SS. | 22-02-2026 04:15 | As per the reports submitted, 230kV SR Pudur SS is operating with single bus configuration. At 4:15hrs Y-G fault was observed in 230kv SR Pudur Sanganeri line and the line tripped. At 4:57hrs, R-G fault was observed in 230kV Kudankulam SR Pudur line and the line tripped. After tripping of both 230kV ines, 230kV SR Pudur bus was charged through 110kV lines from Udayathur and Sanganeri SS. Eventually, 110kV lines tripped on over loading at remote ends and this led to complete outage of 230kV SR Pudur SS. | 1.TANTRANSCO to revise A/r dead time of all feeders at 230kV Sanganeri SS to 1 Sec. 2.TANTRANSCO to ensure Double bus operation of all 220kV & Substations. 3.TANTRANSCO to rectify the DR time sychronization issue at SR Pudur 4.TANTRANSCO to furnish DR at Sangareni end during the incident | TANTRANSCO | cepc:TANTRANSCO: 04/05/2026 16:45:23: 1.dead time revised to 1 sec 2. Action is being taken to implement the double bus operation wherever feasible 3.GPS is available & IEDs sync with GPS 4. since old relay 3sec DR could not be assign . It is proposed to replace old relay with spare one . Awaiting LIne clear | Pending | Pending
141/I/1 | Complete outage of 230kV SR Pudur SS of TANTRANSCO SS. | 22-02-2026 04:15 | As per the reports submitted, 230kV SR Pudur SS is operating with single bus configuration. At 4:15hrs Y-G fault was observed in 230kv SR Pudur Sanganeri line and the line tripped. At 4:57hrs, R-G fault was observed in 230kV Kudankulam SR Pudur line and the line tripped. After tripping of both 230kV ines, 230kV SR Pudur bus was charged through 110kV lines from Udayathur and Sanganeri SS. Eventually, 110kV lines tripped on over loading at remote ends and this led to complete outage of 230kV SR Pudur SS. | NPCIL KKNPP to furnish DR at KKNPP end during the incident | NPCIL KKNPP |  | Pending | Pending
141/II/1 | Tripping of 400kV Bus-2 of 400kV Yelahanka_PG SS of PGCIL SR-2 | 12-02-2026 07:26 | As per the reports submitted, the triggering incident was Y-G fault in 400kV Bus-2 of 400kV Yelahanka_PG SS. Immediately, 400kV Bus-2 BBP operated and all the elements connected to the bus tripped | KPTCL to rectify the DR time sync issue at Neelamanga SS and Yelahanka SS. | KPTCL |  | Pending | Pending
141/II/1 | Tripping of 400kV Bus-2 of 400kV Yelahanka_PG SS of PGCIL SR-2 | 12-02-2026 07:26 | As per the reports submitted, the triggering incident was Y-G fault in 400kV Bus-2 of 400kV Yelahanka_PG SS. Immediately, 400kV Bus-2 BBP operated and all the elements connected to the bus tripped | PGCIL SR-II to report Equipment failure to CEA. | PGCIL SR-II |  | Pending | Pending
141/II/1 | Tripping of 400kV Bus-2 of 400kV Yelahanka_PG SS of PGCIL SR-2 | 12-02-2026 07:26 | As per the reports submitted, the triggering incident was Y-G fault in 400kV Bus-2 of 400kV Yelahanka_PG SS. Immediately, 400kV Bus-2 BBP operated and all the elements connected to the bus tripped | SRLDC to furnsih the reasons for Inphase currents observed during the event and necessary remedial actions to be taken to the forum. | SRLDC | SRLDC_Protection1:SRLDC: 04/05/2026 09:06:34: As deliberated during the meeting, the reason for the in phase currents is due to the zero sequence contribution during fault feeding by radial source. This is a special case where in since the network was radial at LV side and no interconnection such zero sequence currents would be observed and hence any modification in the settings may lead to non operation in genuine cases and would be problematic and the same was deliberated during the meeting. Further remedial actions may be taken after deliberations during the meeting with all entities opinion. | Pending | Pending
141/II/4 | Tripping of 400kV Bus-1 and 2 at Simhadri TPS of NTPC | 25-02-2026 16:03 | The triggering incident is the R-ph CT tracking in 400KV-SIMHADRI-KALPAKKA-4 main bay leading to BBP operation and tripping of all the main breakers connected to Bus-2 and 400KV-SIMHADRI-KALPAKKA-4. Subsequently, after around 5s, Bus-1 BBP operated due to R-ph CT tracking in 400KV-SIMHADRI-KALPAKKA-3 main bay leading to tripping of all elements connected to 400kV Bus-1 and 2 at Simhadri TPS of NTPC. This led to the tripping of Unit-2 and generation loss of around 420MW. During the event, 400kV Bus-3 and 4 were in service at Simhadri TPS | 1.NTPC Simhadri to expecite the process of replacing porcelien insulator with Polymer insulator. 2.NTPCSimhadri to verify the AR logic at their end and ensure single pole AR operation. | NTPC-Simhadri |  | Pending | Pending
141/II/4 | Tripping of 400kV Bus-1 and 2 at Simhadri TPS of NTPC | 25-02-2026 16:03 | The triggering incident is the R-ph CT tracking in 400KV-SIMHADRI-KALPAKKA-4 main bay leading to BBP operation and tripping of all the main breakers connected to Bus-2 and 400KV-SIMHADRI-KALPAKKA-4. Subsequently, after around 5s, Bus-1 BBP operated due to R-ph CT tracking in 400KV-SIMHADRI-KALPAKKA-3 main bay leading to tripping of all elements connected to 400kV Bus-1 and 2 at Simhadri TPS of NTPC. This led to the tripping of Unit-2 and generation loss of around 420MW. During the event, 400kV Bus-3 and 4 were in service at Simhadri TPS | APTRANSCO to expedite the OPGW replacement works on Simhadri Kalpakka Line. | APTRANSCO | eesp:APTRANSCO: 01/05/2026 17:17:59: OPGW replacement works on Simhadri-Kalapaka line will be expedited. | Pending | Pending
141/IV/2 | 400KV-KAIGA-GUTTUR-2 | 24-02-2026 15:45 | As per the reports submitted, the triggering incident is the B-G fault in the line. At both ends the fault was sensed in Z1 and at both ends AR did not operate and 3ph tripped. | KPTCL to review the non-operation of Auto reclosure at Guttur end of 400KV-KAIGA-GUTTUR-line 2. | KPTCL |  | Pending | Pending
141/IV/2 | 400KV-KAIGA-GUTTUR-2 | 24-02-2026 15:45 | As per the reports submitted, the triggering incident is the B-G fault in the line. At both ends the fault was sensed in Z1 and at both ends AR did not operate and 3ph tripped. | NPCIL Kaiga to review the non-operation of Auto reclosure at Kaiga end of 400KV-KAIGA-GUTTUR- line 2. | NPCIL Kaiga |  | Pending | Pending
142/I/4 | Complete Outage 220kV Renew_Surya_Koppal of RENEW | 18-03-2026 22:28 | 220kV Renew_Surya_Koppal is connected radially to KOPPAL through 220 kV-KOPPAL-Renew_Surya_Koppal-1. The triggering incident is the R-G fault in the 220 kV-KOPPAL-Renew_Surya_Koppal-1 line and tripping of the only line connected to 220kV Renew_Surya_Koppal led to the Complete Outage 220 kV Renew_Surya_Koppal of RENEW | M/s Indigrid to submit detailed report for the event. M/s Indigrid to submit DR, EL, FIR to SRLDC & SRPC for the event. | M/s Indigrid |  | Pending | Pending
142/I/4 | Complete Outage 220kV Renew_Surya_Koppal of RENEW | 18-03-2026 22:28 | 220kV Renew_Surya_Koppal is connected radially to KOPPAL through 220 kV-KOPPAL-Renew_Surya_Koppal-1. The triggering incident is the R-G fault in the 220 kV-KOPPAL-Renew_Surya_Koppal-1 line and tripping of the only line connected to 220kV Renew_Surya_Koppal led to the Complete Outage 220 kV Renew_Surya_Koppal of RENEW | M/s Renew to enable the Auto reclosure at their end. | M/s Renew |  | Pending | Pending
140/III/8 | 400KV/220KV CUDDAPAH-ICT-3 | 30-01-2026 11:44 | As per the reports submitted, the triggering incident is the tripping of 400KV/220KV CUDDAPAH-ICT-3 only at HV side due to the external LBB operation during the testing activities which were being carried out at CUDDAPAH(AP) during the wiring scheme implementation for Single Phase LBB logic (as per information received from APTRANSCO). During pre-configuration works, the tripping was disabled temporarily by disconnecting positive trip links for all 220kV feeders including PGCIL-I, 2&3 at 220kV CUDDAPAH (AP) station. 96 operation of PGCIL-3 at CUDDAPAH (AP) signal was taken for group relay tripping at PGCIL end and due to oversight, the said signal was not disabled at CUDDAPAH (AP) which led to the tripping of the ICT. | APTRANSCO to ensure SOP during testing activities. | APTRANSCO | dee2sp:APTRANSCO: 08/04/2026 12:16:25: It is to submit that, PCSC recommendation was communicated to the concerned and they informed that they will ensure the SOP during testing of all protection activities. | Complied | Complied
140/VI/19 | 220KV-CHITTOOR_AP-THIRUVALAM_TN-1 | 19-02-2026 18:00 | 220KV-CHITTOOR_AP-THIRUVALAM_TN-1 | APTRANSCO to rectify the DR time synchronization issue at CHITTOOR_AP - 220KV | APTRANSCO | eesp:APTRANSCO: 01/05/2026 17:16:19: Time synchronization will be provided in 15 days. dee2sp:APTRANSCO: 15/05/2026 12:22:38: On 09/05/2026 existing power relay at 220kV Chittoor SS on Tiruvallam feeder (GE make F650 relay) replaced with (GE make P14DL) relay and adopted SPS settings, provided GPS time synchronization tested and results found satisfactory. | Pending | Pending
141/VI/10 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1 | 01-03-2026 12:10 | Station at which DR time synchronisation was not observed SRISAILAM_RIGHT_BANK - 220KV | APGENCO to rectify the DR time synchronization issue at SRISAILAM RIGHT BANK - 220KV | APGENCO | PROTECTION.HPC:TGGENCO: 05/05/2026 10:55:52: There is no DR time Synchronization issue at NSHES end. In recent following 3 trippings of the above feeder, we can observe the DR time Synchronization . 1. 13/03/2026 @ 13:32 Hrs 2. 26/03/2026 @ 12:35 Hrs 3. 27/03/2026 @ 11:40 Hrs | Complied | Complied
142/I/12 | Complete Outage of 220kVTadipathri | 10-04-2026 14:56 | During antecedent conditions, 220kV Tadipathri Boyareddypalli line was under LC. 220kV Tadipathri SS was being fed through 132kV network through 132kV Tadipathri Kondapuram and 132kV Gooty RS-Gudipadu-Ankireddypalli-Komali- Tadipatri feeders. As per the reports submitted, at 14:56hrs, 132kV Tadipathri Ankireddypalli line tripped on R-G fault. Subsequently, 132kV Ankireddypalli Gudipadu feeder tripped on non directional over current protection at Ankireddypalli end. Tripping of both sources led to complete otuage of 220kV Tadipathri SS. | APTRANSCO to comply with CEA Safety Regulations w.r.t the TAP connection at 132kV connectivity for Penna Cement. APTRANSCO to provide DR time sync for 132kV Tadipatri and Kondapuram SS. | APTRANSCO |  | Pending | Pending
142/III/5 | 20KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1 | 26-03-2026 12:35 | As per the reports submitted the triggering incident was high resistance R-G fault in the line (based on the DR, it can be observed from R/X plot that the fault angle at Srisailam end is around 0 degrees and at Nagarjuna Sagar end the fault angle is around 13 degrees). From both the ends, DEF operated and 3 ph tripped. | APGENCO to review the Non configuration of DT for DEF.APGENCO to review the Time Synch issue at NagarjunaSagar RB APGENCO to submit the detailed report on the incident | APGENCO |  | Pending | Pending
142/III/6 | 00kV-KRISHNAPATNAM-SEIL_P2-1 | 28-03-2026 17:23 | In the antecedent condition, 409 Main CB which is connected to Bus-2 was under LC and the line was only connected through 408 Tie Breaker. As per the reports submitted, the triggering incident is the opening of Y-pole breaker without any fault in 400 kV-KRISHNAPATNAM-SEIL_P2-1 only at KRISHNAPATNAM end. After which Pole discrepancy operated after around 7.5 seconds leading to the tripping of R and B poles. This led to the 3ph tripping at KRISHNAPATNAM end. The line was holding at SEIL_P2 end. | APGENCO to review the tripping of Y-ph pole without any fault. APGENCO to review Pole Discrepancy timer at 400KV-KRISHNAPATNAM APGENCO to review the Time Synch issue at Krishnapatnam APGENCO to submit the detailed report on the incident. | APGENCO |  | Pending | Pending
142/III/8 | 400KV-KALPAKKA-ASUPAKA-1 | 03-04-2026 12:03 | As per the reports submitted, the triggering incident was B-G fault in the line. At Asupaka end, the fault was sensed in zone-1 and B-pole opened. After around 1000ms, A/R operated and the fault was sensed again in zone-1 and line tripped on persistent fault with no delay. At KALPAKKA end, the fault was sensed in carrier aided zone-2 and B-pole opened. After around 1200ms, A/R operated and the fault was sensed in zone-2 and the line tripped with a delay of 560ms | APTRANSCO to submit the detailed OEM report on the AR operation at Kalpakka | APTRANSCO |  | Pending | Pending
142/VI/11 | 220KV-SRISAILAM_RIGHT_BANK-DINDI-1 | 26-03-2026 12:17 | DR Time Synchronization issue at SRISAILAM_RIGHT_BANK - 220KV | APGENCO to rectify the DR Time Synchronization issue at SRISAILAM_RIGHT_BANK - 220KV | APGENCO |  | Pending | Pending
142/VI/47 | 220KV-KOTHAGUDEM_TPS-TIRUVURU-1 | 20-04-2026 15:04 | DR Time Synchronization issue at TIRUVURU - 220KV | APTRANSCO to rectify the DR Time Synchronization issue at TIRUVURU - 220KV | APGENCO |  | Pending | Pending
140/III/11 | 400KV-BHOOPALAPALLY-WARANGAL-2 | 10-02-2026 18:34 | As per the reports submitted, the triggering incident was Pole discrepancy relay maloperation and gave trip at Bhoopalapally end in the line. The line was holding at Warangal end. | TGGENCO to rectify the Pole discrepancy issue at 400kV Bhoopalapally. | TGGENCO |  | Pending | Pending
140/IV/1 | 220KV-VIJAYAWADA-KOTHAGUDEM_TPS-1 | 25-01-2026 00:49 | As per the reports submitted, the triggering incident was B-G fault in the line. The fault distance from Vijayawada end was 115.2 kms and from Kothagudem end was 2.28 kms. At Vijayawada end, the fault was sensed in Z1, A/R did not operate. At KTPS end, the ABC trip operated and the line was tripped. | TGGENCO to review the A/R operation at KOTHAGUDEM_TPS | TGGENCO |  | Pending | Pending
140/VI/2 | 220KV-VIJAYAWADA-KOTHAGUDEM_TPS-1 | 25-01-2026 00:49 | 220KV-VIJAYAWADA-KOTHAGUDEM_TPS-1 | TGGENCO to rectify the DR time synchronization issue at 220kV KTPS | TGGENCO |  | Pending | Pending
141/III/9 | 400KV/11.5KV YADADRI TPP-ST-2 | 09-03-2026 00:09 | As per the reports submitted, the triggering incident in the downstream 11kV fault. During the event, LV REF Protection operated and 3ph trip | TGGENCO to submit a detailed report on the incident. | TGGENCO |  | Pending | Pending
141/VI/9 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1 | 01-03-2026 12:10 | Station at which DR time synchronisation was not observed NAGARJUNASAGAR_TS - 220KV | TGGENCO to rectify the DR time synchronization issue at NAGARJUNASAGAR TS 220KV | TGGENCO |  | Pending | Pending
142/I/13 | Complete Outage of 220kV Upper Jurala of TGGENCO | 14-04-2026 05:32 | 220kV Upper Jurala PH was radially connected through 220kV Upper Jurala-Raichur-1&2. The triggering incident is the BBP maloperation at Upper Jurala leading to the tripping of 220kV Upper Jurala-Raichur-1&2. With the tripping of the only connected lines to the 220kV Upper Jurala led to the complete outage of 220kV Upper Jurala of TGGENCO | TGGENCO to review the CT secondary circuit. Non availability of SCADA SOE at UPPER_JURALA end needs review | TGGENCO |  | Pending | Pending
142/II/6 | Tripping of 400kV Bus-2 at Dichipally of TGTRANSCO | 04-04-2026 22:26 | The triggering incident is the R-G Bus fault in 400 kV Bus-2 due to bus post insulator failure leading to Bus Bar protection Operation and leading to the tripping of 400kV Bus-2 at Dichipally due to inclement weather conditions. 400 kV Dichipally-Nirmal line and 400 kV/220 kV Dichipally ICT-4 got tripped during the event. | TGTRANSCO to review the distance protection settings at Nirmal end. | TGTRANSCO |  | Pending | Pending
140/I/5 | Complete outage of 220kV Guttur SAS, Neelagunda and Tripping of 220kV Bus-1 of Guttur SS of KPTCL | 02-02-2026 01:31 | In the antecedent conditions, 220kV Neelagunda-Ittagi was under idle charged condition from Neelagunda end and hence 220kV Neelagunda is radially connected to 220kV Guttur SS. 220kV Guttur SAS is connected to Bus-1 at Guttur SS. The triggering incident is the failure of B-ph CT in 220KV-GUTTUR-DAVANGERE-2 at GUTTUR end leading to Bus bar protection operation and tripping of all the elements connected to Bus-1 at Guttur SS. Since 220kV Neelagunda and Guttur SAS are only connected Bus-1, with the tripping of Bus-1 led to the complete outage of 220kV Neelagunda and Guttur SAS station. | 1. KPTCL to rectify the DR time sync issue at Guttur SS. 2. KPTCL to verify the Carrier wiring of all lines in Guttur SS. 3. KPTCL to furnish CT failure report to CEA. | KPTCL | Puspha:KPTCL: 05/04/2026 18:53:35: 1. Attended 2,Carrier issue attended and ascertained through end to end test 3.r Failure report is sent to CEA | Complied | Complied
140/I/8 | Complete Outage of 220kV Orient Cement and Tripping of 220kV Bus-1 of 220kV Sedam SS of KPTCL | 10-02-2026 15:15 | 220kV Orient cement is radially fed from 220kV Bus-1 of Sedam SS. As per the reports submitted, at 220kV Sedam SS, while attending to the issue on Line CB of 220kV Sedam Ramasamudra Line-1, the breaker was hand-tripped. During hand tripping, the Y and B poles opened, however, the R pole did not open. Subsequently, 86 A & B operated due to the operation of IN>2 only in the M1 (P442 relay) with a definite time delay of 2s but still the breaker did not open and LBB was initiated. Due to the non-opening of the R phase limb, LBB operated and tripped all the elements connected to 220 kV Bus-1. The bus coupler was already in the open condition. Tripping of 220kv Sedam Bus-1 led to complete outage of 220kV Orient Cement. | 1. KPTCL to configure DR as per FOLD Committee recommendations at Sedam SS. 2. KPTCL to rectify the DT issue for LBB operation at Sedam SS. 3. KPTCL to verify the VT fuse fail logic for all feeders at Sedam SS. | KPTCL | Puspha:KPTCL: 05/04/2026 19:02:17: 1. DR configuration will be verified and impement as per the standard signal list given by SRPC earlier. 2. For DT configuration for LBB, OPGW link is to be established 3. Attended. VTF logic reviewed in other lines in Sedam | Pending | Pending
140/II/4 | Tripping of 400kV Bus-2 of 400kV Talaguppa SS of KPTCL | 07-02-2026 06:28 | As per the reports submitted, while hand-tripping the 125 MVAR Bus Reactor-2, the Bus Reactor-2 circuit breaker (CB-410R.52) experienced a flashover on the R-phase limb, and the R-phase lightning arrester also flashed over. Immediately, it was suspected that the LBB protection of the bus reactor operated, resulting in the tripping of all main breakers connected to the 400 kV Talaguppa Bus-2. However, a DT was sent to the remote ends of the 400 kV Talaguppa Hassan line and 400 kV Talaguppa Nelamangala lines. At the remote ends, the lines tripped, and due to a rise in voltage, the overvoltage protection operated after 8 seconds. Subsequently, a DT was sent to the Talaguppa end, causing the tripping of the tie breakers of these lines, and the lines tripped. | KPTCL to review the relay settings at 400kV Tallagupp SS. | KPTCL | Puspha:KPTCL: 05/04/2026 18:51:40: Relay settings at Talaguppa are verified and it is in order | Complied | Pending
140/III/15 | Multiple trippings at 400/220kV Guttur SS | 13-02-2026 15:00 | As per the reports submitted, the triggering incident is the R-G fault in Guttur-Haveri-1 line. At Guttur end, the fault was sensed in Main-1 in Z2 only as the Main-2 was out of service during the event. However even after sensing the fault in Z2 and 86A/B operated after around 350 ms (Z2 time trip), trip was not extended to the breakers (as per DR) and also LBB did not operate and hence the fault continued to be fed, after which ICT-1 and ICT-2 tripped at Guttur end on EF protection operated where in 400/220kV ICT-1, IN>1 operated around 100 ms prior to that of 400/220kV ICT-2 at around 15:01:22:840 Hrs. With the tripping of the ICTs, the fault continues to be fed through 220kV side and eventually fault developed into R-Y-G fault in Z1 and 3 ph tripped to clear the fault. In the antecedent condition, 220kV Guttur-Haveri lines were under idle charged condition from Guttur end. | 1. KPTCL to rectify the time synchronization issue at Guttur SS. 2. KPTCL was advised to ensure the availability of the Main2 relay for the 220 kV Guttur Haveri Line2 at the earliest. | KPTCL | Puspha:KPTCL: 05/04/2026 18:50:53: 1. Attended. 2, Main-2 relay power supply card is used to 400kV line. Action is taken to procure power supply cards from the OEM on proprietary basis. | Pending | Pending
140/VI/6 | 220KV-CHIKKODI-TALANGADE | 29-01-2026 11:23 | 220KV-CHIKKODI-TALANGADE | KPTCL to rectify the DR time synchronization issue at CHIKKODI - 220KV | KPTCL |  | Pending | Pending
140/VI/10 | 220KV-AMBEWADI-PONDA-2 | 05-02-2026 14:09 | 220KV-AMBEWADI-PONDA-2 | KPTCL to rectify the DR time synchronization issue at AMBEWADI - 220KV | KPTCL | Puspha:KPTCL: 05/04/2026 18:48:36: GPS is in working condition. relays are time synchronized. Few msec difference only | Complied | Complied
140/VI/12 | TALGUPPA - 400KV | 07-02-2026 06:28 | TALGUPPA - 400KV | KPTCL to rectify the DR time synchronization issue at TALGUPPA - 400KV | KPTCL | Puspha:KPTCL: 05/04/2026 18:48:36: GPS is in working condition at Talaguppa 400kV SS | Complied | Complied
140/VI/16 | 400KV/220KV GUTTUR-ICT-2 | 13-02-2026 15:09 | 400KV/220KV GUTTUR-ICT-2 | KPTCL advised to rectify the DR time synchronization issue at GUTTUR - 400KV at the earliest | KPTCL | Puspha:KPTCL: 05/04/2026 18:46:25: Attended. GPS time synchronization of relays restored except few old version relays having limitations | Pending | Pending
141/I/2 | Complete outage 220kV GM Navar SS and Tripping of 220kV Bus-2 at 220kV Nandhihal of KPTCL | 28-02-2026 15:03 | 220kV GMNavar is radially connected to 220kV Nandhihal through 220kV GMNavar- Nandhihal-1&2. In the antecedent conditions, 220kV GMNavar- Nandhihal-1&2 was connected to 220kV Bus-2 at Nandhihal. The triggering incident is the Y-ph isolator contact failure in 220kV Nandhihal-Kudgi line-5 which came into vicinity of 220kV Nandhihal-Kudgi line-3 creating a Y-B phase bus fault in 220kV Bus-2 at Nandhihal. This led to the BBP operation and tripping of all the elements connected to 220kV Bus-2 at 220kV Nandhihal and led to the Complete outage 220kV GM Navar SS | KPTCL to review the protection settings at Nandihal SS and submit a report in this regard. | KPTCL | Puspha:KPTCL: 05/05/2026 13:39:14: Corrective measures required are taken up with the developer M/s Siemens Gamesa as the hand over of the substation is under process. Busbar protection setting will be taken up jointly. | Pending | Pending
141/I/3 | Complete outage of 220 kV Aheri, Nimbarga, Vaishali, Shahbad, Kapnoor, Humnabad, Gulbarga, and Santhapur and tripping of 220 kV Bijapur Bus-2, Shahpur Bus-2, Sedam Bus-2, and Bus-1 & Bus-2 at Kalburgi of KPTCL | 03-03-2026 11:00 | In the antecedent conditions, multiple bus splits were carried out in the vicinity of 400/220 kV Kalburgi substation to facilitate evacuation of RE power. The triggering incident was the tripping of 400/220kV ICT-1 and 2 at Kalburgi substation. Since multiple substations evacuate power through Kalburgi, the tripping of the evacuation path led to the complete outage of 220 kV Aheri, Nimbarga, Vaishali, Shahbad, Kapnoor, Humnabad, Gulbarga, and Santhapur and tripping of 220 kV Bijapur Bus-2, Shahpur Bus-2, Sedam Bus-2, and Bus-1 & Bus-2 at Ferozabad (Kalburgi) of KPTCL. | 1.KPTCL to submit the report on LVRT compliance during the event. 2.KPTCL to review ICT over current settings at Kalaburgi SS. 3.KPTCL to install PMU at Kalaburgi SS. | KPTCL | Puspha:KPTCL: 05/05/2026 13:36:59: 1. Letter is adressed to CEE, Operations, Kalaburgi and all concerned regarding preventive measures required to prevent re occurrence of such incident , conformation regarding LVRT will be collected from the field. 2 Presently ICT Over current settings are set at 110% ., For further review of the same SPS is to be implemented at 110 % loading. Operation studies required for the design of SPS is under process. 3. The matter is taken up with management for approval. Technical specifications for PMU will be finalized taking technical support from Powergrid. | Pending | Pending
141/I/4 | Complete Outage of 220kV Nagamangala, Anchepalya and Magadi SS of KPTCL | 05-03-2026 13:48 | 220kV Nagamangala SS, 220kV Anchepalya SS, and 220kV Magadi SS are being radially fed from the 220kV Nelamangala Anchepalya line and the 220kV Nelamangala Magadi line. The triggering incident was a B-G fault in the 220kV Nelamangala Anchepalya line and the line tripped and after which 220kV Nelamangala Magadi line tripped on over current protection. WIth the tripping of 220kV Nelamangala Anchepalya and 220kV Nelamangala Magadi line led to the Complete Outage of 220kV Nagamangala, Anchepalya and Magadi SS of KPTCL | 1.KPTCL to disable Over current logic for 220kV lines at Neelamangala , Anchenpalya SS. 2.KPTCL to verify the Over current relay rest settings at Neelamangala , Anchenpalya SS. | KPTCL | Puspha:KPTCL: 05/05/2026 13:29:49: 1. At Nelamangala, OCR has been disabled for 220kV Anchepalya and Magadi lines. 2. At the time of tripping OCR with setting 800Amp setting was in enabled condition, OCR disabled subsequently. | Complied | Complied
141/II/3 | Tripping of 400kV Bus-2 at RTPS of KPCL | 24-02-2026 04:27 | The triggering incident is the B-G bus fault in 400kV Bus-2 at RTPS. All the main breakers connected to Bus-2 got tripped and led to the tripping of 400kV Bus-2 at RTPS. 400kV RTPS-Munirabad was only in service with the main breaker connected to Bus-2 and due to the tripping of the Bus-2 led to the tripping of 400kV RTPS-Munirabad line. All other elements were in service through 400kV Bus-1. | KPCL to measure IR testing of BPI periodically. | KPCL | EE (E )/CEED:KPCL: 05/05/2026 12:14:38: Conductiong IR tests of BPI will be taken up subject to bus shutdown availibility. | Pending | Pending
141/III/5 | 400KV-DONI-GUTTUR-1 | 01-03-2026 14:50 | The triggering incident is the tripping of the line only at GUTTUR end due to suspected DC earth fault. The line was holding at DONI end. | KPTCL to review the Healthiness of control cables at both 400kV Doni and Guttur SS. | KPTCL | Puspha:KPTCL: 05/05/2026 14:48:58: At the time DC grounding issue was there in the substation. The same was rectified. Healthiness of control cables in Doni bay is verified. No abnormalities found | Complied | Complied
141/VI/4 | 400KV-KAIGA-GUTTUR-2 | 24-02-2026 15:45 | Station at which DR time synchronisation was not observed : GUTTUR - 400KV | KPTCL to rectify the DR time synchronization issue at GUTTUR 400 KV | KPTCL | Puspha:KPTCL: 05/05/2026 14:47:50: GOS time sync issue at Guttur has been resolved. Except few old version relays having limitations, all other relays synchronized with GPS clock. | Complied | Complied
142/I/3 | Complete Outage of 400kV YTPS Generating Station of KPCL, 400kV Kalaburagi SS, 220 kV Aheri, Nimbarga, Vaishali, Shahbad, Kapnoor, Humnabad, Gulbarga, and Santhapur and tripping of 220 kV Bijapur Bus-2, Shahpur Bus-2, Sedam Bus-2 of KPTCL | 17-03-2026 21:52 | 400kV YTPS Generating Station, 400kV Kalaburagi SS, 220 kV Aheri, Nimbarga, Vaishali, Shahbad, Kapnoor, Humnabad, Gulbarga, and Santhapur ,220 kV Bijapur Bus-2, Shahpur Bus-2, Sedam Bus-2 are being radially connected through 400kV BPS YTPS Line-1&2. As per the reports submitted, 400kV BPS YTPS Line-1 tripped on R-G fault at 20:27hrs and 400kV BPS YTPS Line-2 tripped on RY fault at 22:26hrs. Tripping of both lines led to complete outage of all radial connected stations. | KPTCL to formulate SOP to manage the YTPS generation and grid upon tripping of single YTPS-BPS line. Time synch issues to be rectified at various stations and compliance report to be furnished. ER, DL & TAR for many 220 kV stations not furnished. KPTCL to take up with concerned entitites and copy of the same shall be furnished. KPCL to submit feedback to KPTCL (Planning) to ensure reliable evacuation. | KPTCL |  | Pending | Pending
142/II/2 | Tripping of 400kV Bus-1 of 400kV Kalaburagi SS | 18-03-2026 07:51 | As per the reports submitted, while opening the bus reactor 400kV Bus-1 of Kalaburagi got tripped tripping all elements connected to the 400kV Bus-1 | KPTCL to follow SOP during testing and maintanance activities | KPTCL |  | Pending | Pending
142/III/12 | Multiple trippings at BPS | 13-04-2026 15:52 | As per the reports submitted, the triggering incident Y-G fault in BPS-YTPS_1 line. At YTPS end the fault was sensed in Zone 2 and at BPS end the fault was sensed in Zone 1. A/R didn't operate from both the ends. At YTPS end 3 phase tripping was observed and at BPS end upon receiving the DT 3 phase tripping was observed. After tripping of YTPS-BPS-1 line at JSW end of JINDAL-BPS-4 line the fault was sensed in Zone 3 but no master trip was initiated. Line got tripped at Jindal end due to suspected Ground Potential Rise. JINDAL-BPS-4 line was holding from BPS. | KPCL to rectify the PLCC issues at the YTPS. | KPCL |  | Pending | Pending
142/VI/4 | 220KV-RAICHUR_KA-UPPER_JURALA-2 | 18-03-2026 23:11 | DR Time Synchronization issue at RAICHUR_KA - 220KV | KPCL to rectify the DR Time Synchronization issue at RAICHUR_KA - 220KV | KPCL |  | Pending | Pending
142/VI/7 | 220KV-HIRIYUR-ZENATARIS_PSS-1 | 21-03-2026 14:09 | DR Time Synchronization issue at HIRIYUR - 220KV | KPTCL to rectify the DR Time Synchronization issue at HIRIYUR - 220KV | KPTCL |  | Pending | Pending
142/VI/10 | 220KV-AMBEWADI-PONDA-2 | 25-03-2026 21:20 | DR Time Synchronization issue at AMBEWADI - 220KV | KPTCL to rectify the DR Time Synchronization issue at AMBEWADI - 220KV | KPTCL |  | Pending | Pending
142/VI/20 | 400KV-DONI-GUTTUR-1 | 03-04-2026 12:20 | DR Time Synchronization issue at GUTTUR - 400KV | KPTCL to rectify the DR Time Synchronization issue at GUTTUR - 400KV | KPTCL |  | Pending | Pending
142/VI/30 | 400KV-KALABURAGI-YTPS-2 | 10-04-2026 15:25 | DR Time Synchronization issue at KALABURAGI - 400KV | KPTCL to rectify the DR Time Synchronization issue at KALABURAGI - 400KV | KPTCL |  | Pending | Pending
140/III/4 | 220KV-THENI-SABARIGIRI-1 | 23-01-2026 13:40 | As per the reports submitted, the triggering incident was Y-G fault in the line. The Fault distance from Theni end was 26.9 kms and from Sabarigiri end was 86.1 kms. At Theni end, the fault was sensed in Z1, AR operated and tripped due to persistent fault. At Sabarigiri end, the fault was sensed in Z2, carrier aided trip and Y pole opened and AR operated after around 1.2 sec and tripped due to persistent fault (the issue is delayed fault clearance due to Z2 time trip instead of Z2 carrier aided trip), before which carrier was received for AR operation and Z1 sensing at remote ends. | 1. KSEBL to review the TOR operation at Sabarigiri end. 2. KSEBL to review the Dead time at Sabarigiri end. | KSEBL | aeldkseb:KSEB: 04/05/2026 14:57:36: Sir, At Sabarigiri end, both single-phase and three-phase autoreclosure operations have been put in service. At Udumalppet end, only single-phase autoreclosure is in service. The dead time at Sabarigiri end is set as 1 second. It is requested to close this entry. | Complied | Complied
140/VI/18 | 220KV-THENI-SABARIGIRI-1 | 15-02-2026 13:17 | 220KV-THENI-SABARIGIRI-1 | KSEBL to rectify the DR time synchronization issue at SABARIGIRI - 220KV | KSEBL | aeldkseb:KSEB: 04/05/2026 14:54:31: Sir, The DR time synchronization issue at Sabarigiri end was due to a weak GPS signal in the project area, which is located in a dense forest region. The issue has now been rectified.Please remove this item. | Complied | Complied
142/I/14 | Complete Outage of 220kV Pallom SS and 220kV New Pallom SS of KSEB | 14-04-2026 16:40 | As per the reports submitted, the triggering incident was B-G bus fault on 220kV Bus-2 of 220kV New Pallom station within the bus protection zone of 220kV Pallom - New Pallom line. However, 220kV Bus-2 BBP did not operate at 220kV New Pallom SS and the fault was continuously being fed through 220kV lines connected to 220kV Pallom SS and 220kV New Pallom SS. Eventually these 220kV lines tripped on zone-2 protection at the remote ends and this led to complete outage of 220kV Pallom SS and 220kV New Pallom SS | KSEBL to rectify DR Time sync issue at New Pallom, Sabaragiri & Idduki end. | KSEBL |  | Pending | Pending
142/II/3 | Tripping of 220kV Bus-2 at Idduku PH of KSEB | 18-03-2026 15:26 | As per the reports submitted, the triggering incident was B-G fault in 220kV Bus-2 of Idukki PH. Immediately, 220kV Bus-2 BBP operated and all elements connected to the Bus-2 tripped. | KSEBL to report equipment failure to CEA. | KSEBL |  | Pending | Pending
142/VI/35 | 220KV-PALLOM-NEW PALLOM-1 | 14-04-2026 16:40 | DR Time Synchronization issue at NEW PALLOM - 220KV | KSEB to rectify the DR Time Synchronization issue at NEW PALLOM - 220KV | KSEBL |  | Pending | Pending
142/VI/36 | 220KV-PALLOM-NEW PALLOM-1 | 14-04-2026 16:40 | DR Time Synchronization issue at NEW PALLOM - 220KV | KSEB to rectify the DR Time Synchronization issue at NEW PALLOM - 220KV | KSEBL |  | Pending | Pending
142/VI/36 | 220KV-SABARIGIRI-PALLOM-1 | 14-04-2026 16:40 | DR Time Synchronization issue at SABARIGIRI - 220KV | KSEB to rectify the DR Time Synchronization issue at SABARIGIRI - 220KV | KSEBL |  | Pending | Pending
142/VI/38 | 220KV-IDDUKI-NEW PALLOM-1 | 14-04-2026 16:40 | DR Time Synchronization issue at IDDUKI - 220KV | KSEB to rectify the DR Time Synchronization issue at IDDUKI - 220KV | KSEBL |  | Pending | Pending
140/III/2 | 400KV/110KV ALAMATHY-ICT-6 | 23-01-2026 06:45 | As per the reports submitted, the triggering incident is the B-G fault in 110 kV Alamathy - Avadi line. LBB operated due to failure of breaker and tripped all the elements connected to 110 kV Bus-1, where in 400/110kV ICT-6 at Alamathy also tripped. | TANTRANSCO advised to check the healthiness of the all the line breaker at Alamathy SS. | TANTRANSCO | cepc:TANTRANSCO: 30/03/2026 16:34:30: In general, Healthiness of breaker ( measurement of Contact resistance & Breaker timings were checked) is being checked during monthly maintenance. It will be ensured at Alamathy SS | Pending | Pending
140/III/3 | Tripping of main breakers of 400KV-NCTPS_STAGE_II-SUNGAVARACHATRAM-1&2 | 23-01-2026 10:22 | As per the reports submitted incident triggered due to faulty Main-2 D60 relay of 400KV-NCTPS_STAGE_II-SUNGAVARACHATRAM-1 even though DC supply was available, F8L card missing message observed in Main-2 relay leading to tie LBB operation and tripping of both the main breakers connected to Bus-1 and 2. However the tie breaker was in service during the event. | 1.TANTRANSCO to review the Tie Breaker LBB operation and tripping of Main breakers at Sungavarachatram SS during the incident. 2.TANTRANSCO to rectify the DR time sync issue at Sungavarachatram end | TANTRANSCO | cepc:TANTRANSCO: 30/03/2026 16:34:30: Main.2 D60 relay F8L module checked & found healthy & put into service and observed that No Spurious tripping noticed so far | Pending | Pending
140/III/13 | Multiple Trippings at 230kV Kadaperi SS of TANTRANSCO | 12-02-2026 02:39 | As per the reports submitted, the triggering incident was R-G cable fault in 230kV Kadaperi Alandur_CMRL Line-1. At Alandur end, the fault was sensed in zone-1 and the line tripped. At Kadaperi end, the fault was not sensed in any of distance protections till 800 ms though fault voltage dipped to 76 kV with 16.5 kA fault current. Meanwhile during this period, the same fault was sensed in Z3 in the remote ends of other 230kV lines connected to 230kV Kalivvendapattu Bus like 230kV Kadaperi SR Purur Line-1&2, 230kV Kadaperi Pudur and 230kV Kadaperi Kalivvendapattu line and tripped on zone-3. In 230kV Kadaperi Kalivvendapattu line at Kalivvendapattu end, DEF protection also operated and DT was sent to Kadaperi end. However the 230kV Kadaperi Kalivvendapattu line was holding from Kadaperi end as per TANTRANSCO's report. After around 800ms, the fault was sensed in zone-1 at 230kV Kadaperi end of 230kV Kadaperi Alandur_CMRL Line-1 when the voltage dipped to around 2.7 kV and the line tripped immediately. Though all 230 kV lines tripped, 230 kV Kadaperi Bus-1 and 230 kV Alandur Buses were charged from 110 kV side. At both Kadaperi end and Alandur end in 230kV Kadaperi Alandur_CMRL Line-1 carrier was not to sent to remote ends. | 1.TANTRANSCO to check the healthiness of Western Bus PT. 2.TANTRANSCO to implement differential protection in 230 kV KadaperiAlandur CMRL Line1 3.TANTRANSCO to review the distance protection settings in 230 kV Kadaperi Alandur CMRL Line1. | TANTRANSCO | cepc:TANTRANSCO: 30/03/2026 16:34:30: 1.to be checked 2. Line Differential procurement under progress | Pending | Pending
140/III/16 | 400KV/230KV MANALI-ICT-4 | 14-02-2026 11:16 | As per the reports submitted, the OLTC PRV trip was initiated due to moisture ingress and a trip contact defect noticed in the R-phase OLTC, after which the 86-relay operated. | TANTRANSCO to check the healthiness of the all other 400KV/230KV ICT OLTC contacts at MANALI. | TANTRANSCO | cepc:TANTRANSCO: 30/03/2026 16:34:30: will be ensured | Pending | Pending
141/II/2 | Tripping of 230kV Bus-2 of 230kV Kayathar SS of TANTRANSCO | 22-02-2026 12:48 | 230kV Kayathar SS is operating with double bus with bus coupler at 230kV level but all elements were connected to 230kV Bus-2. As per the reports submitted, the triggering incident was 230kV YB fault in 230kV Bus-2. Hence 230kV BBP operated and all elements connected in Bus-2 got tripped. 110kV side was in service during the event. | 1.TANTRANSCO to do periodic thermo vision scanning of Kayathar SS Switchyard. 2.TANTRANSCO to implement double bus operation at Kayathar SS. | TANTRANSCO | cepc:TANTRANSCO: 04/05/2026 16:45:23: 1.Informed to System operation wing. 2. cepc:TANTRANSCO: 04/05/2026 17:14:00: 2.Protection clearance issued for implementation of double bus operation. | Pending | Pending
141/III/4 | 400KV-MANALI-PULIYANTHOPE-2 | 28-02-2026 06:15 | As per the reports submitted, the triggering incident is the B-G fault in the line. At Pulianthope end, the fault was sensed in Line Differential Protection, AR operated and tripped due to persistent fault. At Manali end, the fault was sensed in LDP and B pole openend. After around 1 sec AR operated at remote end intertrip and 3 ph tripped, but even after which AR operated after around 200ms and tripped due to persistent fault. | 1.TANTRANSCO to review the AR attempt after inter trip at Manali end. 2.TANTRANSCO to rectify the DR time synchronization issue at PULIYANTHOPE SS 3.TANTRANSCO to review the Non-availability of SCADA SOE at PULIYANTHOPE | TANTRANSCO | cepc:TANTRANSCO: 04/05/2026 16:35:01: 1. As per scheme, TC1 & TC2 couldn't get trip pulse from 86 lockout relay since 52a contact already open. Hence this happened 2.Pulianthope SCADA SOE checked & Now reported | Pending | Pending
141/IV/1 | 400KV-NCTPS_STAGE_II-SUNGAVARACHATRAM-1 | 22-02-2026 05:58 | As per the reports submitted, the triggering incident is the B-G fault due to insulator flashover at location 101 from NCTPS ST2 and OPGW cut during the event. At both ends the fault was sensed in Z1 and AR did not operate due to carrier fail. | 1.TNPGCL to review the Non availability of SCADA SOE at NCTPS ST2.2. TNPGCL to review Non operation of AR at NCTPS ST2. | TNPGCL |  | Pending | Pending
141/IV/3 | 220KV-SULURPET-GUMMIDIPOONDI-1 | 27-02-2026 11:39 | As per the reports submitted, the triggering incident is the Y-G fault due to tree clearance issue in the vicinity of the line. At Sullurpet end, the fault was sensed in Z1, AR is disabled and 3ph tripped. At Gummidipundi end, the fault was sensed in Z1, and AR did not operate and 3ph tripped. | 1TANTRANSCO to enable the Auto Reclosure at Sullurpet. 2.TANTRANSCO to review the relay coordination at Gummidipoondi SS, as the phase to ground fault was sensed as phase to phase fault. | TANTRANSCO | cepc:TANTRANSCO: 04/05/2026 16:26:36: AR scheme is healthy in sulurpet feeder. From the DR, It is observed that for a single line to fault in Y phase but R phase current magnitude also around 0.8kA and phase angle is matched with Y & N hence relay may be sensed the fault as line to line fault & issued the three phase trip. On 01.03.2026 at 13:43hrs for a single line to ground fault in B phase AR found successful. | Complied | Complied
141/IV/4 | 765KV-THIRUVALAM-ARIYALUR-1 | 27-02-2026 18:20 | As per the reports submitted, the triggering incident is the Y-G fault in the line. At ARIYALUR, the fault was sensed in Z1, AR operated and was successful and the line was holding. At THIRUVALAM end, the fault was sensed in Z1, AR did not operate in both main and tie and 3ph tripped. | TANTRANSCO to review the Auto Reclosure operation in 765KV-THIRUVALAM-ARIYALUR-1 line at Thiruvalam end. | TANTRANSCO | cepc:TANTRANSCO: 04/05/2026 16:26:36: PGCIL maintain the bay | Pending | Pending
141/VI/3 | 400KV-NCTPS_STAGE_II-MANALI-1 | 24-02-2026 05:01 | Station at which DR time synchronisation was not observed NCTPS_STAGE_II - 400KV | TNPGCL to rectify the DR time synchronization issue at 400kV NCTPS Stage2 | TNPGCL |  | Pending | Pending
141/VI/8 | 400KV-SRIPERUMBADUR-CHITTOOR-1 | 01-03-2026 11:24 | Station at which DR time synchronisation was not observed SRIPERUMBADUR - 400KV | TANTRANSCO to rectify the DR time synchronization issue at SRIPERUMBADUR - 400KV | TANTRANSCO | cepc:TANTRANSCO: 04/05/2026 16:26:36: GPS is available. Time sync will be checked | Pending | Pending
142/I/11 | Complete Outage of 230 kV Arani and Echur of TANTRANSCO | 05-04-2026 23:39 | The triggering incident is the 110kV Y-ph bus PT failure at Arani (as per FIR) causing 110 kV Bus Fault. Without 110kV BBP, the Bus fault was sensed and the lines tripped on Z3 protection operation at remote ends other than 230KV-ARNI-ECHUR-1. 230KV-MAPS-ECHUR-1 line tripped on DEF protection leading to the Complete Outage of 230 kV Arani and Echur of TANTRANSCO | TANTRANSCO to review the remote end Zone3 settings of lines connecting to 230kV Arani SS. TANTRANSCO & NPCIL MAPS to review the distance and DEF coordination and submit report to SRPC & SRLDC. TANTRANSCO to implement 110kV BUSBAR protection at 230kV Arani SS. | TANTRANSCO |  | Pending | Pending
142/II/1 | Tripping of 230kV TTPS Bus-2 of TNPGCL | 17-03-2026 15:15 | The triggering incident is the Y-G fault in TTPS-Kayathar, where in breaker failed to trip and LBB operated leading to tripping of Bus-2 at TTPS. | TNPGCL to furnish detailed report regarding non sending of DT to KKNPP end during LBB operation. | TNPGCL |  | Pending | Pending
142/VI/5 | 400KV-ALAMATHY-SUNGAVARACHATRAM-1 | 19-03-2026 02:35 | DR Time Synchronization issue at SUNGAVARACHATRAM - 400KV | TANTRANSCO to rectify the DR Time Synchronization issue at SUNGAVARACHATRAM - 400KV | TANTRANSCO |  | Pending | Pending
142/VI/6 | 400KV-ALAMATHY-SUNGAVARACHATRAM-1 | 19-03-2026 02:35 | DR Time Synchronization issue at ALAMATHY - 400KV | TANTRANSCO to rectify the DR Time Synchronization issue at ALAMATHY - 400KV | TANTRANSCO |  | Pending | Pending
142/VI/12 | KARAIKUDI(TN) - 230KV | 26-03-2026 17:57 | DR Time Synchronization issue at KARAIKUDI(TN) - 230KV | TANTRANSCO to rectify the DR Time Synchronization issue at KARAIKUDI(TN) - 230KV | TANTRANSCO |  | Pending | Pending
142/VI/26 | 230KV-ARNI-SINGARPET | 05-04-2026 23:39 | DR Time Synchronization issue at SINGARPET - 230KV | TANTRANSCO to rectify the DR Time Synchronization issue at SINGARPET - 230KV | TANTRANSCO |  | Pending | Pending
142/VI/41 | 400KV/230KV SRIPERUMBADUR_TN-ICT-3 | 15-04-2026 13:38 | DR Time Synchronization issue at SRIPERUMBADUR_TN - 400KV | TANTRANSCO to rectify the DR Time Synchronization issue at SRIPERUMBADUR_TN - 400KV | TANTRANSCO |  | Pending | Pending
142/VI/44 | 400KV/230KV PULIYANTHOPE-ICT-1 | 19-04-2026 05:32 | e DR Time Synchronization issue at PULIYANTHOPE - 400KV | TANTRANSCO to rectify the DR Time Synchronization issue at PULIYANTHOPE - 400KV | TANTRANSCO |  | Pending | Pending
140/III/17 | 230KV-NEYVELI_TS_II-VILLIANUR-1 | 14-02-2026 15:49 | 230 KV-NEYVELI_TS_II-VILLIANUR-1 was idle charged from Villianur end. As per the reports submitted, the triggering incident was B-G fault in the line at a distance of 1.7 km from Villianur end. At Villianur end, the fault was sensed in zone-1. A/R operated and the line tripped on persistent fault. However, another A/R attempt was observed during dead time and the same needs review. | PED is advised to review the A/R operation in 230KV Neyveli Villianur Line. | PED | ARUMUGAM:PED: 30/03/2026 16:41:59: During the special relay testing conducted on 05.03.2026, it is observed that A/R close command timing and A/R dead time are set with 1second and and 900milliseconds respectively. It is proposed to revise the above said timing to 100-150milliseconds and 1seconds respectively. As the above said time correction is requiring database updation, it is proposed to implement A/R scheme in Main-I & Main-II Distance Protection relays after discarding the same from BCU. Will be implemented on or before 30.04.2026. ARUMUGAM:PED: 04/05/2026 14:18:38: During the special relay testing conducted on 05.03.2026, it is observed that A/R close command timing and A/R dead time are set with 1second and and 900milliseconds respectively. It is proposed to revise the above said timing to 100-150milliseconds and 1seconds respectively. As the above said time correction is requiring database updation, it is proposed to implement A/R scheme in Main-I & Main-II Distance Protection relays after discarding the same from BCU. Will be implemented on or before 30.06.2026. | Pending | Pending
140/III/5 | 400KV-KURNOOL_PG-NARNOOR-1 | 25-01-2026 18:27 | As per the reports submitted, the triggering incident occurred during 400kV Bus-1 bus bar testing during the shutdown, where in Kurnool main breaker (410) was unavailable. During the bus bar testing activity, BBP operation was high (as per DR) and after around 200ms 41152 tie breaker also got tripped on LBB operation. Due to the tripping of both main and tie breaker led to the tripping of 400kV Kurnool-Nannoor-1 line and DT was sent to remote end. At Narnoor end, the Breaker tripped on DT receive. | PGCIL SR-I advised to follow the SOP during the Bus bar testing. | PGCIL (SR-I) | Venkatasai:PGCIL (SR-I): 01/05/2026 18:14:02: Safety precautions and auto switch OFF of test kit for 100mSec implemented. Advised for all substations under SRTS-I | Complied | Complied
141/VI/11 | 400KV-KOLAR_AC-SRIPERUMBADUR-1 | 03-03-2026 14:09 | Station at which DR time synchronisation was not observed KOLAR_AC - 400KV | PGCIL SR-II to rectify the DR time synchronization issue at KOLAR AC - 400KV | PGCIL (SR-II) |  | Pending | Pending
142/III/9 | 400KV-DICHPALLY-NIZAMABAD-1 | 04-04-2026 22:31 | During the fault at Nirmal substation due to inclement weather, 400 kV-DICHPALLY-NIZAMABAD-1 line tripped only at NIZAMABAD end. | PGCIL SRI was advised to implement line differential protection with both built-in backup distance protection in main-I and mainII relays in 400KVDICHPALLYNIZAMABAD1. PCSC forum advised PGCIL SRI to comply with the grid code and avoid intentional delay of 100msec for zone1 distance protection. PGCIL SRI to provide the detailed report on the incident. | PGCIL (SR-I) |  | Pending | Pending
140/I/1 | Complete Outage of 220kV Kadra, Kodasalli and Karwar of KPTCL | 21-01-2026 09:23 | 220kV Kaiga Bus-1 and Bus-2 was planned to be under shutdown from 1000 hrs to 1600 hrs where in both the 220 kV Kaiga- Kadra and 220 kV Kaiga - Kodasalli had to be opened. In the antecedent condition 220kV Naghjeri-Kodasalli-1&2 were in idle charged condition. After the receipt of code for planned activity, the lines (220 kV Kaiga- Kadra and 220 kV Kaiga - Kodasalli) were opened (not in coordination) leading to the Complete Outage of 220kV Kadra, Kodasalli and Karwar of KPTCL | Kaiga GS to obtain codes from SRLDC and KAR SLDC while taking outages. | NPCIL Kaiga |  | Pending | Pending
140/I/1 | Complete Outage of 220kV Kadra, Kodasalli and Karwar of KPTCL | 21-01-2026 09:23 | 220kV Kaiga Bus-1 and Bus-2 was planned to be under shutdown from 1000 hrs to 1600 hrs where in both the 220 kV Kaiga- Kadra and 220 kV Kaiga - Kodasalli had to be opened. In the antecedent condition 220kV Naghjeri-Kodasalli-1&2 were in idle charged condition. After the receipt of code for planned activity, the lines (220 kV Kaiga- Kadra and 220 kV Kaiga - Kodasalli) were opened (not in coordination) leading to the Complete Outage of 220kV Kadra, Kodasalli and Karwar of KPTCL | SRLDC to bifurcate the Grid occurances into Protectional and operational issues, while furnishing the agenda. | SRLDC | ArthiV~1776856274:SRLDC: 04/04/2026 17:45:08: The Grid Disturbances classification is being done based on Grid standards. Any protection or operational issues are being mentioned in the points for review. | Pending | Pending
140/I/2 | Complete Outage of 230kV M/s Spring Pugalur Pugalur Wind station | 23-01-2026 00:35 | As per the reports submitted, at M/s Spring Pugalur Pugalur Wind Station, SVG lost communication at 00:29hrs causing SVG-1,2 &3 to inject reactive power causing voltage to shoot up to around 1.1PU. Immediately, Over voltage protection that was supposed to trigger only the DR has extended trip signal from Main-2(ABB REL 670 ) relay and the line tripped at M/s Spring Pugalur Pugalur end. DT was sent to Pugalur end and the line tripped at both ends. Tripping of only connected line led to loss of power supply to 230kV M/s Spring Pugalur Pugalur Wind station. | 1. M/s SPRNG Pugalur to rectify the MPPC logic in coordination with OEM. 2. M/s SPRNG Pugalur to disable the Over Voltage / Under voltage and Under frequency tripping of lines. | M/s SPRNG Pugalur |  | Pending | Pending
140/I/7 | Complete Outage of 220kV Vizag Steel SS of APTRANSCO | 06-02-2026 11:31 | 220kV Vizag Steel SS is connected to Vizag Switching Station through 220kV Vizag Steel-Vizag Switching Station-1&2 only. As per the reports submitted, the triggering incident was R-G fault in 220kV Bus of 220kV Vizag Steel SS. Immedeately, 220kV BBP operated and all elements connected to 220kV Bus tripped. However, the lines were holding from the remote ends. This led to complete outage of 220kV Vizag Steel SS. | 1. RINL VSP to submit complete DR files of the event to SRPC & SRLDC. 2. RINL VSP to periodically check and ensure proper CT connections in the switchyard. 3. RINL VSP to expedite the retroffiting of static relays with Numerical relays in the switchyard. 4. RINL VSP to rectify the DR time sync issue 5. RINL VSP to ensure double bus operation | M/s RINL VSP | dee2sp:APTRANSCO: 07/04/2026 14:53:22: PCSC/SRPC recommendations were communicated to M/s. RINL by OMC circle/Vizag and requested for pointwise compliance report from M/s. RINL. dee2sp:APTRANSCO: 09/04/2026 11:48:48: Remarks received from M/s RINL in response to the PCSC -140 recommendations is forwarded to SRPC by email on 09-04-2026 at 11:52 AM. | Pending | Pending
140/II/3 | Tripping of 400kV Bus-1 at Simhadri TPS of NTPC | 31-01-2026 18:04 | The triggering incident is the testing activity of CT after replacement of CT in 412 Bay at Simhadri TPS. Due to human error of testing activities, inadvertently current injection in the secondary side led to the operation BBP operation due to the imbalance and tripping of 400kV Bus-1 at Simhadri TPS. During the same time due to outage of tie breaker led to the tripping of Unit-1 at Simhadri leading to a generation loss of 450MW | NTPC Simhadri to strictly enforce SOP for CT secondary handling during testing activities. | NTPC Simhadri |  | Pending | Pending
140/III/7 | 400KV-NEYVELI_TS2_EXP-PUGALUR-1 | 28-01-2026 06:26 | As per the reports submitted, the triggering incident was B-G fault in the line. The fault distance from Neyveli end was 130.2 kms and from Pugalur end was 130 kms. At Neyveli end, both Main-1 and 2 relays sensed in Z1 fault. But in Main-2 relay CB R-ph pole was already sensed as open status. When B-ph pole was opened due to transient fault (Z1), the M2 relay sensed it as both pole (R & B) open. So M2 relay issued A/R block & A/R Lock out due to which 3-ph lock out operated and DT was sent to remote end. At Pugalur end, B phase single pole tripped but before operation of AR DT received from remote end causing 3 pole trip. | 1. NLC TS-2 EXP is advised to provide detailed report on the incident. 2. NLC TS-2 EXP to rectify the DR Time synch | NLC TS-2 EXP |  | Pending | Pending
140/VI/4 | 400KV-NEYVELI_TS2_EXP-PUGALUR-1 | 28-01-2026 06:26 | 400KV-NEYVELI_TS2_EXP-PUGALUR-1 | NEYVELI_TS2_EXP to rectify the DR time synchronization issue at NEYVELI_TS2_EXP - 400KV | NEYVELI_TS2_EXP |  | Pending | Pending
140/VI/7 | SIMHADRI - 400KV | 30-01-2026 11:08 | SIMHADRI - 400KV | NTPC SIMHADRI to rectify the DR time synchronization issue at SIMHADRI - 400KV | NTPC SIMHADRI |  | Pending | Pending
141/I/5 | Complete Outage 220kV Renew_Surya_Koppal of RENEW | 08-03-2026 05:49 | 220kV Renew_Surya_Koppal is connected radially to KOPPAL through 220KV-KOPPAL-Renew_Surya_Koppal-1. The triggering incident is the B-G fault in the 220KV-KOPPAL-Renew_Surya_Koppal-1 line and tripping of the only line connected to 220kV Renew_Surya_Koppal led to the Complete Outage 220kV Renew_Surya_Koppal of RENEW | 1.M/s Renew to submit detailed report for the event. 2.M/s Renew to Enable Auto reclosure for 220kV Koppal Renew Surya line. | M/s Renew |  | Pending | Pending
141/I/6 | Complete outage of 220kV SPRING_PUGALUR of SPRING | 11-03-2026 14:17 | 220kV SPRING_PUGALUR is connected radially to PUGALUR through 230KV-PUGALUR-SPRING_PUGALUR-1. The triggering incident is the B-G fault in the 230KV-PUGALUR-SPRING_PUGALUR-1 line and tripping of the only line connected to 220kV SPRING_PUGALUR led to the Complete outage of 220kV SPRING_PUGALUR of SPRING | Spring Pugalur to submit detailed report regarding non operation of AR in consulattion with OEM. | M/s Spring Pugalur |  | Pending | Pending
141/I/7 | Complete Outage of 220kV TP SAURYA of TATA POWER | 13-03-2026 15:07 | 220kV TP SAURYA is connected radially to KOPPAL through 220KV-TP SAURYA LIMITED-KOPPAL-1. The triggering incident is the B-G fault in the 220KV-TP SAURYA LIMITED-KOPPAL-1 line and tripping of the only line connected to 220kV TP SAURYA led to the Complete Outage of 220kV TP SAURYA of TATA POWER | 1.TATAPOWER to verify healthiness of the jumpers at all tower locations. 2.TATAPOWER to install pilot insulators for angle towers. 3.TATAPOWER to enable AR in coordination with Indigrid. 4.TATAPOWER to follow the IEGC mentioned timeline for furnish FIR, EL & DR to SRLDC | M/s TATAPOWER |  | Pending | Pending
141/III/8 | 220KV/33KV KSPPL-ICT-2 | 08-03-2026 10:24 | As per the reports submitted, the triggering incident is the 33kV downstream fault, during which 220KV/33KV KSPPL-ICT-2 tripped on Earth Fault Protection. | KLEIO Solar IS advised to conduct a detailed inspection of all isolator clamps and associated conductors in the switchyard to identify any loose connections, mechanical wear or deterioration. Necessary corrective actions shall be undertaken. | M/s KLEIO Solar |  | Pending | Pending
141/VI/12 | 400KV/230KV NTPL-ICT-1 | 04-03-2026 16:38 | Station at which DR time synchronisation was not observed NTPL - 400KV | NTPL to rectify the DR time synchronization issue at NTPL - 400KV | NTPL |  | Pending | Pending
141/VI/13 | 400KV-KAIGA-GUTTUR-2 | 13-03-2026 05:27 | Station at which DR time synchronisation was not observed KAIGA - 400KV | NPCIL KAIGA to rectify the DR time synchronization issue at KAIGA - 400KV | NPCIL KAIGA |  | Pending | Pending
142/I/1 | Complete Outage of 220kV Zenataris | 16-03-2026 14:40 | As per the reports submitted, the triggering incident was DC supply failure at 220kV Zenataris leading to the tripping of 220kV Hiriyur Zenataris line. Tripping of the only connected line led to complete outage of 220kV Zenataris. | M/s Zenatrius to disable CTD for lines. M/s Zentarius to strictly adhere to SOP during testing activites. | M/s Zenatrius |  | Pending | Pending
142/I/5 | Complete Outage of 220kV ZENATARIS_PSS | 21-03-2026 14:09 | 220 kV Zenataris_PSS is connected to Hiriyur through 220KV-HIRIYUR-ZENATARIS_PSS-1. As per the reports submitted, the triggering incident was YB fault in 220KV-HIRIYUR-ZENATARIS_PSS-1 and the line tripped. Tripping of the only connected line led to complete outage of ZENATARIS_PSS - 220KV | M/s Zentaris to submit the detailed report of the event, mentioning the reason for non sening of not detecting the fault at the generator end during the event. | M/s Zentaris |  | Pending | Pending
142/I/6 | Complete Outage of 220kV Serentica_RI3PL_Gadag_Solar and 220kV Serentica_RI3PL_Gadag_wind | 23-03-2026 21:58 | As per the reports submitted, the triggering incident was R-G fault in 220 kV-GADAG_PSS-Serentica_RI3PL_Gadag_Solar-1 and the line tripped. Tripping of the only connected line led to complete outage of 220kV Serentica_RI3PL_Gadag_Solar and 220kV Serentica_RI3PL_Gadag_wind | 1. M/s Serentica to furnish EL, DR & TAR. 2. M/s Serentica to submit the detailed report on the incident. | M/s Serentica |  | Pending | Pending
142/I/8 | Complete Outage of 220kV SAEL2 | 29-03-2026 15:52 | The triggering incident was R-G fault in 220 kV-KURNOOL_PG_III-SAEL2-1 and the line tripped. Tripping of the only connected line led to complete outage of 220 kV SAEL2 | SAEL to rectify the DR time sync issues. SAEL to submit the detailed report for DT sending during the event in consultation with OEM. | SAEL |  | Pending | Pending
142/I/9 | Complete Outage of 220kV Renew_Surya_Koppal of RENEW | 30-03-2026 14:11 | As per the reports submitted, the triggering incident was tripping of 220kV Koppal-RSRPL line while charging 220/33kV ICT-2 at 220kV Renew_Surya_Koppal and DT was sent to Koppal end and the line tripped. Tripping of the only connected line led to complete outage of 220kV Renew_Surya_Koppal. | M/S Renew to consult the OEM and submit detailed report regarding sending of DT and tripping of line during the event. | M/S Renew |  | Pending | Pending
142/I/15 | Complete outage of 400kV JSW_Rajapura and JSW_Gowripura of JSW | 16-04-2026 15:18 | 400kV JSW_Rajapura and JSW_Gowripura of JSW is radially connected to Jindal TPS through 400kV Jindal TPS- JSW_Rajapura. The triggering incident is the R-G fault in the multicircuit tower portion in 400kV Jindal-BPS-4 and 400kV JIndal TPS- JSW_Rajapaura and the lines tripped. Due to the tripping of the only connected line to 400kV JSW_Rajapura and JSW_Gowripura led to the complete outage of 400kV JSW_Rajapura and JSW_Gowripura. During the same time 400kV Jindal-BPS-3 tripped due to suspected ground potential rise. | JSW-RE to funish the DR/ EL regarding the event to SRPC & SRLDC. JSWEL to submit the GPR investigation report from M/s Manav. | JSW-RE |  | Pending | Pending
142/IV/5 | 220KVNPKUNTA PSS3 NPKUNTA1 | 13-04-2026 14:02 | As per the reports submitted, the fault triggering incident was BG fault in the line. At NPKUNTA end the fault was sensed in differential protection, AR operated but due to persistent fault 3 phase tripping was observed. At NPKUNTA PSS3 end fault was sensed in differential protection, AR didn't operate and 3 phase tripped for the first fault itself. | APSPCL to review the AR operation at NP Kunta PSS3 end. | APSPCL |  | Pending | Pending
142/VI/1 | TP SAURYA LIMITED - 220KV | 17-03-2026 19:35 | DR Time Synchronization issue at TP SAURYA LIMITED - 220KV | TP SAURYA LIMITED to rectify the DR Time Synchronization issue at TP SAURYA LIMITED - 220KV | M/s TP SAURYA LIMITED |  | Pending | Pending
142/VI/17 | 220KV-KURNOOL_PG_III-SAEL2-1 | 29-03-2026 15:55 | DR Time Synchronization issue at SAEL2 - 220KV | SAEL to rectify the DR Time Synchronization issue at SAEL2 - 220KV | SAEL |  | Pending | Pending
142/VI/49 | 400KV-KAIGA-GUTTUR-2 | 20-04-2026 20:25 | DR Time Synchronization issue at KAIGA - 400KV | NPCIL KAIGA to rectify the DR Time Synchronization issue at KAIGA - 400KV | NPCIL KAIGA |  | Pending | Pending