## Summary
सुरक्षा प्रदर्शन सूचकांक/ Protection Performance Indices |  |  |  |  | 01-03-2026 | to | 31-03-2026
उपयोगिता का नाम/Name of the Utility | सुरक्षा अभियान के अनुसार ट्रिपिंग क्रम में/Trippings in order as per protection operation (Nc) | अनुचित परिचालनों की संख्या/No.of Unwarranted Operations (Nu) | विफल परिचालनों की संख्या/No.of failed operations (Nf) | (Ni=Nu+Nf) | सुरक्षा सूचकांक/Security Index [S=Nc/ (Nc+NU)] | निर्भरता सूचकांक/Dependability Index [D=Nc/ (Nc+Nf)] | विश्वसनीयता सूचकांक/Reliability Index [R=Nc/ (Nc+Ni)]
APGENCO | 36 | 1 | 0 | 1 | 0.97297 | 1 | 0.97297
APTRANSCO | 195 | 1 | 5 | 6 | 0.9949 | 0.975 | 0.97015
JSW_THERMAL | 0 | 2 | 0 | 2 | 0 | NA | 0
KPCL | 17 | 0 | 0 | 0 | 1 | 1 | 1
NPCIL_KAIGA | 1 | 0 | 0 | 0 | 1 | 1 | 1
NPCIL_KKNP | 3 | 0 | 0 | 0 | 1 | 1 | 1
NPCIL_MAPS | 4 | 0 | 0 | 0 | 1 | 1 | 1
NTECL | 2 | 0 | 0 | 0 | 1 | 1 | 1
NTPC_KUDGI | 4 | 0 | 0 | 0 | 1 | 1 | 1
NTPL | 1 | 0 | 0 | 0 | 1 | 1 | 1
PGCIL SR-1 | 21 | 0 | 0 | 0 | 1 | 1 | 1
PGCIL SR-2 | 43 | 0 | 2 | 2 | 1 | 0.95556 | 0.95556
SEIL | 0 | 0 | 1 | 1 | NA | 0 | 0
Spring_Pugalur | 1 | 0 | 0 | 0 | 1 | 1 | 1
TANTRANSCO | 246 | 1 | 13 | 14 | 0.99595 | 0.94981 | 0.94615
TATA | 3 | 0 | 0 | 0 | 1 | 1 | 1
TGGENCO | 10 | 1 | 0 | 1 | 0.90909 | 1 | 0.90909
TGTRANSCO | 83 | 2 | 2 | 4 | 0.97647 | 0.97647 | 0.95402
ADANI_APL | NA | NA | NA | NA | NA | NA | NA
AMGEPL | NA | NA | NA | NA | NA | NA | NA
Ayana Renewable Power Six Pvt Ltd | NA | NA | NA | NA | NA | NA | NA
BETAMWIND | NA | NA | NA | NA | NA | NA | NA
GREENINFRA | NA | NA | NA | NA | NA | NA | NA
GREENKO | NA | NA | NA | NA | NA | NA | NA
IL&FS | NA | NA | NA | NA | NA | NA | NA
JSW_RE | NA | NA | NA | NA | NA | NA | NA
MEPL | NA | NA | NA | NA | NA | NA | NA
NTPC_SIMHADRI | NA | NA | NA | NA | NA | NA | NA
PONDICHERRY | NA | NA | NA | NA | NA | NA | NA
PVG_IRCON_S | NA | NA | NA | NA | NA | NA | NA
Vena_GadagPS | NA | NA | NA | NA | NA | NA | NA
ADANI_ATL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
APSPCL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
BHAVINI | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
GRT | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
GTL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
HINDUJA | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
HIRIYUR_ZREPL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
ILFS | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
INDIGRID | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
KLEIO_SOLAR | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
KPTCL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
KSEB | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
KSPDCL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
LKPPL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
MYTRAH | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
NLC | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
NTPC | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
NTPC_RSTPS | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
NTPC_TESTPP | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
ORANGE | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
OSTRO_KANNADA | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
RENEW POWER PVT LTD | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
SAEL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
SCCL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
SEPC | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
SEPL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
SERENTICA_RI1PL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
TNGECL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
TNPGCL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified

## All
क्र. स. /S.NO. | एलमन्ट नाम/ ELEMENT NAME | एलमन्ट प्रकार/ELEMENT TYPE | वोल्टेज स्तर/Voltage Level | इंट्रा/इंटर स्टेट एलमन्ट/Intra/Inter state element | एलीमेंट का मालिक/Owner of the element | ट्रिपिंग की तारीख/ TRIPPING DATE | ट्रिपिंग का समय/ TRIPPING TIME | भेजनेवाला/Sending End |  |  |  |  | प्राप्त करनेवाला/Receiving End |  |  |  |  | ट्रिपिंग का कारण /REASON for Tripping
[8 empty] | मालिक/OWNER | वर्गीकरण/Classification | वर्गीकरण टिप्पणी/Classification Comment | कार्य योजना/Action Plan | कार्य योजना की स्थिति/Action Plan Status | मालिक/OWNER | वर्गीकरण/Classification | वर्गीकरण टिप्पणी/Classification Comment | कार्य योजना/Action Plan | कार्य योजना की स्थिति/Action Plan Status
1 | 400KV-DONI-GUTTUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 01-03-2026 | 14:50 | KPTCL | Correct Operation | Nil |  |  | KPTCL | Unwanted Operation | Breakers Not tripped at 400kV Doni. | Healthiness of control cables to be checked by availing line shutdowm | Pending | due to momentary DC ground
2 | 765KV-ARIYALUR-NCPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Intra | TANTRANSCO | 01-03-2026 | 03:59 | TANTRANSCO | Correct Operation | ZONE.1,Y,N Main CB AR successful & Lockout trip initiated due to subsequent fault within reclaim time_At loc.67,Y ph insulator decap at loc.3 &67 |  |  | TANTRANSCO | Correct Operation | ZONE.1Y,N,TOR_At loc.67,Y ph insulator decap at loc.3 &67 |  |  | TRIPPED ON Y-N FAULT
3 | 400KV-SRIPERUMBADUR-CHITTOOR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 01-03-2026 | 11:24 | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | APTRANSCO | Correct Operation | AR operated properly. But feeder tripped due to fault recurring. |  |  | Tripped on B-Phase to ground fault
4 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | TGTRANSCO | 01-03-2026 | 12:10 | APGENCO | Correct Operation | correct operation |  |  | TGGENCO | Correct Operation | Carrier Aided Protection Operated |  |  | TRIPPED ON Y PHASE FAULT
5 | 400KV-KALPAKKA-ASUPAKA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | APTRANSCO | 03-03-2026 | 11:57 | APTRANSCO | Correct Operation | fault tripping |  |  | TGTRANSCO | Correct Operation | Line to ground fault |  |  | Tripped on BN fault
6 | 400KV-SRISAILAM_LEFT_BANK-SATTENPALLY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | TGTRANSCO | 03-03-2026 | 08:54 | TGGENCO | Correct Operation | The relay tripped as per the settings. |  |  | APTRANSCO | Correct Operation | single line to ground fault |  |  | TRIPPED ON B-N FAULT
7 | 400KV-SRISAILAM_LEFT_BANK-SATTENPALLY-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | TGTRANSCO | 03-03-2026 | 09:02 | TGGENCO | Correct Operation | The relay tripped as per the settings. |  |  | APTRANSCO | Correct Operation | single line to ground fault |  |  | TRIPPED ON R-N FAULT
8 | 400KV/220KV KALABURAGI-ICT-1 | TRANSFORMER | 400 | Intra | KPTCL | 03-03-2026 | 11:03 | KPTCL | Correct Operation | Tripped on overflux relay, due to sudden overloading | [7 empty] | UNDER VOLTAGE
9 | 132KV-NARNOOR-ALAMPUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | ANDHRA PRADESH | 02-03-2026 | 15:01 | APTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation | Tripped on B-n,Z1,8.557km,2.41kA and line is open at Kurnoo;. |  |  | TRIPPED ON B-N FAULT
10 | 230KV-PUGALUR-KURUKATHI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 03-03-2026 | 11:50 | PGCIL SR-2 | Correct Operation | AR attempted but Line tripped on Yph-G Fault. |  |  | TANTRANSCO | Correct Operation | CAT,Y,N,AR SUCCESSFUL |  |  | TRIPPED ON Y-N FAULT
11 | 400KV-MUNIRABAD-RTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 02-03-2026 | 17:15 | PGCIL SR-1 | Correct Operation | Line holding from Munirabad end |  |  | KPCL | Correct Operation | Correct Operation |  |  | TRIPPED AND REASON AWAITED
12 | 220KV-BRAHMPURAM-LOWER PERIYAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 01-03-2026 | 09:50 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
13 | 220KV-THENI-SABARIGIRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | KSEB | 02-03-2026 | 05:46 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
14 | 400KV/220KV KALABURAGI-ICT-2 | TRANSFORMER | 400 | Intra | KPTCL | 03-03-2026 | 11:03 | KPTCL | Correct Operation | Tripped on overflux relay, due to sudden overloading | [7 empty] | under voltage protection operated
15 | 220KV-VARAHI-MRS SHIMOGA-3 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 26-03-2026 | 16:50 | KPCL | Correct Operation | AR successful. |  |  | KPTCL |  |  |  |  | Main-21 EarthFault, L3-E, Dist:86.9kms, Main-2 C-N, Zone-2, Dist:89.86kms, IC-2.259KA,
16 | 400KV-URAVAKONDA-MEHBOOBNAGAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | TGTRANSCO | 04-03-2026 | 05:48 | APTRANSCO | Correct Operation | enquired other end found no fault hence the feeder was taken into service |  |  | TGTRANSCO | Correct Operation | Line to ground fault |  |  | TRIPPED ON B-N FAULT
17 | 400KV-NELAMANGALA-TALGUPPA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 03-03-2026 | 13:59 | KPTCL | Correct Operation | NIL |  |  | KPTCL | Correct Operation | Tripped on Distance protection Main 1 and Main 2 |  |  | TRIPPED ON B-N FAULT
18 | 220KV-VARAHI-MRS SHIMOGA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 26-03-2026 | 19:40 | KPCL | Correct Operation | Tripped only @ Varahi end. |  |  | KPTCL |  |  |  |  | Main-2 relay operated, ABC trip, AR lockout, Earth Fault, IA=98.6A, IB=59.59A, IC=132.4AA.
19 | 220KV-VARAHI-MRS SHIMOGA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 26-03-2026 | 19:40 | KPCL | Correct Operation | Tripped @ both ends. |  |  | KPTCL |  |  |  |  | No data @ varahi end
20 | 220KV-VARAHI-MRS SHIMOGA-3 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 28-03-2026 | 12:19 | KPCL | Correct Operation | AR Successful. |  |  | KPTCL |  |  |  |  | Main- relay operated, trip B- Phase, Carrier aided trip, FL: L3-E, Dist: 88kms, Earth Fault,IL3=1.40KA.
21 | 220KV-ASUPAKA-LOWER_SILERU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 04-03-2026 | 12:59 | TGTRANSCO | Failure Operation | A/R not operated |  | Pending | APGENCO | Correct Operation | AR Operated successfully at Lower Sileru end |  |  | tripped on R-N Fault
22 | 400KV-VTPS_IV-SURYAPET-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | TGTRANSCO | 03-03-2026 | 13:15 | APGENCO | Correct Operation | Main1 and main 2 operated |  |  | TGTRANSCO | Correct Operation | Line to ground fault |  |  | TRIPPED ON R-N FAULT
23 | 400KV-KOLAR_AC-SRIPERUMBADUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 03-03-2026 | 14:09 | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | TRIPPED ON Y-N FAULT
24 | 400KV/220KV TALGUPPA-ICT-2 | TRANSFORMER | 400 | Intra | KPTCL | 05-03-2026 | 14:35 | KPTCL | Unwanted Operation | ICT#2 tripped due to maloperation of PRV contact multiplier. | Contact multiplication relay was replaced | Completed | [5 empty] | PRV(HV) mal-operated
25 | 220KV/33KV KSPPL-ICT-2 | TRANSFORMER | 220 | Intra | KLEIO_SOLAR | 08-03-2026 | 10:24 | KLEIO_SOLAR | Correct Operation | Correct | [7 empty] | Trip
26 | 400KV-GOOTY-SOMANAHALLI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 05-03-2026 | 12:28 | PGCIL SR-1 | Correct Operation | A/R attempted and tripped on persisting R-N fault |  |  | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | TRIPPED ON R-N FAULT
27 | 400KV/230KV NTPL-ICT-1 | TRANSFORMER | 400 | Intra | NTPL | 04-03-2026 | 16:38 | NTPL | Correct Operation | The relays tripped correctly on actual fault. | [7 empty] | 220kv side R phase LA burst
28 | 400KV-SATTENPALLY-PODILI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 08-03-2026 | 05:39 | APTRANSCO | Correct Operation | single line to ground fault |  |  | APTRANSCO | Correct Operation | At location no,69(SP) Y phase (middle) disc insulators flashed over and the conductor fallen on the bottom phase cross arm and rectification work under progress |  |  | Tripped
29 | 220KV-KOPPAL-Renew_Surya_Koppal-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | RENEW POWER PVT LTD | 08-03-2026 | 05:49 | INDIGRID | Correct Operation | Fault tripping |  |  | RENEW POWER PVT LTD | Unwanted Operation | B-Phase to Ground Distance protection operated. |  |  | TRIPPED ON B-N FAULT
30 | 765KV-KURNOOL_PG-CUDDAPAH-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Intra | POWERGRID | 08-03-2026 | 18:01 | PGCIL SR-1 | Correct Operation | NIL |  |  | PGCIL SR-1 | Correct Operation | NIL |  |  | Tripped on Over Voltage
31 | 400KV-SRISAILAM_LEFT_BANK-SATTENPALLY-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | TGTRANSCO | 08-03-2026 | 15:36 | TGGENCO | Correct Operation | The relay tripped as per the settings. |  |  | APTRANSCO | Correct Operation | No visible fault observed |  |  | 6.39kA, 13.4km, rph, z-1
32 | 400KV/110KV KAMUDHI-ICT-3 | TRANSFORMER | 400 | Intra | TANTRANSCO | 06-03-2026 | 16:04 | TANTRANSCO | Unwanted Operation | HV WTI trip | The contact of winding temperature trip found defective condition. Spare contact utilized for the same function and verified found ok. | Completed | [5 empty] | HV Winding Temperature trip spurious
33 | 220KV-ANCHEPALYA-NELAMANGALA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 05-03-2026 | 13:48 | KPTCL | Correct Operation | AR successful and line was holding |  |  | KPTCL | Correct Operation | Correctly operated. AR blocked due to high fault current |  |  | Tripped
34 | 220KV-NELAMANGALA-MAGADI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 05-03-2026 | 13:48 | KPTCL | Correct Operation | NA |  |  | KPTCL | Correct Operation | Mai supply failed to Anchepalya, Magadi and Nagamangala due to tripping of Anchepalya and Magadi both the lines at Nelamangala end |  |  | Tripped
35 | 400KV/11.5KV YADADRI TPP-ST-2 | TRANSFORMER | 400 | Intra | TGGENCO | 09-03-2026 | 00:09 | TGGENCO | Unwanted Operation | Three Phase fault observed in one of the 11kV boards,which further led to tripping of ST-2 on LV REF Protection. | [7 empty] | Tripped on LV2 REF Operated
36 | 220KV-THENI-SABARIGIRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | KSEB | 03-03-2026 | 07:46 | TANTRANSCO | Correct Operation | CAT,B,N,AR SUCCESSFUL |  |  | KSEB | Correct Operation | AR OPERATED |  |  | AR OPERATED
37 | 220KV-KANIYAMPETTA-KUNAMANGALAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 08-03-2026 | 12:26 | KSEB | Unwanted Operation | During relay testing of the 220 kV Kunnamangalam–Areacode Main-2 relay at the 220 kV Kunnamangalam Substation, an unintended trip occurred on the Main-1 relay of the 220 kV Kunnamangalam–Kaniyametta feeder. This was due to an incorrectly mapped GOOSE signal that is instead of AR initiation to the Main 1 of same feeder GOOSE subscribed by the other panel Main 1 relay. | GOOSE Subscription has been corrected in the Main 1 relay of 220kV Kaniyambetta Kunnamangalam at Kunnamangalam substation | Completed | KSEB | Correct Operation | No tripping occurred |  |  | 86A&86B relay optd
38 | 220KV-KANIYAMPETTA-KUNAMANGALAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 08-03-2026 | 13:29 | KSEB | Unwanted Operation | During relay testing of the 220 kV Kunnamangalam–Areacode Main-2 relay at the 220 kV Kunnamangalam Substation, an unintended trip occurred on the Main-1 relay of the 220 kV Kunnamangalam–Kaniyametta feeder. This was due to an incorrectly mapped GOOSE signal that is instead of AR initiation to the Main 1 of same feeder GOOSE subscribed by the other panel Main 1 relay. For Verification of this wrong GOOSE signal subscription this second tripping has been done | GOOSE Subscription has been corrected in the Main 1 relay of 220kV Kaniyambetta Kunnamangalam at Kunnamangalam substation | Completed | KSEB | Correct Operation | Not tripped |  |  | 86A&86B relay optd
39 | 765KV-CUDDAPAH-THIRUVALAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Inter | POWERGRID | 09-03-2026 | 18:01 | PGCIL SR-1 | Correct Operation | NIL |  |  | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | Tripped on Over Voltage
40 | 765KV-THIRUVALAM-ARIYALUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Intra | TANTRANSCO | 08-03-2026 | 18:55 | PGCIL SR-2 | Failure Operation | AR Failed to Operate. "CB Oil Pressure Low Reclosing Alarm" caused AR LO. | Bays belongs to TANTRANSCO- Tantransco have arranged OEM Engineer deputation for checking and revision of CB Pressure Setting. | Completed | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESFUL |  |  | A/R not successful at Thiruvalam
41 | 230KV-KARAIKUDI-PUDUKKOTTAI | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 12-03-2026 | 13:13 | PGCIL SR-2 | Correct Operation | Ar Attempted - tripped on persisting fault in Line. Rph-G Fault. 51.2 km/2.8 kA. |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | R Phase supporting insulator flashed over at Loc.No.8
42 | 230KV-PUGALUR-SPRING_PUGALUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | Spring_Pugalur | 11-03-2026 | 14:17 | PGCIL SR-2 | Correct Operation | 230KV Line AR sucessful at PGCIL end on 11-03-2026 at 14:17:37 Hrs in Dist Protection Zone-01 , B-G fault |  |  | Spring_Pugalur | Correct Operation | 230KV Line Fault tripped in transient fault |  |  | TRIPPED ON B-N FAULT
43 | 220KV-ASUPAKA-LOWER_SILERU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 12-03-2026 | 15:01 | TGTRANSCO | Failure Operation | AR not operated |  |  | APGENCO | Correct Operation | NA |  |  | Tripped
44 | 400KV-NCTPS_STAGE_II-VALLUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 12-03-2026 | 08:31 | TNPGCL | Correct Operation | nil |  |  | NTECL | Correct Operation | LINE TRIPPED ON ZONE-1 FAULT |  |  | Tripped on Y-B Fault
45 | 400KV-KALPAKKA-ASUPAKA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | APTRANSCO | 12-03-2026 | 11:57 | APTRANSCO | Correct Operation | fault tripping |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | TRIPPED ON B-N FAULT
46 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | TGTRANSCO | 13-03-2026 | 13:32 | APGENCO | Correct Operation | correct operation |  |  | TGGENCO | Correct Operation | Carrier Aided Protection Operated |  |  | TRIPPED DUE TO R-N FAULT
47 | 220KV-TP SAURYA LIMITED-KOPPAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TATA | 13-03-2026 | 15:07 | TATA | Correct Operation | Nil |  |  | INDIGRID | Correct Operation | Fault Tripping |  |  | B-N fault; Line Differential Operated
48 | 400KV-KAIGA-GUTTUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 13-03-2026 | 05:27 | NPCIL_KAIGA | Correct Operation | nil |  |  | KPTCL | Failure Operation | AR lockout should have not been initiated. |  |  | Rph to Ground fault
49 | 765KV-ARIYALUR-NCPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Intra | TANTRANSCO | 15-03-2026 | 06:50 | TANTRANSCO | Correct Operation | ZONE,1,Y,N,TOR_At loc.5,20,45,55,74,79,80,87&109 suspension insulator flashover |  |  | TANTRANSCO | Correct Operation | Zone.1,Y,N, TOR_At loc.5,20,45,55,74,79,80,87&109 suspension insulator flashover |  |  | TRIPPED ON Y-N FAULT
50 | 220KV-HIRIYUR-HIRIYUR_KAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 15-03-2026 | 12:34 | PGCIL SR-2 | Correct Operation | Line tripped due to Fault in KPTCL Line. |  |  | KPTCL |  |  |  |  | Tripped on B-ph fault. 1.2 kA 8.9 km from Hiriyur PG end
51 | 132KV-MADIRA-CHILLAKALLU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | APTRANSCO | 14-03-2026 | 01:49 | TGTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation |  |  |  | TRIPPED ON R-N FAULT
52 | 220KV-KUDGI_NTPC-VAJRAMATTI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 14-03-2026 | 03:01 | NTPC_KUDGI | Correct Operation | Main-1 and Main-2 Relays Zone-2 Protection initiated in R-Phase, Auto Reclosing Initiated from Relay end but as Carrier Healthy signal is not available Hence Auto Reclosure lock out operated and Converted to 3 Phase tripping |  |  | KPTCL |  |  |  |  | Tripped
53 | 220KV-KUDGI_NTPC-VAJRAMATTI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 14-03-2026 | 03:48 | NTPC_KUDGI | Correct Operation | Main-1 and 2 Zone-1 Protection operated in Y- Phase. As Carrier Healthy signal is not available, Single phase trip is converted to 3 phase tripping |  |  | KPTCL |  |  |  |  | yph fault
54 | 400KV-NARNOOR-SRISAILAM_LEFT_BANK-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | TGTRANSCO | 13-03-2026 | 15:05 | APTRANSCO | Correct Operation | Feeder tripped on Distance Protection |  |  | TGGENCO | Correct Operation | The relay tripped as per the settings. |  |  | TRIPPED ON B-N FAULT
55 | 400KV-TIPPAPUR-CHANDALAPUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 16-03-2026 | 12:28 | TGTRANSCO | Correct Operation | Correcet operation |  |  | TGTRANSCO | Unwanted Operation | spurious tripping |  |  | DT RECEIVED
56 | 765KV-CHILAKALURIPETA-CUDDAPAH-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Intra | PSITSL | 12-03-2026 | 18:01 | PGCIL SR-1 | Correct Operation | O/V St-1 Optd, DT Send, Gr-A/B Optd |  |  | PGCIL SR-1 | Correct Operation | DT receive from remote end due to OV ST-1 operated at remote end. |  |  | TRIPPED ON OVER VOLTAGE.
57 | 230KV-ARNI-BHAVANI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 18-03-2026 | 05:35 | TANTRANSCO | Correct Operation | ZONE.2,R,N |  |  | BHAVINI |  |  |  |  | Fault at Bhavini ss end
58 | 220KV-HIRIYUR-ZENATARIS_PSS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | HIRIYUR_ZREPL | 16-03-2026 | 14:40 | PGCIL SR-2 | Correct Operation | No trip/ fault events @ Hiriyur end. |  |  | HIRIYUR_ZREPL | Correct Operation | Breaker tripped on DC supply failure |  |  | tripped due to DC supply failure
59 | 220KV-HIRIYUR-Chitradurga-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 18-03-2026 | 18:44 | PGCIL SR-2 | Correct Operation | Line tripped due to Rph- G Fault in Line.- 8.6 km / 11kA. |  |  | KPTCL | Correct Operation | RN fault in ZOne-1 , no visual fault was detected during line inspection |  |  | Line tripped due to Rph- G Fault in Line.
60 | 230KV-MAPS-ECHUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 17-03-2026 | 08:15 | NPCIL_MAPS | Correct Operation | Jumper cut |  |  | TANTRANSCO | Correct Operation | BROKEN CONDUCTOR ALARM |  |  | R’ phase jumper cut at loc. 109
61 | 400KV-BPS-JAGALUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 16-03-2026 | 17:10 | KPTCL | Correct Operation | Correct Operation |  |  | KPTCL |  |  |  |  | Trip
62 | 400KV-JINDAL-BPS-4 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 16-03-2026 | 17:10 | JSW_THERMAL | Unwanted Operation | NO |  |  | KPTCL | Correct Operation | Line tripped only at BPS end |  |  | MAL-OPERATION
63 | 230KV-KUDANKULAM-TTPS | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 17-03-2026 | 15:15 | NPCIL_KKNP | Correct Operation | Kudankukalm & Kayathar 1 feeders are connected in Main Bus 2. |  |  | TNPGCL | Correct Operation | LBB protection operated in Kayathar #1 feeder connected in Main bus2. Hence kudankulam feeder connected in main Bus 2 also got tripped. |  |  | LBB protection operated in Kayathar #1 feeder connected in Main bus2. Hence kudankulam feeder connected in main Bus 2 also got tripped.
64 | 220KV-BIDADI_PG-BIDADI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 17-03-2026 | 18:23 | PGCIL SR-2 | Correct Operation | AR attempted but line tripped on persisiting fault in line- 1.4 KM, 19.4 kA. |  |  | KPTCL |  |  |  |  | DPR OPERATED
65 | 400KV-KALABURAGI-YTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 17-03-2026 | 21:52 | KPTCL | Correct Operation | At 21:53: Main Supply Failed from YTPS end. Both 400kV Bus voltages were Zero. At the same time both YTPS 1 & 2 lines CBs, ICT-1 & ICT-2 CBs were in closed condition along with this all 220kV lines CBs were in charged condition. |  |  | KPCL | Correct Operation | Correct operation |  |  | Tripped along with YTPS BPS Circuit *-2
66 | 132KV-BONAKAL-CHILLAKALLU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | TGTRANSCO | 18-03-2026 | 19:46 | TGTRANSCO | Correct Operation | station belongs to Railwys and feeding from Chillakallu |  |  | APTRANSCO | Correct Operation |  |  |  | B-Ph IF-6.02KA
67 | 400KV-KALABURAGI-YTPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 17-03-2026 | 21:52 | KPTCL | Correct Operation | At 21:53: Main Supply Failed from YTPS end. Both 400kV Bus voltages were Zero. At the same time both YTPS 1 & 2 lines CBs, ICT-1 & ICT-2 CBs were in closed condition along with this all 220kV lines CBs were in charged condition. |  |  | KPCL | Correct Operation | Correct operation |  |  | Tripped along with YTPS BPS Circuit -2
68 | 400KV-BPS-YTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 17-03-2026 | 20:27 | KPTCL | Correct Operation | Correct Operation |  |  | KPCL | Correct Operation | Correct operation |  |  | Tripped YTPS end 10.4 KA, 10.8 Kms R - N fault
69 | 220KV-TP SAURYA LIMITED-KOPPAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TATA | 17-03-2026 | 19:35 | TATA | Correct Operation | nil |  |  | INDIGRID | Correct Operation | Fault tripping |  |  | TRIPPED ON B-N FAULT
70 | 400KV-BPS-YTPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 17-03-2026 | 21:52 | KPTCL | Correct Operation | Correct Operation |  |  | KPCL | Correct Operation | Correct operation |  |  | Tripped
71 | 400KV/220KV KALABURAGI-ICT-1 | TRANSFORMER | 400 | Intra | KPTCL | 17-03-2026 | 21:52 | KPTCL | Correct Operation | At 21:53: Main Supply Failed from YTPS end. Both 400kV Bus voltages were Zero. At the same time both YTPS 1 & 2 lines CBs, ICT-1 & ICT-2 CBs were in closed condition along with this all 220kV lines CBs were in charged condition. | [7 empty] | Tripped
72 | 230KV-MAPS-ACHARAPAKAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 18-03-2026 | 23:56 | NPCIL_MAPS | Correct Operation | Location 17 all 3 phase insulators replaced by TNEB. R-PHASE was decapped. |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,R_Loc No.17 tension tower , R phase conductor has fallen down |  |  | TRIPPED AND REASON AWAITED
73 | 400KV-GAJWEL-CHANDALAPUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 16-03-2026 | 13:10 | TGTRANSCO | Correct Operation | Line is in service at Gajwel end. |  |  | TGTRANSCO | Unwanted Operation | spurious tripping |  |  | DC FAILURE
74 | 400KV/220KV KALABURAGI-ICT-2 | TRANSFORMER | 400 | Intra | KPTCL | 17-03-2026 | 21:52 | KPTCL | Correct Operation | YTPS line 1,2 charged at 08:08hrs and 08:23 hrs respectively and ICT-2 charged at 08:24 hrs. | [7 empty] | Tripped
75 | 220KV-GOOTY-RS-GOOTY-SWS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 18-03-2026 | 17:52 | APTRANSCO | Failure Operation | Line tripped at both ends on Y-N, zone-1 protection and AR Successful, line was holding from Gooty SwS end. AR not operated at Gooty RS end. | At Gooty RS end, It is observed that, CB READY opto input to distance relays was in OFF condition during tripping. The CB of the 220kV Gooty SwS line is of Pneumatic type, spring charge status was not wired. AR block, 3-Phase trip issued. The problem was rectified by making Spring charge status to relay permanently high. | Completed | APTRANSCO | Correct Operation |  |  |  | DETAILS AWAITED; LBB INITIATED
76 | 400KV-ARIYALUR-PUGALUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 19-03-2026 | 01:08 | TANTRANSCO | Correct Operation | ZONE.1R,N,TOR_Line breakdown attended at Loc .No.32 |  |  | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | R Phase distance protection operated
77 | 400KV-JINDAL-BPS-3 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 16-03-2026 | 17:10 | JSW_THERMAL | Unwanted Operation | NO |  |  | KPTCL | Correct Operation | Line tripped only at JSWEL end |  |  | MAL-OPERATION
78 | 220KV-RAICHUR_KA-UPPER_JURALA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | KPTCL | 18-03-2026 | 23:11 | KPTCL | Correct Operation | Due to Transient Fault |  |  | TGGENCO | Correct Operation | JURALA-RAICHUR-2 LINE Circuit Breaker is in Open condition at our end and tripped at Raichur end |  |  | R PHASE FAULT
79 | 220KV-KOPPAL-Renew_Surya_Koppal-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | RENEW POWER PVT LTD | 18-03-2026 | 22:28 | INDIGRID | Correct Operation | Fault tripping |  |  | RENEW POWER PVT LTD | Correct Operation | Tripping happened during the Heavy rain and lightning time. We have witnessed more lightning spikes around the site. So the tripping was occurred. |  |  | earth fault R phase
80 | 400KV-NCTPS_STAGE_II-VALLUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 19-03-2026 | 02:42 | TNPGCL | Correct Operation | nil |  |  | NTECL | Correct Operation | LINE TRIPPED ON ZONE-1 FAULT |  |  | TRIPPED AND REASON AWAITED
81 | 230KV-MAPS-S P KOIL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-03-2026 | 13:05 | NPCIL_MAPS | Correct Operation | B- N fault |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR_ TRANSIENT FAULT |  |  | TRIPPED ON B-N FAULT
82 | 400KV/220KV GADAG_PSS-ICT-6 | TRANSFORMER | 400 | Intra | GTL | 23-03-2026 | 21:58 | GTL | Unwanted Operation | The complete protection scheme and relay settings have been reviewed and verified in accordance with the OEM recommendations. | [7 empty] | differetial protection operated
83 | 400KV-ALAMATHY-SUNGAVARACHATRAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 19-03-2026 | 02:35 | TANTRANSCO | Correct Operation | DT RECEIVED |  |  | TANTRANSCO | Correct Operation | OV stage .1 operated_Voltage before tripping Vag=246.728 kV, Vbg=258.873 kV, Vcg=248.704 kV. Setting adopted Stage-1: 440 kV/8 s and Stage-2: 560 kV/100 ms. |  |  | Tripped on Over Voltage
84 | 220KV-KUDGI_NTPC-VAJRAMATTI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 19-03-2026 | 16:22 | NTPC_KUDGI | Correct Operation | Main-1 and 2 Zone-2 Protection operated in R & Y Phases. Carrier received from Remote end. Carried aided Trip Opetated. Currents during Fault: 2558 / 2312 / 161 A. Voltages During Fault: 97.22 / 101.2 / 125.1 KV Fault Location: 75.73 km from Kudgi End. Total Line Length: 79.42 km from Kudgi End. |  |  | KPTCL |  |  |  |  | Earth wire snapped at Loc No:12
85 | 220KV-KUDGI_NTPC-VAJRAMATTI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 19-03-2026 | 16:29 | NTPC_KUDGI | Correct Operation | Main-1 and 2 Zone-2 Protection operated in R & Y Phases. Carrier received from Remote end. Carried aided Trip Opetated. Currents during Fault: 2848 / 2533 / 259 A. Voltages During Fault: 102.6/ 106.7 / 128.1 KV Fault Location: 74.59 km from Kudgi End. Total Line Length: 79.42 km from Kudgi End. |  |  | KPTCL |  |  |  |  | Earth wire snapped at Loc No:12
86 | 132KV-KODADA-CHILLAKALLU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | TGTRANSCO | 24-03-2026 | 10:38 | TGTRANSCO | Correct Operation | Tripped on B-N,Zone-2 |  |  | APTRANSCO | Correct Operation |  |  |  | TRIPPED ON B-N FAULT
87 | 220KV-UDUMALPET-Pallivasal-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | KSEB | 12-03-2026 | 05:24 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | KSEB | Correct Operation | AR operated |  |  | AR OPERATED
88 | 132KV-KODADA-CHILLAKALLU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | TGTRANSCO | 20-03-2026 | 07:30 | TGTRANSCO | Correct Operation | Tripped on B-N,Zone-2 |  |  | APTRANSCO | Correct Operation |  |  |  | TRIPPED ON B-N FAULT
89 | 132KV-KODADA-CHILLAKALLU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | TGTRANSCO | 20-03-2026 | 15:06 | TGTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation |  |  |  | TRIPPED ON B-N FAULT
90 | 132KV-KODADA-CHILLAKALLU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | TGTRANSCO | 21-03-2026 | 07:42 | TGTRANSCO | Correct Operation | Tripped on B-N,Zone-2 |  |  | APTRANSCO | Correct Operation |  |  |  | TRIPPED ON R-N FAULT
91 | 220KV-IDDUKI-KOTHAMANGALAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 18-03-2026 | 15:26 | KSEB | Correct Operation | BBUSBAR SECTION 2 OPERATED AT IDUKKI DUE TO PT FLASH IN 2IDKL2 FEEDER |  |  | KSEB | Correct Operation |  |  |  | Relay Indications : Trip relay, AR block, no CLS perm, 96 BB/LBB
92 | 220KV-UDUMALPET-Pallivasal-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | KSEB | 12-03-2026 | 05:33 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | KSEB | Correct Operation | AR operated |  |  | AR OPERATED
93 | 400KV/220KV DONI-ICT-1 | TRANSFORMER | 400 | Intra | KPTCL | 20-03-2026 | 08:03 | KPTCL | Unwanted Operation | Human error |  | Pending | [5 empty] | Bus reactor B phase CB limb flashover.
94 | 132KV-KODADA-CHILLAKALLU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | TGTRANSCO | 21-03-2026 | 10:17 | TGTRANSCO | Correct Operation | Tripped on B-N,Zone-2 |  |  | APTRANSCO | Correct Operation |  |  |  | TRIPPED ON R-N FAULT
95 | 132KV-KODADA-CHILLAKALLU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | TGTRANSCO | 22-03-2026 | 06:54 | TGTRANSCO | Correct Operation | Tripped on B-N,Zone-2 |  |  | APTRANSCO | Correct Operation |  |  |  | Tripped
96 | 220KV-HIRIYUR-ZENATARIS_PSS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | HIRIYUR_ZREPL | 21-03-2026 | 14:09 | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | HIRIYUR_ZREPL | Correct Operation | Nil |  |  | Tripped on Y-B Fault
97 | 220KV-KANHIRODE-AMBALATHARA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 15-03-2026 | 05:43 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
98 | 132KV-KODADA-CHILLAKALLU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | TGTRANSCO | 22-03-2026 | 07:37 | TGTRANSCO | Correct Operation | Tripped on B-N,Zone-2 |  |  | APTRANSCO | Correct Operation |  |  |  | TRIPPED ON B PHASE FAULT
99 | 132KV-KODADA-CHILLAKALLU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | TGTRANSCO | 23-03-2026 | 02:57 | TGTRANSCO | Correct Operation | Tripped on B-N,Zone-2 |  |  | APTRANSCO | Correct Operation |  |  |  | TRIPPED ON B-N FAULT
100 | 132KV-KODADA-CHILLAKALLU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | TGTRANSCO | 23-03-2026 | 05:26 | TGTRANSCO | Correct Operation | Tripped on B-N,Zone-2 |  |  | APTRANSCO | Correct Operation |  |  |  | TRIPPED ON B-N FAULT
101 | 132KV-KODADA-CHILLAKALLU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | TGTRANSCO | 23-03-2026 | 06:13 | TGTRANSCO | Correct Operation | Tripped on B-N,Zone-2 |  |  | APTRANSCO | Correct Operation |  |  |  | TRIPPED DUE TO B-N LINE FAULT
102 | 400KV-TUMKUR-KUDGI_PG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KTL | 19-03-2026 | 01:11 | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | Tripped on YB fault
103 | 220KV-MYLATTI-AMBALATHARA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 15-03-2026 | 11:49 | KSEB | Correct Operation | No tripping . Incoming supply failure |  |  | KSEB | Correct Operation | No tripping
104 | 220KV-MADAKATHARA-ELANKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 18-03-2026 | 04:22 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
105 | 220KV-IDDUKI-KALAMASSERY-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 18-03-2026 | 15:26 | KSEB | Correct Operation | BBUSBAR SECTION 2 OPERATED AT IDUKKI DUE TO PT FLASH IN 2IDKL2 FEEDER |  |  | KSEB | Correct Operation |  |  |  | R phase PT flashed of 2IDKL 2 at Moolamattom Switchyard end and busbar protection acted
106 | 220KV-LOWER PERIYAR-IDDUKI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 18-03-2026 | 15:26 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation | BBUSBAR SECTION 2 OPERATED AT IDUKKI DUE TO PT FLASH IN 2IDKL2 FEEDER |  |  | Ann: M1 DP optd, MT86 optd M1:DP:R-G,---,46km M2:No indications
107 | 220KV-NEWKATAKADA-VIZHINJAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 18-03-2026 | 09:58 | KSEB | Unwanted Operation | .Maloperation of P545 Relay as the inrush current while charging the primary of Transformer at Receiving end SS (At the same Time R PH PT Fuse lug was damged and the relay misunderstood the fault as Zone 1 E/F and Tripped .Autoreclosure functioned at sending end and TOR issued but the relay tripped in Zone 1 E/F Indication. | The minimum settings for functioning of PT Fuse Fail Function revised to 20mA from 50mA,enabling the operation of the VT Fuse Fail Fn for lower values of load current. | Completed | KSEB | Correct Operation | Not Operated |  |  | Ann: DP optd, AR L/O DP:R-G,Z1,3.413km
108 | 220KV-HIRIYUR-INFOSYS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 25-03-2026 | 12:41 | PGCIL SR-2 | Correct Operation | Line Tripped due to fault in line. | AR testing carried out. |  | KPTCL |  |  |  |  | TRIPPED DUE TO R-N FAULT
109 | 220KV-IDDUKI-KOTHAMANGALAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 30-03-2026 | 16:27 | KSEB | Correct Operation | AR/LO |  |  | KSEB | Correct Operation | AR/LO |  |  | M2: DP: B-N, Z1, 83.28m
110 | 220KV-GADAG_PSS-Serentica_RI3PL_Gadag_S-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | SERENTICA_RIPL | 23-03-2026 | 21:58 | GTL | Correct Operation | AR Successful at gadag end. |  |  | SERENTICA_RI1PL |  |  |  |  | DIFFERENTIAL PROTECTION OPERATED at TIPPAPUR
111 | 132KV-WADAPALLI-PIDUGURALLA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | APTRANSCO | 26-03-2026 | 04:00 | TGTRANSCO | Correct Operation | Line is in open condition@ Wadapally SS |  |  | APTRANSCO | Correct Operation |  |  |  | R-N, Z-1, 25.77 Km, 3.77 kA
112 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | TGTRANSCO | 27-03-2026 | 11:40 | APGENCO | Correct Operation | correct operation |  |  | TGGENCO | Correct Operation | DEF Protection Operated |  |  | Reason awaited
113 | 220KV-AMBEWADI-PONDA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | KPTCL | 25-03-2026 | 21:20 | KPTCL | Correct Operation | NA | [7 empty] | TRIPPED ON B-N FAULT
114 | 220KV-UDUMALPET-Pallivasal-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | KSEB | 30-03-2026 | 03:28 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | KSEB | Correct Operation | AR operated |  |  | AR OPERATED
115 | 220KV-EDAMON-EDAPPON-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 28-03-2026 | 15:54 | KSEB | Unwanted Operation | PSB FAULT,PSB FAULT detected was routed to lockout trip | logic modified | Completed | KSEB | Correct Operation | No Tripping observed at Edappon end. |  |  | POWER SWING B DETECTED
116 | 220KV-TP SAURYA LIMITED-KOPPAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TATA | 25-03-2026 | 16:23 | TATA | Correct Operation | nil |  |  | INDIGRID | Correct Operation | Fault tripping |  |  | bph fault
117 | 400KV-PUGALUR-VELLALAVIDUTHI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 30-03-2026 | 13:56 | PGCIL SR-2 | Correct Operation | Line belongs to TNEB |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,B_Line patrol done & No visible fault |  |  | Tripped
118 | 220KV-SRISAILAM_RIGHT_BANK-DINDI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | TGTRANSCO | 26-03-2026 | 12:17 | APGENCO | Correct Operation | correct operation |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | YB FAULT
119 | 220KV-KOTHAMANGALAM-Pallivasal-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 30-03-2026 | 16:20 | KSEB | Correct Operation | AR OPERATED. |  |  | KSEB | Correct Operation | AR operated |  |  | AR OPERATED
120 | 220KV-IDDUKI-KALAMASSERY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 30-03-2026 | 17:09 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
121 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | TGTRANSCO | 26-03-2026 | 12:35 | APGENCO | Correct Operation | correct operation |  |  | TGGENCO | Correct Operation | DEF Protection Operated |  |  | Reason awaited
122 | 220KV-IDDUKI-KALAMASSERY-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 30-03-2026 | 17:09 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
123 | 230KV-NEYVELI_TS_II-KADALANGUDI | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 27-03-2026 | 15:56 | NLC | Correct Operation | A/R not happened at TS-2 end. |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRIPPED ON Y-N FAULT
124 | 220KV-KURNOOL_PG_III-SAEL2-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | SAEL | 29-03-2026 | 15:55 | PGCIL SR-1 | Correct Operation | Tripped on R-Phase to Gnd fault. |  |  | SAEL |  |  |  |  | DP, Z-1, R-N
125 | 220KV-NEWKATAKADA-VIZHINJAM_PORT-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 18-03-2026 | 09:58 | KSEB | Unwanted Operation | .Maloperation of P545 Relay as the inrush current while charging the primary of Transformer at Receiving end SS (At the same Time R PH PT Fuse lug was damged and the relay misunderstood the fault as Zone 1 E/F and Tripped .Autoreclosure functioned at sending end and TOR issued but the relay tripped in Zone 1 E/F Indication. | The Failed R-Phase PT Fuse of 02NKVI Feeder replaced and the minimum current to operate the PT Fuse Fail Function was rtevised to 20mA enabling operation even at 16A Load Current(Initially set at 50mA) | Completed | KSEB | Correct Operation | Not Operated |  |  | Ann: DP optd, AR L/O DP:R-G,Z1,3.413km
126 | 400KV/230KV MADURAI_PG-ICT-3 | TRANSFORMER | 400 | Intra | PGCIL SR-2 | 27-03-2026 | 19:39 | PGCIL SR-2 | Correct Operation | Protection Schemes operated correct. | [7 empty] | operation of Buchholz trip, PRV -2 , Transformer Differential and REF protections. Heavy fire reported
127 | 400KV-NCTPS_STAGE_II-SUNGAVARACHATRAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 26-03-2026 | 18:33 | TNPGCL | Correct Operation | NIL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | Tripped
128 | 220KV-PUNNAPRA-NEW PALLOM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | POWERGRID | 25-03-2026 | 03:28 | KSEB | Correct Operation | AR OPERATED. |  |  | KSEB | Correct Operation | AR operated |  |  | AR OPERATED
129 | 220KV-EDAMON-POTHENCODE-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 28-03-2026 | 17:29 | KSEB | Correct Operation | AR OPERATED. |  |  | KSEB | Correct Operation | AR operated |  |  | AR OPERATED
130 | 220KV-EDAMON-SABARIGIRI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 28-03-2026 | 15:54 | KSEB | Correct Operation | EARTH WIRE SNAPPING,reclosed & tripped due to persistent fault |  |  | KSEB | Correct Operation | EARTH WIRE SNAPPING |  |  | Ann: M1 DP & M2 optd, AR optd, AR L/O, carrier received M1: DP: R ph,Z1,---, VT fuse fail, ZCOM, AR optd M2:DP: RYB,Z1,29.96km, L1-N
131 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | TGTRANSCO | 29-03-2026 | 11:44 | APGENCO | Correct Operation | Correct operation |  |  | TGGENCO | Correct Operation | Zone-1 Operated |  |  | TRIPPED ON B-N FAULT
132 | 220KV-KANHIRODE-AMBALATHARA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 28-03-2026 | 16:01 | KSEB | Correct Operation | AR OPERATED. |  |  | KSEB | Correct Operation | AR operated |  |  | AR OPERATED
133 | 400KV-KRISHNAPATNAM-SEIL_P2-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | ANDHRA PRADESH | 28-03-2026 | 17:23 | APGENCO | Correct Operation | Pole discrepancy operated |  |  | SEIL | Failure Operation | Relay Maloperation |  | Completed | Tripped with no indications
134 | 220KV-SHORNUR-AREACODE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 28-03-2026 | 14:48 | KSEB | Correct Operation | AR OPERATED. |  |  | KSEB | Correct Operation | AR operated |  |  | AR OPERATED
135 | 220KV-AREACODE-KUNAMANGALAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 28-03-2026 | 16:02 | KSEB | Correct Operation | AR was attempted; however, due to the persistence of the fault, the system went into lockout. |  |  | KSEB | Correct Operation | AR was attempted; however, due to the persistence of the fault, the system went into lockout. |  |  | Ann: M1 M2 DP optd,AR optd M1:Diff:C-N,Z1-Z2-Z3,21.72km M1:Diff:C-G,---,32.1km
136 | 400KV-KALPAKKA-KHAMMAM_PG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | APTRANSCO | 29-03-2026 | 13:52 | APTRANSCO | Correct Operation | feeder tripped on fault |  |  | PGCIL SR-1 | Correct Operation | Feeder tripped on R-N fault |  |  | Khammam: Z-1, R-N, 80.47 Kms, 3.896 kA; Kalpakka: Z-1, R-N, 266.01 Kms, 1.57 kA
137 | 400KV-KOZHIKODE-MADAKKATHARA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KSEB | 28-03-2026 | 15:55 | PGCIL SR-2 | Correct Operation | AR Successful Both ends- Rph-G Fault- 12.55 km / 11.25 kA. |  |  | KSEB | Correct Operation | AR operated |  |  | AR Successful Both ends. Rph-G Fault in line,
138 | 220KV-LOWER PERIYAR-MADAKATHARA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 28-03-2026 | 20:33 | KSEB | Correct Operation | AR OPERATED. |  |  | KSEB | Correct Operation | AR operated |  |  | AR OPERATED
139 | 220KV-ALUVA-KOTHAMANGALAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 29-03-2026 | 16:15 | KSEB |  |  |  |  | KSEB |  |  |  |  | Ann: Nil M1: DP: R-G, Z1, 10.6km Diff protn: Rph M2: DP: R-N, Z1, 12.55km Diff protn: Rph M1: DP: R-G, ----, 11.2km, AR optd M2: Diff protn: Rph, AR optd M1: DP: R-G, Z1, 13.2km, SOTF optd Diff protn: Rph, AR optd M2: DP: R-N, Z1, 10.39km, SOTF optd Diff protn: Rph, AR optd
140 | 220KV-TIRUNELVELI-EDAMON-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | POWERGRID | 30-03-2026 | 19:59 | PGCIL SR-2 | Correct Operation | AR successful both ends, Bph-G - 81.6 km / 1.78 kA. |  |  | KSEB | Correct Operation | AR OPTD,Z1 FAULT |  |  | Ar Successful Both ends- Bph-G Fault in line.
141 | 220KV-EDAMON-SABARIGIRI-3 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 30-03-2026 | 19:59 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation | AR optd Z1 fault |  |  | AR OPERATED
142 | 220KV-EDAMON-SABARIGIRI-3 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 28-03-2026 | 15:54 | KSEB | Correct Operation | EARTH WIRE SNAPPING |  |  | KSEB | Correct Operation | EARTH WIRE SNAPPING,reclosed & tripped due to persistent fault |  |  | Ann: M1 DP & M2 optd, AR optd, AR L/O M1: DP: Y ph, B ph,Z1,17km M2:DP: Y ph, B ph,Z1,52.4km,L2-L3,VT fuse fail, ZCOM,
143 | 220KV-HIRIYUR-HIRIYUR_KAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 31-03-2026 | 20:25 | PGCIL SR-2 | Correct Operation | AR Unsuccessful due Line fault. Rph-G Fault in Line- 9.21 km / 8.8 kA. |  |  | KPTCL |  |  |  |  | tripped on R-N Fault
144 | 220KV-KOPPAL-Renew_Surya_Koppal-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | RENEW POWER PVT LTD | 30-03-2026 | 14:11 | INDIGRID | Unwanted Operation | Direct Trip (DT) signal received from the remote end |  |  | RENEW POWER PVT LTD | Correct Operation | Based on the operation, the tripping was correct. |  |  | DT Received (Mal-Operation)
145 | 400KV-PAVAGADA_PG-TUMKUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 31-03-2026 | 18:21 | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | PGCIL SR-2 | Failure Operation | AR Failed. Bays belong to KPTCL. | AR Logic issue rectified @ Tumkur end. | Completed | B PHASE TO GROUND FAULT
146 | 400KV-KALPAKKA-ASUPAKA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | APTRANSCO | 04-03-2026 | 12:39 | APTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation | AR operated |  |  | B-PH FAULT
147 | 220KV-CHILLAKALLU-SURYAPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | TGTRANSCO | 08-03-2026 | 20:35 | APTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation | AR Successful |  |  | B-PH FAULT
148 | 400KV-KALPAKKA-ASUPAKA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | APTRANSCO | 20-03-2026 | 22:30 | APTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation | AR Successful |  |  | B-PH FAULT
149 | 400KV-MALKARAM-SURYAPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 27-03-2026 | 21:55 | TGTRANSCO | Correct Operation | AR OPERATED SUCESSFULLY |  |  | TGTRANSCO | Correct Operation | AR Successful |  |  | Y-phase to ground fault
150 | 400KV-NELLORE_PG-VIJAYAWADA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 28-03-2026 | 06:12 | PGCIL SR-1 | Correct Operation | AR operated successfully |  |  | PGCIL SR-1 | Correct Operation | AR operated successfully |  |  | AR operated successfully at both ends
151 | 400KV-CUDDAPAH-TUMKUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | PSITSL | 18-03-2026 | 23:23 | PGCIL SR-1 | Correct Operation | AR operated successfully at both ends |  |  | PGCIL SR-2 | Correct Operation | AR Successful both ends - Rph-G fault- 151.6 km/ 2.05 kA. |  |  | AR operated successfully at both ends
152 | 400KV-CUDDAPAH-NP_KUNTA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 18-03-2026 | 21:58 | PGCIL SR-1 | Correct Operation | AR operated successfully |  |  | PGCIL SR-1 | Correct Operation | AR operated successfully |  |  | AR operated successfully
153 | 400KV-KURNOOL_PG-NAGARJUNASAGAR_PG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 18-03-2026 | 05:24 | PGCIL SR-1 | Correct Operation | AR operated successfully |  |  | PGCIL SR-1 | Correct Operation | AR operated successfully |  |  | AR operated successfully
154 | 400KV-GOOTY-NELAMANGALA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 11-03-2026 | 14:08 | PGCIL SR-1 | Correct Operation | AR operated successfully |  |  | KPTCL | Correct Operation |  |  |  | AR operated successfully
155 | 400KV-GHANAPUR-NAGARJUNASAGAR_PG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 09-03-2026 | 05:47 | PGCIL SR-1 | Correct Operation | AR operated successfully |  |  | PGCIL SR-1 | Correct Operation | AR operated successfully |  |  | AR operated successfully
156 | 400KV-VIJAYAWADA-NELLORE_AP-3 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 18-03-2026 | 16:11 | PGCIL SR-1 | Correct Operation | AR operated successfully |  |  | APTRANSCO | Correct Operation |  |  |  | AR operated successfully
157 | 765KV-NIZAMABAD-WARDHA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Inter | POWERGRID | 18-03-2026 | 02:43 | PGCIL SR-1 | Correct Operation | AR operated successfully | [7 empty] | AR operated successfully
158 | 400KV-ILFS-NAGAPATTNAM_PS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | ILFS | 28-03-2026 | 15:15 | ILFS |  |  |  |  | PGCIL SR-2 | Correct Operation | AR Successful both ends- Rph-G Fault in line - 6.42 km / 10.18 kA. |  |  | R-E fault due to tree hit
159 | 400KV-ILFS-NAGAPATTNAM_PS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | ILFS | 28-03-2026 | 12:45 | ILFS |  |  |  |  | PGCIL SR-2 | Correct Operation | AR Successful- Rph-G 6.42 km / 10.18 kA. |  |  | R-E fault due to tree hit
160 | 230KV-KUDANKULAM-S R PUDUR | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 30-03-2026 | 11:41 | NPCIL_KKNP | Correct Operation | ADL15 SR-Pudur line got tripped on Zone-1 distance protection |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | ADL15 SR-Pudur line got tripped on Zone-1 distance protection, B-phase to earth fault, fault current: 6813A, fault distance: 29.7KM. Auto reclose successfully completed.
161 | 220KV-RTPS-SHAHAPUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 01-03-2026 | 20:59 | KPCL | Correct Operation |  |  |  | KPTCL | Correct Operation | A/R operated and successful |  |  | 220KV RTPS END:Zone-2, Fault loop Rph-GND, Distance:75.2 KM ,I=2.0 KA
162 | 220KV-LINGSUGUR-RTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 03-03-2026 | 00:11 | KPTCL | Correct Operation | RN fault in zone-1, 1.16kA,64.64km, TOR operated due to persistent fault |  |  | KPCL | Correct Operation |  |  |  | 220KV RTPS END:Zone-1, Fault loop Rph-GND, Distance:33.85 KM ,I=4.708 KA
163 | 220KV-LINGSUGUR-RTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 03-03-2026 | 12:45 | KPTCL | Correct Operation | BN fault in ZOne-1 ,78.4, TOR due to persistent fault |  |  | KPCL | Correct Operation |  |  |  | 220KV RTPS END : Zone-1, Fault loop Bph-GND, Distance:34KM ,I=4.395 KA
164 | 220KV-RTPS-RAMASAMUDRA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 15-03-2026 | 15:57 | KPCL | Correct Operation |  |  |  | KPTCL |  |  |  |  | 220KV RTPS END : Zone-1, Fault loop Bph-GND, Distance:584 Mtr ,I= 32 KA
165 | 220KV-LINGSUGUR-RTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 17-03-2026 | 20:17 | KPTCL | Correct Operation | AR successful at Lingasugur end , BN fault in ZOne-1 |  |  | KPCL | Correct Operation |  |  |  | 220KV RTPS END : Zone-1, Fault loop Bph-GND, Distance: 41.5 KM ,I= 3.42 KA
166 | 220KV-RTPS-SHAHAPUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 22-03-2026 | 06:01 | KPCL | Correct Operation |  |  |  | KPTCL | Correct Operation | BN fault in Zone-1, No visual fault detected during line inspection |  |  | 220KV RTPS END : Zone-1, Fault loop Bph-GND, Distance: 7.5 KM ,I= 14 KA
167 | 220KV-LINGSUGUR-RTPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 25-03-2026 | 14:43 | KPTCL | Correct Operation | BN fault in ZOne-1,5.9kA,18.1km,TOR |  |  | KPCL | Correct Operation |  |  |  | 220KV RTPS END : Zone-2, Fault loop Bph-GND, Distance: 102.8 KM ,I= 1.58 KA
168 | 220KV-RTPS-SHAHAPUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 28-03-2026 | 01:52 | KPCL | Correct Operation |  |  |  | KPTCL | Correct Operation | Zone-1 ,RN fault, 59.8km , TOR |  |  | 220KV RTPS END : Zone-1, Fault loop Rph-GND, Distance: 8.44 KM ,I= 12.34 KA
169 | 765KV-ARIYALUR-NCPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Intra | TANTRANSCO | 19-03-2026 | 03:12 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
170 | 400KV-SHOLINGANALLUR-KALVENDAPATTU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 19-03-2026 | 02:36 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | PGCIL SR-2 | Correct Operation | AR Successful - Rph-G- 20.4 km / 7.43 kA. |  |  | TRANSIENT FAULT Rph-G fault- AR Successful both ends.
171 | 400KV-MANALI-PULIYANTHOPE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 19-03-2026 | 02:42 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
172 | 400KV-ALAMATHY-TIRUVALAM_TN-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 20-03-2026 | 09:54 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
173 | 400KV-ALAMATHY-TIRUVALAM_TN-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 23-03-2026 | 12:41 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
174 | 230KV-SRIPERUMBADUR_TN-THARAMANI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 01-03-2026 | 07:14 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | CAT,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
175 | 230KV-MYVADI-O.K.MANDAPAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 01-03-2026 | 12:08 | TANTRANSCO | Correct Operation | CAT,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
176 | 230KV-MYVADI-O.K.MANDAPAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 01-03-2026 | 12:15 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
177 | 220KV-SULURPET-GUMMIDIPOONDI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | TANTRANSCO | 01-03-2026 | 13:43 | APTRANSCO | Correct Operation |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
178 | 230KV-KAVANUR-MILAVITTAN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 01-03-2026 | 13:55 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
179 | 230KV-PASUMALAI-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-03-2026 | 01:55 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
180 | 230KV-Chekkanurani-AMUDHAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-03-2026 | 03:23 | TANTRANSCO | Correct Operation | CAT,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
181 | 230KV-SINGARPET-TIRUVANAMALAI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 03-03-2026 | 03:31 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
182 | 230KV-KARAIKUDI-SEMBATTI | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 03-03-2026 | 05:29 | PGCIL SR-2 | Correct Operation | AR Successful both ends- Karaikudi end - 64.596KM, FC: 2.85 KA. |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
183 | 230KV-COIMBATORE-SELVAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 05-03-2026 | 05:55 | TANTRANSCO | Failure Operation | ZONE.1,Y,N,_DIFF RELAY TIME SYNC ISSUE_ AR BLOCK | GPS DEFECTIVE PATCH CORD REPLACED | Completed | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
184 | 220KV-KAKINADA-PARAVADA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 06-03-2026 | 23:42 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
185 | 220KV-PARAVADA-ANRAK-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 02-03-2026 | 12:10 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
186 | 220KV-KAKINADA-PARAVADA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 03-03-2026 | 10:24 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
187 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 03-03-2026 | 12:48 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
188 | 220KV-CUDDAPAH-RENIGUNTA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 03-03-2026 | 13:52 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
189 | 220KV-VTPS-RENTACHINTHALA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 04-03-2026 | 04:20 | APGENCO | Correct Operation | R-PH, Z-1 ,AR OPERATED AND SUCCESS , Fault Distance: 84.25 KM, Current: 2.029KA |  |  | APTRANSCO | Correct Operation
190 | 220KV-SULURPET-NELLORE_AP-3 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 05-03-2026 | 11:37 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
191 | 220KV-BOYAREDDYPALLI-TADIPATHRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 05-03-2026 | 11:40 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
192 | 220KV-ONGOLE-KANDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 05-03-2026 | 11:59 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
193 | 220KV-BOYAREDDYPALLI-TADIPATHRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 05-03-2026 | 12:07 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Failure Operation |  | 220kV Tadipatri-Boyareddypalli line tripped at both ends on B-N fault. AR Successful, line was holding from Tadipatri end and AR not operated at Boyareddypalli end. CB Spring charge status was changed to OFF condition, resulted in changing of CB READY status to OFF for both Main 1 and 2 distance relays. Due to this, AR function was blocked by distance relays. Hence 3 Phase trip operated. At 220kV SS Boyareddypalli, on 220kV Tadipatri line, Termination for the spring charge auxiliary contact in B Phase CB limb cubicle was not in firm contact with the terminal of auxiliary contact. The same was rectified and ensured the healthiness of spring charge status. | Completed
194 | 220KV-CUDDAPAH-KADAPA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 05-03-2026 | 12:45 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
195 | 220KV-KANDUKUR-RACHARLAPADU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 05-03-2026 | 13:06 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
196 | 400KV-KALPAKKA-VEMAGIRI_AP-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 06-03-2026 | 07:27 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
197 | 220KV-PODILI_OLD-PARCHOOR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 06-03-2026 | 11:08 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
198 | 220KV-ANANTHAPUR-KALYANDURGA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 06-03-2026 | 11:40 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
199 | 220KV-RENIGUNTA-KODURU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 06-03-2026 | 13:00 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
200 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_AP-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 06-03-2026 | 13:45 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
201 | 220KV-PENDURTHI-MARADAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 07-03-2026 | 04:48 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
202 | 220KV-KAKINADA-PARAVADA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 07-03-2026 | 05:26 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
203 | 220KV-PENDURTHI-MARADAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 07-03-2026 | 06:04 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
204 | 230KV-TIRUVALAM_TN-KANCHIPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 05-03-2026 | 09:57 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
205 | 220KV-PODILI_OLD-PARCHOOR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 07-03-2026 | 06:07 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
206 | 230KV-KARAIKUDI(TN)-KAVANUR-4 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 05-03-2026 | 14:09 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
207 | 230KV-METTURAUTO-HOSUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 05-03-2026 | 14:15 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
208 | 220KV-CUDDAPAH-RENIGUNTA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 07-03-2026 | 13:49 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
209 | 230KV-KARIMANAGALAAM-UDANAPALLI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 05-03-2026 | 14:15 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
210 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_AP-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 07-03-2026 | 14:01 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
211 | 220KV-PODILI_OLD-MARKAPUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 08-03-2026 | 06:12 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
212 | 220KV-ATMAKUR-PODILI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 08-03-2026 | 06:45 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
213 | 230KV-MAPS-ECHUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 06-03-2026 | 13:04 | NPCIL_MAPS | Correct Operation | B- PHASE Transient fault and AR was success |  |  | TANTRANSCO | Correct Operation | CAT,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
214 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 09-03-2026 | 02:54 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
215 | 220KV-SRISAILAM_RIGHT_BANK-BILAKALAGUDUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 09-03-2026 | 04:08 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
216 | 230KV-UDUMALPET-ALIYAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 06-03-2026 | 23:38 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
217 | 230KV-UDUMALPET-ALIYAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 07-03-2026 | 01:21 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
218 | 230KV-KARAIKUDI(TN)-KARAMBAYAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 07-03-2026 | 04:20 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
219 | 400KV-KALPAKKA-KHAMMAM_PG-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | APTRANSCO | 08-03-2026 | 12:49 | APTRANSCO | Correct Operation |  |  |  | PGCIL SR-1
220 | 230KV-KADAMPARAI-MYVADI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 07-03-2026 | 05:54 | TNGECL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
221 | 220KV-BOMMUR-LOWER_SILERU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 09-03-2026 | 12:55 | APTRANSCO | Correct Operation |  |  |  | APGENCO | Correct Operation | At Lower sileru end as per the DR analysis the Earth fault start observed in Main-1 relay(P442), meanwhile advance tripping happened in the Upper Sileru and Bommuru end. |  |  | The 220KV Lower Sileru-Bommuru feeder tripped at Bommuru end and upper Sileru end only. No relays operated at Lower sileru and Donkarayi end. As per the DR analysis at Upper sileru end detect the VT fuse fail and operated the Non-directional Earth fault in Main-2(D60) relay
222 | 230KV-KAYATHAR(TN)-SANGANERI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 07-03-2026 | 06:50 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
223 | 230KV-EACHANGADU-POIYUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 07-03-2026 | 13:38 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
224 | 230KV-KAYATHAR(TN)-TTPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-03-2026 | 04:02 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TNPGCL | Correct Operation | AR success at TTPS end |  |  | TRANSIENT FAULT
225 | 230KV-Chekkanurani-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-03-2026 | 05:41 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
226 | 230KV-KADAMPARAI-MYVADI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 09-03-2026 | 02:54 | TNGECL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
227 | 230KV-THIRUVARUR-KARAMBAYAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 09-03-2026 | 04:34 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Failure Operation | ZONE.1,Y,N,PD operated | AR Close pulse Contact defect in sifang relay. New Output card arranged . Line clear awaited | Pending | TRANSIENT FAULT
228 | 230KV-STCMS-DEVIAKURICHI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 09-03-2026 | 06:03 | TANTRANSCO | Correct Operation | Line idly charged from Deviakuruchi |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
229 | 230KV-KADALANGUDI-KUMBAKONAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 10-03-2026 | 11:38 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | CAT,B,N,AR SUCCESSFUL
230 | 230KV-MYVADI-O.K.MANDAPAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 10-03-2026 | 11:40 | TANTRANSCO | Correct Operation | Line idly charged from O.K.Mandapam |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
231 | 230KV-Chekkanurani-AMUDHAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 11-03-2026 | 01:46 | TANTRANSCO | Correct Operation | CAT,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
232 | 230KV-UDUMALPET-ALIYAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 12-03-2026 | 05:43 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
233 | 230KV-AMUDHAPURAM-NALLAMANAICKENPATTI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 13-03-2026 | 02:33 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
234 | 230KV-INGUR-KARAMADAI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 13-03-2026 | 06:03 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
235 | 230KV-PUGALUR-KURUKATHI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 13-03-2026 | 08:29 | PGCIL SR-2 | Correct Operation | AR successful Both ends . Rph-G - 17.62 km / 8.24 kA. |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT Rph-G.
236 | 230KV-KAVANUR-MILAVITTAN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 13-03-2026 | 20:28 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
237 | 220KV-KAKINADA-PARAVADA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 09-03-2026 | 19:37 | APTRANSCO | Unwanted Operation | Tripped at Kakinada end only on operation of Pole discrepancy relay. | Positive supply extended to R,Y-Phase leads in TC 1 cable, R and Y poles tripped. later PD operated. The defective TC-1 cable was replaced with sapre cable. | Completed | APTRANSCO | Correct Operation
238 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 10-03-2026 | 02:07 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
239 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 11-03-2026 | 05:11 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
240 | 220KV-GOOTY-SWS-SHAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 11-03-2026 | 12:17 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Failure Operation | Line tripped at both ends due to R-N fault. AR Successful, line was holding from Shapuram end. DT received at Gooty end, hence 3-Phase trip operated. | At Shapuram end, Carrier send signal from relay was given to DT send signal in protection coupler. For zone-1 fault, carrier send signal generated by Relay and due to wrong wiring, DT was send to remote end. The wiring was modified and corrected. | Completed
241 | 220KV-GUDIVADA-AKIVEEDU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 11-03-2026 | 19:52 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
242 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 12-03-2026 | 00:30 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
243 | 220KV-GARIVIDI-BOBBILI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 12-03-2026 | 12:17 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
244 | 220KV-KAKINADA-ANRAK-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 12-03-2026 | 12:18 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
245 | 220KV-PARAVADA-ANRAK-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 12-03-2026 | 12:18 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
246 | 220KV-SOMASAMUDRA-REGULAPADU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 12-03-2026 | 12:22 | KPTCL | Correct Operation |  |  |  | APTRANSCO | Correct Operation
247 | 220KV-SRISAILAM_RIGHT_BANK-SOMAYAJULAPALLI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 12-03-2026 | 13:29 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
248 | 220KV-SRISAILAM_RIGHT_BANK-BILAKALAGUDUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 12-03-2026 | 13:30 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
249 | 220KV-GARIVIDI-BOBBILI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 12-03-2026 | 14:26 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
250 | 220KV-PENDURTHI-MARADAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 12-03-2026 | 14:35 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
251 | 220KV-GARIVIDI-TEKKALI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 14-03-2026 | 12:33 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
252 | 220KV-PODILI_OLD-MARKAPUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 15-03-2026 | 07:00 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
253 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_AP-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 17-03-2026 | 15:01 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
254 | 220KV-PULIVENDULA-GOLLAPURAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 18-03-2026 | 00:54 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
255 | 220KV-KONDAPALLI-CHILLAKALLU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 18-03-2026 | 05:17 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
256 | 220KV-VTPS-RENTACHINTHALA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 18-03-2026 | 16:41 | APGENCO | Correct Operation | R-PH, Z-1 ,AR OPERATED AND SUCCESS, Fault Distance 2.967KM, current: 25.80KA |  |  | APTRANSCO | Correct Operation
257 | 220KV-DHONE-NANSURALLA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 18-03-2026 | 19:48 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
258 | 220KV-LAKKASAGARAM-NANSURALLA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 18-03-2026 | 19:49 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
259 | 230KV-KARAIKUDI(TN)-KAVANUR-4 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 15-03-2026 | 12:58 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
260 | 230KV-KAVANUR-KAMUDHI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 15-03-2026 | 23:35 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
261 | 230KV-TTPS-KINNIMANGLAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 16-03-2026 | 06:10 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
262 | 230KV-UDUMALPET-ALIYAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 17-03-2026 | 13:37 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
263 | 230KV-PUGALUR-KURUKATHI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 17-03-2026 | 21:22 | PGCIL SR-2 | Correct Operation | AR Successful Rph-G Fault- 41.9 KM / 4.449 kA. |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT, AR Successful
264 | 230KV-UDUMALPET-ALIYAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 18-03-2026 | 00:35 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
265 | 230KV-MYVADI-O.K.MANDAPAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 18-03-2026 | 04:47 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
266 | 230KV-KAYATHAR(TN)-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 18-03-2026 | 09:28 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TNPGCL | Correct Operation | AR success at TTPS end |  |  | TRANSIENT FAULT - Y PH, Zone 1,
267 | 230KV-PALAVADI-UDANAPALLI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 18-03-2026 | 17:54 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
268 | 230KV-PALAVADI-UDANAPALLI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 18-03-2026 | 19:23 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
269 | 230KV-KARAIKUDI(TN)-VALATHUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 18-03-2026 | 22:03 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
270 | 230KV-SALEM_TN-UNJANAI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 18-03-2026 | 23:44 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | CAT,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
271 | 230KV-PASUMALAI-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-03-2026 | 04:46 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
272 | 230KV-METTURAUTO-PALAVADI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-03-2026 | 00:07 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | CAT,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
273 | 230KV-DEVIAKURICHI-VALAYAPATTY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-03-2026 | 01:54 | TANTRANSCO | Failure Operation | ZONE.1,R,N,AR Lockout due to carrier fail signal at Deviakuruchi | Carrier fail has to be checked | Pending | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
274 | 230KV-HOSUR_PG-TIRUPATTUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 21-03-2026 | 02:27 | PGCIL SR-2 | Correct Operation | AR Successful both ends Rph-G fault- 6.6 kM /13.65 kA. |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT- Rph-G Fault - AR Successful both ends.
275 | 230KV-KINNIMANGLAM-SAMAYANALLUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 21-03-2026 | 06:43 | TANTRANSCO | Failure Operation | ZONE.1,B,N,AR LOCKOUT_BREAKER ISSUE | Spring charge issue attended | Completed | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
276 | 230KV-ARASUR-GOBI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 21-03-2026 | 14:10 | TANTRANSCO | Correct Operation | idly charged from Gobi |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
277 | 230KV-UDUMALPET-ALIYAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 22-03-2026 | 04:26 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
278 | 230KV-TTPS-KINNIMANGLAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 22-03-2026 | 06:04 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
279 | 220KV-MADANAPALLY-KALIKIRI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 18-03-2026 | 21:15 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
280 | 220KV-CUDDAPAH-RENIGUNTA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 18-03-2026 | 22:25 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
281 | 230KV-KARAIKUDI(TN)-KARAMBAYAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 22-03-2026 | 13:29 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
282 | 220KV-RENIGUNTA-KODURU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 19-03-2026 | 00:19 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
283 | 220KV-SRISAILAM_RIGHT_BANK-PODILI_OLD-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 19-03-2026 | 13:28 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
284 | 230KV-SALEM_TN-UNJANAI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 22-03-2026 | 14:04 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | CAT,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
285 | 220KV-ONGOLE-PODILI_OLD-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 19-03-2026 | 15:17 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
286 | 230KV-UDUMALPET-ALIYAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 23-03-2026 | 02:15 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
287 | 220KV-PODILI_OLD-PODILI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 19-03-2026 | 17:45 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
288 | 230KV-PUGALUR(TN)-RENGANATHAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 24-03-2026 | 06:06 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
289 | 220KV-KONDAPALLI-CHILLAKALLU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 19-03-2026 | 21:41 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
290 | 230KV-KARAIKUDI(TN)-KAVANUR-4 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 24-03-2026 | 08:01 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
291 | 220KV-GOOTY-SWS-SHAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 20-03-2026 | 12:04 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
292 | 230KV-HOSUR_PG-HOSUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 25-03-2026 | 05:47 | PGCIL SR-2 | Correct Operation | AR Successful- Rph-G- 23.69 km/ 5,28 kA. |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT- Rph-G, - AR Successful both ends
293 | 220KV-GUDIVADA-AKIVEEDU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 20-03-2026 | 12:10 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
294 | 220KV-KALPAKKA-SIMHACHALM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 20-03-2026 | 19:30 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
295 | 230KV-Chekkanurani-AMUDHAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 25-03-2026 | 21:03 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
296 | 220KV-KAKINADA-ANRAK-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 20-03-2026 | 22:46 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
297 | 220KV-ONGOLE-KANDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 21-03-2026 | 05:41 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
298 | 230KV-KADALANGUDI-PP_NALUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 27-03-2026 | 04:45 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
299 | 400KV-VTPS_IV-THALLAYAPALEM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 21-03-2026 | 14:59 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
300 | 230KV-TTPS-KINNIMANGLAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 27-03-2026 | 05:50 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
301 | 220KV-TADIKONDA-GUNTUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 21-03-2026 | 16:02 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
302 | 220KV-GOOTY-RS-REGULAPADU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-03-2026 | 14:02 | APTRANSCO | Failure Operation | Line tripped at both ends on B-N, zone-1 protection and AR operated and tripped due to persistent fault at Ragulapadu end. AR not operated at Gooty RS end. | At Gooty Rs end, Voltage dip was observed in R-Phase along with B-Phase in Main-2 relay (REL 670). The relay sensed Ph-Ph fault. 3-Phase trip issued. At Gooty RS end, for 220kV Ragulapadu line, neutral wire of PT/CVT selected voltages in TTB of Main-1 relay was not in firm contact with TTB terminal. The same was rectified. | Completed | APTRANSCO | Correct Operation
303 | 230KV-SAVASPURAM-OTTAPIDARAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 27-03-2026 | 14:21 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | Idly charged from Savasapuram |  |  | TRANSIENT FAULT
304 | 220KV-NARSARAOPET-SATTENPALLY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 23-03-2026 | 02:08 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
305 | 230KV-MYVADI-O.K.MANDAPAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 28-03-2026 | 05:59 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | idly charged from Myvadi |  |  | TRANSIENT FAULT
306 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 23-03-2026 | 14:35 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
307 | 230KV-ARASUR_PG-GOBI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 28-03-2026 | 13:44 | PGCIL SR-2 | Correct Operation | AR Successful Both ends- Bph-G Fault- 16.14km /5.94 kA. |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT- AR Successful both Ends.
308 | 220KV-GADDAMVARIPALLI-GODDUMARRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 24-03-2026 | 03:45 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
309 | 220KV-BORAMPALLI-URAVAKONDA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 24-03-2026 | 14:19 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
310 | 230KV-MANDIPATTI-VELLALAVIDUTHI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 28-03-2026 | 14:11 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
311 | 220KV-CUDDAPAH-RENIGUNTA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 25-03-2026 | 12:47 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
312 | 230KV-Chekkanurani-RENGANATHAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 29-03-2026 | 03:29 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
313 | 220KV-CUDDAPAH-THIMAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 25-03-2026 | 16:57 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
314 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 25-03-2026 | 22:21 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
315 | 230KV-KARAIKUDI(TN)-KARAMBAYAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 29-03-2026 | 05:56 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
316 | 220KV-GARIVIDI-TEKKALI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 26-03-2026 | 04:19 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
317 | 230KV-UDUMALPET-ALIYAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 29-03-2026 | 12:49 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
318 | 220KV-GUDIVADA-AKIVEEDU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 26-03-2026 | 07:19 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
319 | 230KV-KAVANUR-MILAVITTAN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 30-03-2026 | 04:29 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
320 | 220KV-PIDUGURALLA-INAPARAJUPALLI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 27-03-2026 | 10:15 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
321 | 230KV-KARAIKUDI(TN)-KAVANUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 30-03-2026 | 11:34 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
322 | 220KV-RAYALSEEMA TPP-THIMAPRAM_LI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 27-03-2026 | 12:43 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation |  |  |  | Transient fault
323 | 220KV-RAYALSEEMA TPP-THIMAPRAM_LI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 27-03-2026 | 12:43 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation |  |  |  | Transient fault
324 | 230KV-MYVADI-O.K.MANDAPAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 31-03-2026 | 05:50 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
325 | 220KV-VTPS-PODILI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 28-03-2026 | 02:27 | APGENCO | Correct Operation | B-PH, Z-1 ,AR OPERATED AND SUCCESS, Fault Distance:112.1 KM, Current: 1.566 KA |  |  | APTRANSCO | Correct Operation
326 | 220KV-ATMAKUR-PODILI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 28-03-2026 | 10:13 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
327 | 220KV-BOMMUR-LOWER_SILERU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 28-03-2026 | 12:39 | APTRANSCO | Correct Operation |  |  |  | APGENCO | Correct Operation | At Lower sileru end as per the DR analysis the Earth fault start and Zone-1 time start observed in Main-1 relay(P442), meanwhile tripping happened in the Donkarayi and Bommuru end only. however the main-1 & main-2 relays tested and found normal. |  |  | The 220KV Lower Sileru-Bommuru feeder tripped at Bommuru end and Donkarayi end only. No relays operated at Lower sileru end. As per the DR analysis at Donkarayi end detect the VT fuse fail and operated the Non-directional Earth fault in Main-2(D60) relay.
328 | 220KV-GOOTY-SWS-ANANTHAPUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 29-03-2026 | 06:03 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
329 | 220KV-ATMAKUR-PODILI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 29-03-2026 | 13:23 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
330 | 400KV-VEMAGIRI_AP-KV_KOTA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 29-03-2026 | 13:25 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
331 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_AP-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 29-03-2026 | 13:27 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
332 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 29-03-2026 | 14:36 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
333 | 220KV-NARSARAOPET-SATTENPALLY-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 30-03-2026 | 05:07 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
334 | 220KV-BOMMUR-LOWER_SILERU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 30-03-2026 | 09:12 | APTRANSCO | Correct Operation |  |  |  | APGENCO | Unwanted Operation | LBB Start Relay Pickedup during DC supply changeover switching time | Maloperated LBB start relay (ABB make RXSF1 Relay) replaced by the OEN make Auxiliary Relay | Completed | LBB Re-Trip Operated for Bommuru feeder during DC Supply change over from DC Bank-2 to Dc Bank-1
335 | 220KV-JAMMALAMADUGU-BETAMCHERLA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 30-03-2026 | 14:17 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
336 | 220KV-PENDURTHI-UPPER_SILERU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 31-03-2026 | 12:37 | APTRANSCO | Correct Operation |  |  |  | APGENCO | Correct Operation | 3 Ph Trip |  |  | 3Ph Trip
337 | 220KV-CUDDAPAH-THIMAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 31-03-2026 | 13:42 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
338 | 220KV-KV_KOTA_OLD-NUZVID-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 31-03-2026 | 13:53 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
339 | 220KV-URAVAKONDA-IPPERU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 31-03-2026 | 15:46 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
340 | 220KV-URAVAKONDA-IPPERU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 31-03-2026 | 15:46 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
341 | 230KV-SHOLINGANALLUR-SIRUSERI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 07-03-2026 | 04:33 | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | replacing B- Phase Flashover insulator at Location No.53
342 | 230KV-KUNDAH3-KARAMADAI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 12-03-2026 | 13:06 | TNGECL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,TOR |  |  | Loc. No. 39 to 82 Tree cutting work done
343 | 230KV-ORAGADAM-SRIPERUMBADUR_TN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 18-03-2026 | 11:45 | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | Line patrol done & No visible fault
344 | 230KV-ARASUR-GOBI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 18-03-2026 | 19:15 | TANTRANSCO | Correct Operation | idly charged from Gobi |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | Line patrol done & No visible fault
345 | 230KV-SHOLINGANALLUR-SIRUSERI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-03-2026 | 01:54 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | "Insulator flash over at location 30
346 | 230KV-BASIN_BRIDGE-TONDIARPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-03-2026 | 02:26 | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TANTRANSCO | Correct Operation | idly charged from Basin Bridge |  |  | R phase Insulator decap
347 | 230KV-ETPS-TONDIARPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 05-03-2026 | 10:10 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR OFF |  |  | TRANSIENT FAULT
348 | 230KV-ETPS-TONDIARPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 05-03-2026 | 10:57 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR OFF |  |  | TRANSIENT FAULT
349 | 230KV-ETPS-MANALI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 06-03-2026 | 09:21 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR OFF |  |  | TRANSIENT FAULT
350 | 230KV-ETPS-TONDIARPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 06-03-2026 | 10:41 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,Y |  |  | Tree clearance done at various locations
351 | 230KV-MYVADI-O.K.MANDAPAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 10-03-2026 | 12:22 | TANTRANSCO | Correct Operation | Idly charged from Myvadi |  |  | TANTRANSCO | Correct Operation | DEF TRIP |  |  | TREE FAULT
352 | 230KV-KUNDAH3-KARAMADAI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 12-03-2026 | 12:14 | TNGECL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,TOR |  |  | TRANSIENT FAULT
353 | 230KV-ALAMATHY-MANALI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-03-2026 | 02:21 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR OFF_ COMPOSITE FEEDER |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR OFF_ COMPOSITE FEEDER |  |  | TRANSIENT FAULT
354 | 230KV-NCTPS-SRIPERUMBADUR_TN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-03-2026 | 02:26 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,Y |  |  | Rphase insulator disc flashover at Loc No 81
355 | 230KV-MANALI-CMRL_CENTRAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-03-2026 | 07:24 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR OFF_COMPOSITE FEEDER |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR OFF_COMPOSITE FEEDER |  |  | TRANSIENT FAULT
356 | 230KV-MANALI-CMRL_CENTRAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-03-2026 | 10:20 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR OFF_COMPOSITE FEEDER |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR OFF_COMPOSITE FEEDER |  |  | Location : 36 & 37, Kodungaiyur garpage dumping yard clearance was carried out
357 | 230KV-PUGALUR(TN)-PARATHIYUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 29-03-2026 | 12:24 | TANTRANSCO | Correct Operation | ZONE.3,R,N |  |  | TANTRANSCO | Correct Operation | DT RECEIVED_AR OFF SINCE RE |  |  | High Resistive Fault nearby Paruthiyur 230kV SS
358 | 230KV-VEERAPURAM-CUDDALORE-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 05-03-2026 | 13:52 | TANTRANSCO | Correct Operation | idly charged from Cuddalore |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,B,N |  |  | TRANSIENT FAULT
359 | 230KV-MILAVITTAN-OTTAPIDARAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 05-03-2026 | 15:59 | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | TANTRANSCO | Correct Operation | holding |  |  | Loc no-29 R PH Jumper cut & earthed towards Milavitan end. The same was attended
360 | 230KV-KADAMPARAI-MYVADI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 10-03-2026 | 13:42 | TNGECL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,Y |  |  | replacing defective insulators in R-Ph at Loc.50
361 | 230KV-METTURAUTO-HOSUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 11-03-2026 | 19:59 | TANTRANSCO | Correct Operation | ZONE.3,Y,B |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | Fire observed in the Godown 8 Kms from the Hosur end. Z3 tripping is correct while analyzing the fault DR.
362 | 230KV-THUVAKUDI-VELLALAVIDUTHI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-03-2026 | 13:08 | TANTRANSCO | Correct Operation | ZONE.1,R,Y |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,Y |  |  | TRANSIENT FAULT
363 | 230KV-SAMAYAPURAM-TRICHY(TN)-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 26-03-2026 | 12:59 | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | TRANSIENT FAULT
364 | 230KV-KADAPERI-SRIPERUMBADUR_TN-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 01-03-2026 | 05:18 | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | attending Insulator Flash Over at Tower Location No:43
365 | 230KV-KAYATHAR(TN)-VEERANAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 01-03-2026 | 13:49 | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TRANSIENT FAULT
366 | 230KV-O.K.MANDAPAM-ANAIKADAVU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-03-2026 | 14:24 | TANTRANSCO | Correct Operation | CAT,B,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TRANSIENT FAULT
367 | 230KV-O.K.MANDAPAM-ANAIKADAVU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-03-2026 | 17:03 | TANTRANSCO | Correct Operation | CAT,B,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | tree clearance between Loc.116 & 117
368 | 230KV-PERAMBALUR-JAMBUNATHAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 05-03-2026 | 21:39 | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL
369 | 230KV-KARAIKUDI(TN)-KAVANUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 06-03-2026 | 14:58 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
370 | 230KV-AMUDHAPURAM-NALLAMANAICKENPATTI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 24-03-2026 | 23:13 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
371 | 230KV-O.K.MANDAPAM-ANAIKADAVU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-03-2026 | 14:40 | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TRANSIENT FAULT
372 | 230KV-KARAIKUDI(TN)-KAVANUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 06-03-2026 | 12:34 | TANTRANSCO | Correct Operation | ZONE.1,R,N AR Lockout due to subsequent fault in Y phase |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N, AR Lockout due to subsequent fault in Y phase |  |  | TRANSIENT FAULT
373 | 230KV-UDUMALPET-ALIYAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 07-03-2026 | 00:24 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TRANSIENT FAULT
374 | 230KV-SINGARPET-GURUBARAPALLI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 12-03-2026 | 17:12 | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TRANSIENT FAULT
375 | 230KV-KARAIKUDI(TN)-KARAMBAYAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-03-2026 | 04:41 | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | Loc No:246 R Phase line decap attended
376 | 230KV-KARAIKUDI(TN)-KARAMBAYAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 25-03-2026 | 10:30 | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | LOC.No. 4 TO 5 EARTH WIRE CUT & RECTIFIED
377 | 230KV-UDUMALPET-ALIYAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 29-03-2026 | 13:16 | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | tree clearance between Loc 103& 104
378 | 230KV-O.K.MANDAPAM-ANAIKADAVU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 05-03-2026 | 05:56 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Failure Operation | CAT,Y,N,LOCKOUT | Coupler has to be replaced . Now AR selection is switched to Main.2 relay | Completed | At Anikadavu end, AR is in Main-1. Zone - 2 started in Main-1, but due to non receipt of carrier signal from Main-1 of Othakkalmandapam, CAT not operated in Main-1 of Anikadavu. Main-2 at Anikadavu tripped on CAT (3 pole trip). Feeder tied at Anikadavu at 06.14 Hrs
379 | 230KV-ACHARAPAKAM-VILLUPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 05-03-2026 | 06:14 | TANTRANSCO | Correct Operation | idly charged from Villupuram |  |  | TANTRANSCO | Failure Operation | ZONE.1,Y,N,AR LOCKOUT due to carrier fail | carrier channel has to be checked | Pending | TRANSIENT FAULT
380 | 230KV-ALAGAR_KOVIL-VALATHUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 06-03-2026 | 03:57 | TANTRANSCO | Failure Operation | ZONE.1,R,N,LOCKOUT_ due to carrier fail | OLTE defect at Alagarkoil end has to be attended | Pending | TANTRANSCO | Failure Operation | ZONE.1,R,N,LOCKOUT_ due to carrier fail | OLTE defect at Alagarkoil end has to be attended | Pending | OLTE defect at Alagarkoil end
381 | 220KV-CHITTOOR-KALIKIRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 06-03-2026 | 13:10 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation |  |  |  | B-N fault
382 | 220KV-ONGOLE-KANDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 07-03-2026 | 03:07 | APTRANSCO | Failure Operation | AR Successful, line was holding from Kandukuru end. At Ongole end, AR close pulse given by the relay, but CB not closed, PDR operated. R-phase limb close latch struck up in mechanism box. | R-phase limb (SIEMENS make)close latch struck up in mechanism box, the same was rectified | Completed | APTRANSCO | Correct Operation
383 | 220KV-CUDDAPAH-THIMAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 07-03-2026 | 14:23 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation |  |  |  | R-N fault
384 | 230KV-ALAGAR_KOVIL-VALATHUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 07-03-2026 | 06:01 | TANTRANSCO | Failure Operation | ZONE.1,B,N, LOCKOUT | OLTE defect has to be attended at Alagarkoil end | Pending | TANTRANSCO | Failure Operation | ZONE.1,B,N, LOCKOUT | OLTE defect has to be attended at Alagarkoil end | Pending | OLTE DEFECT AT ALAGARKOIL END
385 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 11-03-2026 | 02:56 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
386 | 220KV-CHITTOOR-KALIKIRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 11-03-2026 | 15:21 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
387 | 230KV-ALAGAR_KOVIL-SAMAYANALLUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-03-2026 | 07:47 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Failure Operation | ZONE.1,R,N,LOCKOUT | Carrier digital counter defect at Alagarkoil end | Pending | TRANSIENT FAULT
388 | 230KV-ALAGAR_KOVIL-SAMAYANALLUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-03-2026 | 09:14 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Failure Operation | ZONE.1,R,N,Lockout | Carrier digital counter defect at Alagarkoil end | Pending | TRANSIENT FAULT
389 | 230KV-ALAGAR_KOVIL-SAMAYANALLUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 19-03-2026 | 10:25 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Failure Operation | ZONE.1,R,N,LOCKOUT | Carrier digital counter defect at Alagarkoil end | Pending | TRANSIENT FAULT
390 | 230KV-BASIN_BRIDGE-MYLAPORE_GIS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-03-2026 | 23:47 | TANTRANSCO | Correct Operation | ZONE.1,B,N,LOCKOUT_Composite feeder |  |  | TANTRANSCO | Correct Operation | idly charged from Basin Bridge |  |  | Cable fault at Maddox road
391 | 230KV-THARAMANI-SHOLINGANALLUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 14-03-2026 | 10:19 | TANTRANSCO | Correct Operation | ZONE.1,B,N,LOCKOUT_AR OFF _ Composite feeder |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,LOCKOUT_AR OFF _ Composite feeder |  |  | TRANSIENT FAULT
392 | 230KV-THINGALUR-ERODE_GIS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 26-03-2026 | 06:41 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR OFF_Composite feeder |  |  | TANTRANSCO | Correct Operation | CAT,R,N,AR OFF_Composite feeder
393 | 230KV-MANALI-CMRL_CENTRAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 18-03-2026 | 15:50 | TANTRANSCO | Correct Operation | ZONE.1,B,N,LOCKOUT_AR OFF_CABLE FEEDER |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,LOCKOUT_AR OFF_CABLE FEEDER |  |  | TRANSIENT FAULT
394 | 230KV-MYLAPORE-TNEB_HQ-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 25-03-2026 | 12:14 | TANTRANSCO | Correct Operation | LDP_Y _AR OFF_ Cable feeder |  |  | TANTRANSCO | Correct Operation | LDP_Y _AR OFF_ Cable feeder |  |  | Y Phase Cable Fault located at opposite to VIP gate of TNEB building
395 | 230KV-MANALI-CMRL_CENTRAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 30-03-2026 | 15:40 | TANTRANSCO | Correct Operation | ZONE.1,B,N,LOCKOUT_AR OFF_ CABLE FEEDER |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,LOCKOUT_AR OFF_ CABLE FEEDER |  |  | TRANSIENT FAULT
396 | 230KV-TIRUVALAM_TN-SINGARPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 01-03-2026 | 12:56 | TANTRANSCO | Correct Operation | Idly charged from Singarapet |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
397 | 220KV-BHEEMGAL-RAMPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 03-03-2026 | 13:08 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | PHASE TO PHASE FAULT
398 | 220KV-ASUPAKA -VK_RAMAVARAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 05-03-2026 | 15:40 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
399 | 220KV-JULURUPADU-KALLUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 06-03-2026 | 06:55 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
400 | 220KV-KHAMMAM_TS-WADDEKOTHAPALLE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 06-03-2026 | 01:21 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | PHASE TO PHASE FAULT
401 | 220KV-SHAPURNAGAR-JANAGAON-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 07-03-2026 | 11:41 | TGTRANSCO | Correct Operation | COMPOSITE LINE |  |  | TGTRANSCO | Correct Operation | COMPOSITE LINE |  |  | PHASE TO PHASE FAULT
402 | 230KV-HOSUR_PG-TIRUPATTUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 18-03-2026 | 18:03 | PGCIL SR-2 | Correct Operation | AR Successful both ends, Rph-G Fault - 22.8 km/ 6.06 kA. |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT- Rph- G AR Successful.
403 | 230KV-ARASUR-GOBI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 18-03-2026 | 18:54 | TANTRANSCO | Correct Operation | Idly charged from Gobi |  |  | TANTRANSCO | Correct Operation | DEF TRIP |  |  | TRANSIENT FAULT
404 | 220KV-SHAPURNAGAR-JANAGAON-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 07-03-2026 | 13:49 | TGTRANSCO | Correct Operation | COMPOSITE LINE |  |  | TGTRANSCO | Correct Operation | COMPOSITE LINE |  |  | Line to ground fault
405 | 230KV-KUDANKULAM-TTPS | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 17-03-2026 | 15:15 | NPCIL_KKNP | Correct Operation | Nil |  |  | TNPGCL | Correct Operation | Nil |  |  | Trip
406 | 230KV-KAYATHAR(TN)-TTPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 31-03-2026 | 13:00 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TNPGCL | Correct Operation | AR success at TTPS end |  |  | TRANSIENT FAULT, B Ph , Z1
407 | 220KV-GACHIBOWLI-RAYADURG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 08-03-2026 | 04:57 | TGTRANSCO | Correct Operation | COMPOSITE LINE |  |  | TGTRANSCO | Correct Operation | COMPOSITE LINE |  |  | Line to ground fault
408 | 220KV-CHNDRAYANGUTTA-MAMIDAPALLI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 08-03-2026 | 12:06 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | PHASE TO PHASE FAULT
409 | 220KV-GAJWEL-KAMAREDDY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 08-03-2026 | 13:44 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
410 | 220KV-GAJWEL-KAMAREDDY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 10-03-2026 | 12:23 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
411 | 220KV-JULURUPADU-PEDAGOPATHI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 10-03-2026 | 19:20 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
412 | 220KV-JULURUPADU-PEDAGOPATHI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 10-03-2026 | 19:20 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
413 | 220KV-SIRICILLA-RAMADUGU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 01-03-2026 | 06:08 | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | Line to ground fault
414 | 220KV-MANDAMARRI-MURMUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 03-03-2026 | 12:15 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | PHASE TO PHASE FAULT
415 | 220KV-JULURUPADU-PEDAGOPATHI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 10-03-2026 | 20:13 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
416 | 220KV-JULURUPADU-PEDAGOPATHI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 10-03-2026 | 21:10 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
417 | 220KV-BOOTHPUR-MEHBOOBNAGAR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 10-03-2026 | 22:43 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
418 | 220KV-KOTHAGUDEM_TPS-WADDEKOTHAPALLE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 13-03-2026 | 23:40 | TGGENCO |  |  |  |  | TGTRANSCO | Correct Operation | A/R kept OFF due to oher end not implemented |  |  | Line to ground fault
419 | 220KV-WARANGAL_TG-MAHABUBABAD-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 18-03-2026 | 22:24 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
420 | 220KV-PARGI-KOSIGI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 19-03-2026 | 05:56 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
421 | 220KV-JAGITIYAL-VEMNOOR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 20-03-2026 | 12:46 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | PHASE TO PHASE FAULT
422 | 220KV-SHAPURNAGAR-GACHIBOWLI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 24-03-2026 | 18:24 | TGTRANSCO | Correct Operation | COMPOSITE LINE |  |  | TGTRANSCO | Correct Operation | COMPOSITE LINE
423 | 220KV-MALKARAM-CHOUTUPPAL-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 27-03-2026 | 14:09 | TGTRANSCO | Correct Operation | A/R operated and tripped again due to persistent fault. |  |  | TGTRANSCO | Correct Operation | A/R operated and tripped again due to persistent fault. |  |  | Line to ground fault
424 | 230KV-KAYATHAR(TN)-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 17-03-2026 | 15:15 | TANTRANSCO | Correct Operation | ZONE,1Y,B |  |  | TNPGCL | Correct Operation | Nil |  |  | Trip
425 | 220KV-MALKARAM-CHOUTUPPAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 27-03-2026 | 14:13 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
426 | 220KV-JULURUPADU-KALLUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 28-03-2026 | 03:41 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
427 | 220KV-MALYALAPALLI-MEDARAM_TG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 28-03-2026 | 11:58 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | PHASE TO PHASE FAULT
428 | 220KV-NIRMAL-UTNOOR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 30-03-2026 | 23:46 | TGTRANSCO | Correct Operation | A/R operated and tripped again due to persistent fault. |  |  | TGTRANSCO | Correct Operation | A/R operated and tripped again due to persistent fault. |  |  | Line to ground fault
429 | 220KV-MALYALAPALLI-JAGITIYAL-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 31-03-2026 | 01:09 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
430 | 220KV-MALYALAPALLI-JAGITIYAL-3 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 31-03-2026 | 01:16 | TGTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Line to ground fault
431 | 400KV-NAGAPATTNAM_PS-NEYVELI_TS_II-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 31-03-2026 | 12:07 | PGCIL SR-2 | Correct Operation | AR Successful both ends Bph-G Fault- 7.28 km / 10.47 kA. |  |  | NLC |  |  |  |  | AR Successful both ends Bph-G Fault-
432 | 400KV-NARENDRA-GUTTUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 18-03-2026 | 22:39 | PGCIL SR-2 | Correct Operation | AR Successful both ends - Yph-G Fault- 58.9 km / 2,4 kA. |  |  | KPTCL |  |  |  |  | AR Successful both ends - Yph-G Fault- 58.9 km / 2,4 kA.
433 | 400KV-MADURAI_PG-TIRUNELVELI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 18-03-2026 | 16:46 | PGCIL SR-2 | Correct Operation | AR Successful- both ends- Rph-G Fault in Line.- 121.4 km / 2.79 kA. |  |  | PGCIL SR-2 | Correct Operation | AR Successful- both ends- Rph-G Fault in Line.- 37.3 km / 8.16 kA. |  |  | AR Successful- both ends- Rph-G Fault in Line.
434 | 400KV-TIRUNELVELI-UDUMALPET_PG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 17-03-2026 | 17:41 | PGCIL SR-2 | Correct Operation | AR Successful- both ends- Rph-G Fault in Line.- 65.1 km / 4.8 kA. |  |  | PGCIL SR-2 | Correct Operation | AR Successful- both ends- Rph-G Fault in Line.-210 km / 2.06 kA. |  |  | AR Successful- both ends- Rph-G Fault in Line.
435 | 400KV-PUGALUR HVDC-ARASUR_PG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 16-03-2026 | 18:24 | PGCIL SR-2 | Correct Operation | AR Successful- both ends- Bph-G Fault in Line.- 49.5 km / 7.39 kA. |  |  | PGCIL SR-2 | Correct Operation | AR Successful- both ends- Bph-G Fault in Line.- 11.89 km / 11.32 kA. |  |  | AR Successful Bph-G Fault.
436 | 400KV-SALEM-NNTPP-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 15-03-2026 | 12:41 | PGCIL SR-2 | Correct Operation | AR Successful both ends - Yph-G - 32.37 km / 6.35 kA |  |  | NLC |  |  |  |  | AR Successful both ends - Yph-G - 32.37 km / 6.35 kA