## Slide 1
ADDITIONAL AGENDA FOR THE 142ND PCSC MEETING
Date: 06TH MAY 2026

## Slide 2
400KV JSW-BPS GIS BREAKERS INADVERTENT TRIPPINGS

## Slide 3
220KV
lines
JSW 220KV Network
ICT-1 315MVA
JSW 400 KV Network
JSW ENERGY LTD SWITCHYARD LAYOUT
220kV BUS-1 (Non Islanding Bus)
220kV BUS-2 (Islanding Bus)
B/C
B/C
JSW 400kV BUS-2
2X 300MW GEN
130 MW
ICT-2 315MVA
JSW 400kV BUS-1
B/C: BUS COUPLER
BPS
400KV
lines
Pavgada Lines
YTPS LINES
L1
L2
L1
L2
BPS STATION
270 MW
Non Islanding
Network
2X 300MW GEN
220kV JSW LOADS
400kV JSW GIS LOADS
400kV JSW GIS LOADS
220kV CRITICAL JSW LOADS
400kV JSW AIS LOADS
X
X
X
X
X
X
X
X
400kV JSW AIS LOADS
X
X
X
X
X
X
X
X
X
X
X
X
X
X
400kV BUS
X
X
H N HOLE LINES
X
X
L1
L 2
JSW SUB STATION
X
2*50MVAR REACTOR

## Slide 4
GIS BREAKERS INADVERTENT OPERATIONS DURING REMOTE FAULT
During Z1 fault on remote lines, at JSW end 400KV GIS breakers open without command
Above is observed in all BPS connected lines and no common pattern is noted
Relay Binary inputs are also getting high in all GIS Bay IED’s
Remote end breakers of BPS –JSW breaker also tripped on DT
2022 – 5 EVENTS
2025 – 2 EVENTS
2026 – 5 EVENTS till date
Effected GIS breakers:
  BPS L3 and L4, TR18 and 19
At GIS only TR15 is stable and No tripping's are seen during any event
DI/DO signals actuations noted in New RE lines also – Which are not yet commissioned.
These incidents are associated for all Zone 1 event of BPS Station outgoing lines with Different distances
PROBLEM STATEMENT

## Slide 5
INTERNAL TEAM SOLUTIONS
EXTENTSIVE BRIANSTORMING DONE, FOLLOWING WERE IMPLEMENTED
  Inspection of wiring and trip logics review.
  Operation selection made to SCADA mode for monitoring command in case of trip event.
  Open command/trip circuit cables Insulation testing carried out from remote panels replacement
  Earth connectivity of GIS skids and C&R panel checked, Ensured double Earthing
  Trip coils pickup voltages and ensured operation as per specifications
  Circuit modifications carried out with flag indications
  Remote trip commands connected to Annunciators for monitoring
  Master trips and Other trip relays inspected for any leakage
DISCUSSED PROBLEM WITH KPTCL, CPRI AND ERDA FOR SUGGESTIONS TO MITIGATE ISSUE

## Slide 6
TROUBLE SHOOTING
Approached M/s PRDC in AUG 2022 for mitigation of problem, Following were suggested
Control power DC system leakage to be identified and eliminated
Control cables, trip relays healthiness to be checked
After analysis, M/s PRDC suggested to strengthen the earth system due to TGPR during mentioned SLG event, Suggested to investigate the Earthing system through Sub Matter expert i.e. M/s Manav
VTFO/TGPR were suspected
Actions taken:
All control cable healthiness checked. Cable shields and Gland were connected to ground additionally
Ensured no DC system leakages are present in the system
All DR’s were reviewed carefully
Engaged M/s Manav Energy for detailed GIS and TGPR study
Engaged M/s Manav Energy for detailed study of GPR issue with total cost of around 2.1 Cr

## Slide 7
TYPICAL DR DURING EVENTS

## Slide 8
Mitigations IMPLEMENTED – PHASE 1
Boundary Earthing with special compound
Interconnection of transformer
neutral with Earth grid
New chemical earth pits
Separate Earthing of cable shields
Earth pit and raiser connections were tested
Earth integrity tests like Tagg slope were carried out
Copper Earthing provided for GIB’s from Earth point to Raiser.
Installation of New earth pits with Curec+ For GIS/C&R panels
AIS, Gantries and GIS Earthing interconnection
Boundary Earthing around complete switchyard
Interconnection of Neutrals and earth grid with Curec+
Refurbishment of earth pits -15 Nos
NO TRIPPINGS FROM OCT 2022 to MAR 2025

## Slide 9
Mitigations IMPLEMENTED – PHASE 2 After 11 APR 2025
Additional peripheral Earthing for GIS
3*3 mtr Earth mat for Line area
Installation of New deep bore earth pits
Additional dual Earthing for GIS bay skids
Separate earth 3*3 earth mat provided at Lines area
Additional 18 Deep bore earth pits with depth of 9 meters
Extension of double Earthing from each GIS skid to deep bore earth grid
Earthing audit carried out
All implementations were validated by M/s Manav – To identify gaps
TWO EVENTS in 2025 and No such events till APR 2026
Validation by M/s Manav

## Slide 10
Mitigations IMPLEMENTED – PHASE 3 After 11 APR 2026
  Capacitive earth pits (Plate earth) are provided to GIS body and LA Earthing in parallel with current Earthing
  All trip circuit related cables for Line bay will be replaced with New shielded cables – Laying is completed and connections will be done during line outage
  Providing interconnection between switchyard gantry and first transmission tower with 40 mm MS rod
  Installation of Low pass filters in consultation with OEM – M/s GE provided with data and awaiting response
  DC earth fault alarms were hooked to high speed logging at DCS.

## Slide 11
WAY FORWARD
EFFORTS UNDER WAY
  M/s Manav technical team is visited for assessment and Technical director is reviewed implementations at site
  M/s Manav provided with all DR’s for detailed study at their lab
  Low pass filter modelling and implementation as per M/s GE - GIS OEM
  M/s PRDC recommendations are awaited – Already required data shared to concern
  Request mail sent to PCSC for study/visit – PSSG team
  M/s Hitachi also approached regarding events, reply is awaited
  Standing instructions to Sub station control room provided for quick restoration in case of such event
  LDC and SRLDC control room provided with details of implementations and requested quicker permission for normalization as interim measure

## Slide 12
THANK YOU