# Draft Report on grid event Complete Outage of 220kV Zenataris in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 13-04-2026 12:00

# Event Summary (घटना का सारांश):

# As per the reports submitted, the triggering incident was DC supply failure at 220kV Zenataris leading to the tripping of 220kV Hiriyur Zenataris line. Tripping of the only connected line led to complete outage of 220kV Zenataris.

- Time and Date of the Event (घटना का समय और दिनांक:  16-03-2026 14:40

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): KARNATAKA

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Karnataka State Demand (MW) | 17879 | 17847 |
| Karnataka State Generation (MW) | 10936 | 10778 |
| Grid Frequency (Hz) | 49.94 | 49.98 |
| SR Demand (MW) | 69145 | 69216 |
| SR Generation (MW) | 54371 | 54219 |

*Pre and post data of 1 minute before and after the event

| Elements under outage | - ZENATARIS_PSS - 220KV |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 0.0 MW | 0.0 MW |

- Duration of interruption (रुकावट की अवधि):  2 hours, 1 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - ZENATARIS_PSS - 220KV

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

As per the reports submitted, at Zenataris SS, Phase-2 commissioning internal testing is presently underway, and the DC supply was accidentally switched off due to human error, which led to the tripping of the circuit breaker of the 220 kV Hiriyur–Zenataris Line-1 at the Zenataris end only. The line was holding at the Hiriyur end. The tripping of the only connected line resulted in a complete outage of the 220 kV Hiriyur–Zenataris Line-1.

- DR Analysis:

220KV-HIRIYUR-ZENATARIS_PSS-1

|  | ZENATARIS_PSS - 220KV | HIRIYUR - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:16-03-2026 14:40:32.939 MAIN CB R OPEN, MAIN CB B OPEN MAIN CB Y OPEN CB OPEN AR PREP 3PH Ir (max): 0.00 kA Iy (max): 0.00 kA Ib (max): 0.00 kA Vr (max): 125.51 kV Vy (max): 125.49 kV Vb (max): 124.91 kV DR Trigger Time:16-03-2026 14:40:32.939 MAIN CB R OPEN, MAIN CB B OPEN MAIN CB Y OPEN CB OPEN AR PREP 3PH Ir (max): 0.00 kA Iy (max): 0.00 kA Ib (max): 0.00 kA Vr (max): 125.51 kV Vy (max): 125.49 kV Vb (max): 124.91 kV | Line was holding at Hiriyur end |

ZENATARIS_PSS - 220KV

|  | ZENATARIS_PSS - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:16-03-2026 14:40:32.939 MAIN CB R OPEN, MAIN CB B OPEN MAIN CB Y OPEN CB OPEN AR PREP 3PH Ir (max): 0.00 kA Iy (max): 0.00 kA Ib (max): 0.00 kA Vr (max): 125.51 kV Vy (max): 125.49 kV Vb (max): 124.91 kV DR Trigger Time:16-03-2026 14:40:32.939 MAIN CB R OPEN, MAIN CB B OPEN MAIN CB Y OPEN CB OPEN AR PREP 3PH Ir (max): 0.00 kA Iy (max): 0.00 kA Ib (max): 0.00 kA Vr (max): 125.51 kV Vy (max): 125.49 kV Vb (max): 124.91 kV |

- A) PMU Analysis:

From the PMU, no fault is observed during the event

B) SCADA Analysis:

From the SCADA plot, no generation was observed at Zenataris prior to the event .

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| HIRIYUR_ZREPL | 1. SOP to be followed during testing activities. 2. Reason for hand tripping of both DC supply sources at Zenataris end. |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| HIRIYUR_ZREPL | DC distribution area to be prohibited |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

220KV-HIRIYUR-ZENATARIS_PSS-1 tripped at 16-03-2026 14:40 and restored at 16-03-2026 15:42

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | HIRIYUR_ZREPL |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | HIRIYUR_ZREPL |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) | HIRIYUR_ZREPL |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: