# Draft Report on grid event Complete outage of 220kV RSRPL_GadagPS of RENEW in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 27-04-2026 11:36

# Event Summary (घटना का सारांश):

# As per the reports submitted, the triggering incident was YB-G fault in 220kV Gadag RSRPL_Gadag_PS line at 205 line bay at RSRPL end. At RSRPL end, the fault was sensed in I>4 non directional over current protection and 3ph tripped. However the line tripped only at RSRPL end and the line was holding at Gadag end. Tripping of the only connected line led to complete outage of 220kV RSRPL_GadagPS.

- Time and Date of the Event (घटना का समय और दिनांक:  05-04-2026 08:55

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): KARNATAKA

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Karnataka State Demand (MW) | 14608 | 14642 |
| Karnataka State Generation (MW) | 7987 | 8261 |
| Grid Frequency (Hz) | 50.06 | 50.1 |
| SR Demand (MW) | 59454 | 59544 |
| SR Generation (MW) | 48568 | 48831 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

At RSRPL end:

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 10.0 MW | 0.0 MW |

- Duration of interruption (रुकावट की अवधि):  1 hours, 18 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 220KV-GADAG_PSS-RSRPL_GadagPS-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

220kV RSRPL_GadagPS was radially connected to Gadag through 220KV-GADAG_PSS-RSRPL_GadagPS-1. As per the reports submitted, the triggering incident was YB-G fault in 220kV Gadag RSRPL_Gadag_PS line at 205 line bay at RSRPL end (as per FIR) due to foreign object (monkey). At RSRPL end, the fault was sensed in I>4 non directional over current protection in only one Main (Main-1 as shown below) and DT was sent to Gadag end (as per DR).

However the DT was not received at Gadag end as the line tripped only at RSRPL end and the line was holding at Gadag end. At Gadag end, the fault was not sensed and the line was holding. Tripping of the only connected line to RSRPL_GadagPS led to complete outage of 220kV RSRPL_GadagPS.

- DR Analysis:

220KV-GADAG_PSS-RSRPL_GadagPS-1

|  | GADAG_PSS - 220KV | RSRPL_GadagPS - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | Line Holding | DR Trigger Time:05-04-2026 08:55:08.701 Any Trip, I>4 Trip, 86.1 TRIP AR Block CB_R-ph Open, CB_B-ph open, CB_Y-ph Open DT Send CH-1 Ir (max): 0.67 kA Iy (max): 3.85 kA Ib (max): 2.74 kA Vr (max): 138.67 kV Vy (max): 140.76 kV Vb (max): 131.53 kV |

RSRPL_GadagPS - 220KV

|  | RSRPL_GadagPS - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:05-04-2026 08:55:08.701 Any Trip, I>4 Trip, 86.1 TRIP AR Block CB_R-ph Open, CB_B-ph open CB_Y-ph Open DT Send CH-1 Ir (max): 0.67 kA Iy (max): 3.85 kA Ib (max): 2.74 kA Vr (max): 138.67 kV Vy (max): 140.76 kV Vb (max): 131.53 kV |

- A) PMU Analysis:

From the PMU, dip in Y and B-phases is observed indicating YB-G fault during the event with a delayed fault clearance of around 200ms.

B) SCADA Analysis:

From SCADA plot, tripping of 220kV Gadag RSRPL_Gadag_PS line can be observed with a generation loss of around 17MW at 220kV RSRPL_GadagPS.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| RENEW POWER PVT LTD | 1. Enabling of over current (I>4) at RSRPL_GadagPS needs review |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):  Nil

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

RSRPL_GadagPS - 220KV tripped at 05-04-2026 08:55 and restored at 20-04-2026 18:44

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | RENEW POWER PVT LTD |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | RENEW POWER PVT LTD, GTL |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) | RENEW POWER PVT LTD |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: