# Draft Report on grid event Complete Outage of 230 kV Arani and Echur of TANTRANSCO in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 15-04-2026 16:27

# Event Summary (घटना का सारांश):

# The triggering incident is the 110kV Y-ph bus PT failure at Arani (as per FIR) causing 110 kV Bus Fault. Without 110kV BBP, the Bus fault was sensed and the lines tripped on Z3 protection operation at remote ends other than 230KV-ARNI-ECHUR-1. 230KV-MAPS-ECHUR-1 line tripped on DEF protection leading to the Complete Outage of 230 kV Arani and Echur of TANTRANSCO

- Time and Date of the Event (घटना का समय और दिनांक:  05-04-2026 23:39

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): TAMILNADU

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| TamilNadu State Demand (MW) | 15849 | 15660 |
| TamilNadu State Generation (MW) | 6430 | 6425 |
| Grid Frequency (Hz) | 49.92 | 49.97 |
| SR Demand (MW) | 52763 | 52574 |
| SR Generation (MW) | 45878 | 45802 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

Bus Configuration at Echur end :

Bus Configuration at Arani end :

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 0.0 MW | 231.0 MW |

- Duration of interruption (रुकावट की अवधि):  0 hours, 40 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण):

| Equipment Type | Equipment make |
| --- | --- |
| PT | Details not provided |

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 230KV-ARNI-BHAVANI-1

      - 230KV-ARNI-BHAVANI-2

      - 230KV-ARNI-KANCHIPURAM-2

      - 230KV-ARNI-SINGARPET

      - 230KV-MAPS-ECHUR-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

230kV Echur is connected to 230kV Arani and MAPS. 230kV Arani is connected to Singarpet, Kanchipuram and Bhavini as shown below.

The triggering incident is the 110kV Y-ph bus PT failure at Arani (as per FIR) causing 110 kV Bus Fault. As the BBP protection is not available at 110kV level, the fault was not isolated instantaneously. It can be observed that initially the fault was sensed in R-ph and further developed into R-Y ph fault after around 350ms.

The R-ph fault can be observed from 23:39:35.280 Hrs, and further developed into R-Y fault at around 23:39:35.640. The fault was not isolated by the high set protection of the 230/110kV PTRs and was fed through the connected lines. At remote ends (Kanchipuram, Singarpet) end the fault was sensed in Z3. At Kanchipuram end the fault started sensing the fault in Z3 from the fault instance and tripped after around 850ms at 23:39:26.160 Hrs. At Singarpet end the fault was sensed in Z3 after the fault was developed into R-Y ph fault and tripped after around 850ms in Z3.

Further 230kV Bhavini-Arani-1 line tripped on Z3 protection operation at 23:39:26.330 Hrs and further 230kV Bhavini-Arani-2 line tripped at 23:39:26.420 Hrs in Z3 protection operation after almost 1 sec from the fault initiation.

After which, the only connection to Arani is through 230kV Arani-Echur-MAPS, where in 230kV MAPS-Echur line got tripped at 23:39:26.600 on DEF protection operation which was set for 100mA Time delay- 1.2 sec CTR-600/1A isolating the fault and this led to the complete outage of Complete Outage of 230 kV Arani and Echur of TANTRANSCO. The complete tripping sequence is as below

- DR Analysis:

ECHUR - 230KV

|  | ECHUR - 230KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | No DR uploaded |

ARNI - 230KV

|  | ARNI - 230KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | No DR uploaded |

230KV-ARNI-BHAVANI-1

|  | ARNI - 230KV | BHAVANI - 230KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | No DR uploaded. Line Holding | DR Trigger Time:05-04-2026 23:39:25.350 DIST : Starting Z< A, MAIN : General starting, MAIN : Starting A, MAIN : Starting GF, DIST : Zero-sequ. starting, DIST : General starting, DIST : Start. switch. to PG, FT_RC: Record. trig. active, FT_RC: System disturb. runn, FT_RC: Record. in progress, DIST : Starting Z< DIST : Zone 1.ze starting, DIST : Zone 1 starting, DIST : Zone 2 starting, DIST : Zone 3 starting, DIST : Zone 4 starting, DIST : Zone 5 starting, DIST : Zone 6 starting, DIST : Zone 7 starting, DIST : Zone 8 starting DIST : tVmemory running, DIST : Fault forwd. / LS. A, DIST : Fault forward / LS, DIST : Dir.using Vmeas Sys1, DIST : t1 elapsed DTOC : Starting IN> GFSC : IN> triggered PSB : IN> triggered DIST : t2 elapsed DIST : Starting Z< B, MAIN : Starting B DIST : Fault forwd. / LS. B, DIST : Dir.using Vmeas Sys2, DIST : Dir.using Vmeas Sys3 DIST : t3 elapsed DIST : Starting I>> A V<> : Starting V<, V<> : Starting V</<< A(-B), V<> : Starting V<< DIST : Starting I>> B DIST : Trip signal zone 3, DIST : Trip sig. zone 2-8, DIST : Trip signal MAIN : Send transfer trip A, MAIN : Send transfer trip B, MAIN : Send transfer trip C, MAIN : Trip signal 1. 3p, MAIN : Gen. trip command 1, MAIN : Gen. trip signal 1, MAIN : Trip signal 1. A, MAIN : Trip signal 1. B, MAIN : Trip signal 1. C, MAIN : Gen. trip command, MAIN : Trip command 1. A, MAIN : Trip command 1. B, MAIN : Trip command 1. C, LOGIC: Output 4, LOGIC: Output 7, LOGIC: Output 11, LOGIC: Output 12, LOGIC: Output 13 LOGIC: Output 1, LOGIC: Output 2, LOGIC: Output 6, LOGIC: Output 9 DIST : t4 elapsed V<> : Starting V</<< B(-C), V<> : Starting V</<< C(-A), V<> : Starting V< 3-pole, DTOC : Fault N forward V<> : Starting Vpos<, V<> : Starting Vpos<< DIST : Start. switch. to PG DIST : Zero-sequ. starting Ir (max): 0.88 kA Iy (max): 0.77 kA Ib (max): 0.30 kA Vr (max): 132.81 kV Vy (max): 133.26 kV Vb (max): 132.64 kV |

230KV-ARNI-KANCHIPURAM-2

|  | ARNI - 230KV | KANCHIPURAM - 230KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | No DR uploaded. Line Holding | DR Trigger Time:05-04-2026 23:39:24.967 T1 Any Start, T1, IN>1 Start IN>1 Timer Block Z3 A/R Trip 3P, A/R Lockout Any Trip, DIST Trip A, DIST Trip B, DIST Trip C, AR Lockout Shot> BLK AR(3PH.TRIP) CB Aux A, CB Aux B, CB Aux C, MCB-RPH OPEN, MCB-YPH OPEN, MCB-BPH OPEN Any Pole Dead, All Pole Dead Ir (max): 1.52 kA Iy (max): 1.34 kA Ib (max): 0.61 kA Vr (max): 134.58 kV Vy (max): 135.53 kV Vb (max): 135.79 kV |

230KV-ARNI-BHAVANI-2

|  | ARNI - 230KV | BHAVANI - 230KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | No DR uploaded. Line Holding | DR Trigger Time:05-04-2026 23:39:26.397 L6 A/R L/O L10 C PH A/R INI Any Trip C Any Trip B, R16 A/R L/O ANN, L9 B PH A/R INIT Any Trip A, L8 A PH A/R INIT L1 R PH OPEN, L2 Y PH OPEN, L3 B PH OPEN Ir (max): 1.09 kA Iy (max): 1.00 kA Ib (max): 0.41 kA Vr (max): 110.68 kV Vy (max): 115.40 kV Vb (max): 128.05 kV |

230KV-ARNI-SINGARPET

|  | ARNI - 230KV | SINGARPET - 230KV |
| --- | --- | --- |
| Time Sync Issue | No | Yes |
| DR Analysis | No DR uploaded. Line Holding | DR Trigger Time:05-04-2026 23:39:20.147 Any Start DIST Fwd DIST Fwd Z3 AR INITIA B PH AR INITIA R PH, AR INITIA Y PH AR BLOCK Any Trip Any Pole Dead, All Pole Dead Ir (max): 1.70 kA Iy (max): 1.48 kA Ib (max): 0.67 kA Vr (max): 132.26 kV Vy (max): 132.98 kV Vb (max): 131.92 kV |

230KV-ARNI-ECHUR-1

|  | ARNI - 230KV | ECHUR - 230KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | No DR uploaded. Line Holding | No DR uploaded. Line Holding |

230KV-MAPS-ECHUR-1

|  | MAPS - 230KV | ECHUR - 230KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:05-04-2026 23:39:26.553 Any Trip Ir (max): 1.67 kA Iy (max): 1.48 kA Ib (max): 1.04 kA Vr (max): 120.34 kV Vy (max): 131.08 kV Vb (max): 128.52 kV | No DR uploaded. Line Holding |

- A) PMU Analysis:

From the PMU plot initial R-ph fault can be observed and further developed into R-Y fault with delayed fault clearance of around 1.2s

B) SCADA Analysis:

From SCADA data, multiple tripping of the lines can be observed

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| TANTRANSCO | 1. Non operation of ICT highset protection needs review 2. Single bus operation at 230kV ARNI (Single main and transfer) and ECHUR needs review 3. Non operation of Z3 for 230KV-ARNI-ECHUR-1 at ECHUR end needs review |
| NPCIL_MAPS | 1. Enabling of DEF DT needs review |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| TANTRANSCO | 1. Zone-3 setting revision to be reviewed at remote ends. |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

230kV Arani- Kancheepuram: 06-04-2026 at 00:19hrs

230kV Arani- Singarapet: 06-04-2026 at 00:27hrs

230kV Arani- Echur : 06-04-2026 at 00:40 hrs

230kV Arani- Bhavini1 : 06-04-2026 at 01:33hrs

230kV Arani- Bhavini.2: 06-04-2026 at 01:45hrs

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | TANTRANSCO |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | BHAVINI |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 | TANTRANSCO |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: