# Draft Report on grid event Complete Outage of 220kVTadipathri in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 22-04-2026 18:08

# Event Summary (घटना का सारांश):

# During antecedent conditions, 220kV Tadipathri Boareddypalli line was under LC. 220kV Tadipathri SS was being fed through 132kV network through 132kV Tadipathri Kondapuram and 132kV Gooty RS-Gudipadu-Ankireddypalli-Komali- Tadipatri feeders. As per the reports submitted, at 14:56hrs, 132kV Tadipathri Ankireddypalli line tripped on R-G fault. Subsequently, 132kV Ankireddypalli Gudipadu feeder tripped on non directional over current protection at Ankireddypalli end. Tripping of both sources led to complete otuage of 220kV Tadipathri SS.

- Time and Date of the Event (घटना का समय और दिनांक:  10-04-2026 14:56

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): ANDHRA PRADESH

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Andhra Pradesh State Demand (MW) | 13504 | 13466 |
| Andhra Pradesh State Generation (MW) | 7695 | 7710 |
| Grid Frequency (Hz) | 49.98 | 49.95 |
| SR Demand (MW) | 73991 | 74132 |
| SR Generation (MW) | 54978 | 55037 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 27.0 MW | 97.0 MW |

- Duration of interruption (रुकावट की अवधि):  0 hours, 14 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

During antecedent conditions, 220kV Tadipathri Boareddypalli line was under LC. 220kV Tadipathri SS, 132kV Komatikuntla,132kV RTSS Komali, 132kV Ankireddypalli SS and 132kV Penna cements  were being fed through 132kV network through 132kV Tadipathri Kondapuram and 132kV Gooty RS-Gudipadu-Ankireddypalli-Komali- Tadipatri feeders. As per the reports submitted, at 14:56hrs, the triggering incident was Y-G fault in 132kV Tadipathri Kondapuram line . At Tadipathri end, this fault was sensed as Y-G fault in zone-1. At Kondapuram end, this fault was sensed as R-G fault in zone-1 and the line tripped. Subsequently, the 132 kV Ankireddypalli–Gudipadu feeder tripped on non-directional overcurrent protection, which had been inadvertently enabled at the Ankireddypalli end. However, the same could not be verified due to non availability of DR. Tripping of both sources led to complete outage of 220kV Tadipathri SS, 132kV Komatikuntla,132kV RTSS Komali, 132kV Ankireddypalli SS and 132kV Penna cements.

- DR Analysis:

TADIPATHRI - 220KV

|  | TADIPATHRI - 220KV |
| --- | --- |
| Time Sync Issue | Yes |
| DR Analysis | 132kV Tadipatri Kondapuram at Tadipatri end: DR Trigger Time:10-04-0026 14:21:02.226 FIDEN, 50GF, 32QGE, 32QE FSA, 32QF, 32GF, F32Q, F32QG *, 50ABC, X5ABC, X6ABC Z4G, XAG4 Z2G, Z3G, XAG2, XAG3 TRP, A, G, ZONE1, Z1G, Z1GT, Z1T, TRIP, OUT107, OUT104, OUT103, OUT102, OUT101, XAG1 Ir (max): 3.26 kA Iy (max): 0.37 kA Ib (max): 0.49 kA 132kV Tadipatri Kondapuram at Kondapuram end: DR Trigger Time:10-04-2026 14:35:16.778 50GF, 50GR FIDEN, 32QGE, 32QE 32QF, 32GF, F32Q, F32QG FSB Z3G, Z4G, XBG3, XBG4 Z2G, XBG2 TRP, B, G, ZONE1, Z1G, Z1GT, Z1T, TRIP, OUT107, OUT104, OUT103, OUT102, OUT101, XBG1 |

- A) PMU Analysis:

From PMU, dip in Y-phase is observed indicating Y-G fault during the event.

B) SCADA Analysis:

From SCADA, tripping of 220kV Tadipathri Bus-1 can be observed.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| APTRANSCO | 1. Tripping of 132kV Ankireddypalli Gudipadu on over current protection. 2. Non furnishing of DR of 132kV Ankireddypalli Gudipadu line. 3. DR time sync issue in 132kV Tadipathri Kondapuram line. 4. Fault in 132kV Tadipathri Kondapuram line is seen as R-G fault at Kodapuram end and Y-G fault at Tadipathri end. |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):  Nil

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

TADIPATHRI - 220KV tripped at 10-04-2026 14:56 and restored at 10-04-2026 15:10

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) |  |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | APTRANSCO |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 | APTRANSCO |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: