# Draft Report on grid event Complete Outage of 220kV Pallom SS and 220kV New Pallom SS of KSEB in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 25-04-2026 20:32

# Event Summary (घटना का सारांश):

# As per the reports submitted, the triggering incident was B-G bus fault on 220kV Bus-2 of 220kV New Pallom station within the bus protection zone of 220kV Pallom New Pallom line. However, 220kV Bus-2 BBP did not operate at 220kV New Pallom SS and the fault was continuously being fed through 220kV lines connected to 220kV Pallom SS and 220kV New Pallom SS . Eventually these 220kV lines tripped on zone-2 protection at the remote ends except 220kV Pallom New Pallom line which tripped on over current protection and subsequently after which due to the tripping of grid connected 110kV lines and this led to complete outage of 220kV Pallom SS and 220kV New Pallom SS

- Time and Date of the Event (घटना का समय और दिनांक:  14-04-2026 16:40

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): KERALA

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Kerala State Demand (MW) | 4780 | 4610 |
| Kerala State Generation (MW) | 871 | 901 |
| Grid Frequency (Hz) | 50.06 | 50.09 |
| SR Demand (MW) | 67854 | 67682 |
| SR Generation (MW) | 50564 | 50288 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

At 220kV Pallom SS:

At 220kV New Pallom SS:

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 0.0 MW | 275.0 MW |

- Duration of interruption (रुकावट की अवधि):  0 hours, 36 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 220KV-SABARIGIRI-PALLOM-1

      - 220KV-KOTTAYAM-PALLOM-1

      - 220KV-IDDUKI-NEW PALLOM-1

      - 220KV-KAYAMKULAM-NEW PALLOM-1

      - 220KV-PUNNAPRA-NEW PALLOM-1

      - 220KV-KAYAMKULAM-NEW PALLOM-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

As per the reports submitted, the triggering incident was B-G bus fault on 220kV Bus-2 of 220kV New Pallom station within the bus protection zone of 220kV Pallom New Pallom line due to flashover in the suspension insulator as shown in the SLD below.

During this instance, the main zone busbar protection for both Bus 1 and Bus 2 was sensed at the New Pallom end due to the isolator high status of the 220 kV Pallom–New Pallom line in Bus-1 as well, whereas the isolator status is supposed to be set high only for Bus-2. However, as busbar checkzone protection was not sensed due to logic issue which was as follows and hence BBP did not operate isolating the fault.

And hence the fault was being fed through 220kV lines connected to 220kV New Pallom SS, where in all lines tripped on remote end on zone-2 protection except 220kV Pallom New Pallom line as the line has pilot wire differential protection with no distance protection in Main-1 and only backup over current protection in Main-2. However, the Backup over current protection of Main-2 has picked up and tripped the line after around 720ms, but before the over current operation, multiple lines tripped at remote ends, and the sequence of tripping of 220kV lines connected to Pallom and New Pallom stations is as shown in the sequence below.

| Line Name | Trip Time | Tripped at | Indication |
| --- | --- | --- | --- |
| 1. 220 kV Sabarigiri-Pallom-1 | 14/04/2026 16:40:41:302 | Sabarigiri | Z2 |
| 2. 220 kV Idduki-New Pallom-1 | 14/04/2026 16:40:41:311 | Idduki | Z2 |
| 3. 220 kV Kottayam-Pallom-1 | 14/04/2026 16:40:41:344 | Kottayam | Z2 |
| 4. 220 kV Kayamkulam-New Pallom-1 | 14/04/2026 16:40:41:345 | Kayamkulam | Z2 |
| 5. 220 kV Punnapra-New Pallom-1 | 14/04/2026 16:40:41:433 | Punnapra | Z2 |
| 6. 220kV Pallom-New Pallom | 14/04/2026 16:40:41:631 | New Pallom | Over Current |

With the tripping of 220kV Pallom-New Pallom led to the complete outage of 220kV New Pallom SS station and clearing of the fault. 220kV Pallom was in service through 110kV connectivity. 220/110kV Pallom ICT-1 tripped during the event (as per SCADA SOE) and further 110kV grid connected lines tripped leading to the Complete outage of 220kV Pallom station.

And hence led to the Complete Outage of 220kV Pallom SS and 220kV New Pallom SS of KSEB

- DR Analysis:

PALLOM - 220KV

|  | PALLOM - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR not available at this end. |

NEW PALLOM - 220KV

|  | NEW PALLOM - 220KV |
| --- | --- |
| Time Sync Issue | Yes |
| DR Analysis |  |

220KV-PALLOM-NEW PALLOM-1

|  | PALLOM - 220KV | NEW PALLOM - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | Yes |
| DR Analysis | DR not available at this end. | DR Trigger Time:14-04-0026 16:40:40.946 50GF, 50GR, 51G2, DD, * 51G, 50QF, 50QR 51P, FSC 51C, 27B81 27C1 DD, * * 51PR 51CR, ICMET * 27A1, 27B1, 3P27, OUT103 3PO, * 51G2R 51GR Ir (max): 0.32 kA Iy (max): 0.73 kA Ib (max): 6.66 kA |

220KV-KOTTAYAM-PALLOM-1

|  | KOTTAYAM - 220KV | PALLOM - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:14-04-2026 16:40:41.305 GEN.TRIP, GEN.TRIP-C, Z2G-OPT, 86A opertaed, 86B operated, M1B Opertaed ARC1_FT, M1R Operated, M1Y Operated Z3S-ORX Ir (max): 0.68 kA Iy (max): 1.24 kA Ib (max): 4.82 kA Vr (max): 121.95 kV Vy (max): 120.58 kV Vb (max): 90.89 kV DR Trigger Time:14-04-2026 16:40:41.295 Zone 2 Trip, 86A TRIP RLY, 86B TRIP RLY, TRIP TO Yph, TRIP TO Bph, TRIP TO Rph A/R Lockout 86B OPTD GCB Q0 B OPEN GCB Q0 R OPEN, GCB Q0 Y OPEN Ir (max): 0.68 kA Iy (max): 1.24 kA Ib (max): 4.97 kA Vr (max): 128.03 kV Vy (max): 127.85 kV Vb (max): 126.91 kV | Line was holding |

220KV-SABARIGIRI-PALLOM-1

|  | SABARIGIRI - 220KV | PALLOM - 220KV |
| --- | --- | --- |
| Time Sync Issue | Yes | No |
| DR Analysis | DR Trigger Time:14-04-2026 16:40:40.913 Dis.Pickup L3, Dis.Pickup E, Dis. forward, Relay PICKUP, Relay PICKUP L3, Relay PICKUP E Dis. Pickup Z2, Dis. Pickup Z3 Dis.TripZ2/3p, Relay TRIP L1, Relay TRIP L2, Relay TRIP L3, Relay TRIP 1pole open L3 Ir (max): 0.32 kA Iy (max): 0.88 kA Ib (max): 2.32 kA Vr (max): 129.13 kV Vy (max): 128.32 kV Vb (max): 127.12 kV DR Trigger Time:14-04-2026 16:40:18.114 21 Pickup ØC, 21 Pickup G, Relay PICKUP, Relay PICKUP ØC, Relay PICKUP G 21 PU forward, 21 PU Z3 21 PU Z2 21 TRIP 3p. Z2, Relay TRIP ØA, Relay TRIP ØB, Relay TRIP ØC, Relay TRIP >52b 3p Open, >52b Bkr1 3p Op 1pole open ØC Ir (max): 0.32 kA Iy (max): 0.88 kA Ib (max): 2.32 kA Vr (max): 128.80 kV Vy (max): 128.33 kV Vb (max): 127.15 kV | Line was holding |

220KV-IDDUKI-NEW PALLOM-1

|  | IDDUKI - 220KV | NEW PALLOM - 220KV |
| --- | --- | --- |
| Time Sync Issue | Yes | No |
| DR Analysis | DR Trigger Time:14-04-2026 16:40:11.311 PHASE SELECT CG OSC TRIGGER ON (VO64) OSC TRIGGER ON (VO64), GND DIST Z2 OP L3 M CB B OPN ON (CI3) L1 M CB R OPN ON (CI1) L2 M CB Y OPN ON (CI2) PHASE SELECT BC PHASE SELECT BC Ir (max): 0.40 kA Iy (max): 0.63 kA Ib (max): 3.31 kA Vr (max): 128.27 kV Vy (max): 127.22 kV Vb (max): 126.81 kV DR Trigger Time:14-04-2026 16:40:40.937 Any Start DIST Start C DIST Fwd, Z2, Z3 Any Trip, DIST Trip C L4-86B OPTD L6-86A OPTD Ir (max): 0.41 kA Iy (max): 0.63 kA Ib (max): 3.34 kA Vr (max): 128.26 kV Vy (max): 127.71 kV Vb (max): 126.19 kV | Line was holding |

220KV-KAYAMKULAM-NEW PALLOM-1

|  | KAYAMKULAM - 220KV | NEW PALLOM - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:14-04-2026 16:40:40.940 T1 Any Start DIST Fwd Z3 T2 10_CB HEALTHY Ir (max): 0.09 kA Iy (max): 0.36 kA Ib (max): 2.14 kA Vr (max): 127.45 kV Vy (max): 127.87 kV Vb (max): 126.68 kV DR Trigger Time:14-04-2026 16:40:40.949 PHS-STFWL3, PHS-STFWPE ZM03-START ZM02-START TRIP_TRIP, TRIP L1, TRIP L2, TRIP L3, ZM02-TRIP CB OPEN R CB OPEN Y, CB OPEN B Ir (max): 0.09 kA Iy (max): 0.36 kA Ib (max): 2.13 kA Vr (max): 127.30 kV Vy (max): 127.79 kV Vb (max): 126.73 kV | Line was holding |

220KV-PUNNAPRA-NEW PALLOM-1

|  | PUNNAPRA - 220KV | NEW PALLOM - 220KV |
| --- | --- | --- |
| Time Sync Issue | Yes | No |
| DR Analysis | DR Trigger Time:14-04-2026 16:40:40.959 EF Pickup, Relay PICKUP, Relay PICKUP L3, Relay PICKUP E Dis.Pickup L3, Dis.Pickup E, Dis. forward, Dis. Pickup Z3 Dis. Pickup Z2, Relay TRIP L1, Relay TRIP L2, Relay TRIP L3, Relay TRIP 1pole open L3 Ir (max): 0.37 kA Iy (max): 1.01 kA Ib (max): 2.30 kA Vr (max): 126.08 kV Vy (max): 125.61 kV Vb (max): 125.05 kV DR Trigger Time:13-04-1996 16:40:40.959 EF Pickup, Relay PICKUP, Relay PICKUP L3, Relay PICKUP E Dis. forward, Dis. Pickup Z3 Dis. Pickup Z2, Dis.Gen. Trip, Dis.TripZ2/3p, Relay TRIP L1, Relay TRIP L2, Relay TRIP L3, Relay TRIP 1pole open L3 Ir (max): 0.37 kA Iy (max): 1.01 kA Ib (max): 2.30 kA Vr (max): 125.96 kV Vy (max): 125.70 kV Vb (max): 125.04 kV | Line was holding |

- A) PMU Analysis:

From the PMU plot , B-G fault can be observed in the Pallom-New Pallom line with delayed clearance of around 400ms.

B) SCADA Analysis:

From the SCADA data tripping of all 220kV lines connected to 220kV Pallom SS and New Pallom SS is observed.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| KSEB | 1. The Non-operation of checkzone busbar protection at 220kV New Pallom SS needs review 2. The high status of Bus-1 isolator of 220kV Pallom New Pallom line at New Pallom SS needs review. 3. The non availabilty of distance protection in Pallom-New Pallom line needs review. 4. Protection settings co-ordination of Backup over current protection of 220kV Pallom New Pallom and Zone-2 of 220kV lines connected to 220kV Pallom SS Needs review. |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| KSEB | 1. Logic has been corrected at New Pallom end for the checkzone busbar protection. |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

14/04/2026 17:16

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | KSEB |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | NTPC, KSEB |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 | KSEB |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: