# Draft Report on grid event Complete Outage of 220kV TP SAURYA of TATA POWER in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 28-03-2026 21:30

# Event Summary (घटना का सारांश):

# 220kV TP SAURYA is connected radially to KOPPAL through 220KV-TP SAURYA LIMITED-KOPPAL-1. The triggering incident is the B-G fault in the 220KV-TP SAURYA LIMITED-KOPPAL-1 line and tripping of the only line connected to 220kV TP SAURYA led to the Complete Outage of 220kV TP SAURYA of TATA POWER

- Time and Date of the Event (घटना का समय और दिनांक:  17-03-2026 19:35

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): KARNATAKA

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Karnataka State Demand (MW) | 10783 | 10745 |
| Karnataka State Generation (MW) | 6261 | 6263 |
| Grid Frequency (Hz) | 50.0 | 50.0 |
| SR Demand (MW) | 52977 | 52894 |
| SR Generation (MW) | 51252 | 51238 |

*Pre and post data of 1 minute before and after the event

| Elements under outage | - 220KV-TP SAURYA LIMITED-KOPPAL-1 - TP SAURYA LIMITED - 220KV |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Rainy , Thunders , Windy |

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 0.0 MW | 0.0 MW |

- Duration of interruption (रुकावट की अवधि):  3 hours, 45 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 220KV-TP SAURYA LIMITED-KOPPAL-1

      - TP SAURYA LIMITED - 220KV

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

220kV TP SAURYA is connected radially to KOPPAL through 220KV-TP SAURYA LIMITED-KOPPAL-1. The triggering incident is the B-G fault in the 220KV-TP SAURYA LIMITED-KOPPAL-1 line.It is reported that at TP Saurya end line tripped due to distance protection. However the same could not be verified due to incomplete DR. At Koppal end, the fault behaviur could not be assessed due to non submission of FIR, DR, and EL.Tripping of the only line connected to 220kV TP SAURYA led to the Complete Outage of 220kV TP SAURYA of TATA POWER.

- DR Analysis:

220KV-TP SAURYA LIMITED-KOPPAL-1

|  | TP SAURYA LIMITED - 220KV | KOPPAL - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:17-03-2026 19:35:33.372 CAR FL FROM DTPC Ir (max): 0.00 kA Iy (max): 0.00 kA Ib (max): 0.00 kA Vr (max): 1.02 kV Vy (max): 0.72 kV Vb (max): 0.69 kV DR is incomplete | DR is not uploaded. |

TP SAURYA LIMITED - 220KV

|  | TP SAURYA LIMITED - 220KV |
| --- | --- |
| Time Sync Issue | Yes |
| DR Analysis | DR Trigger Time:17-03-2026 19:35:33.372 CAR FL FROM DTPC Ir (max): 0.00 kA Iy (max): 0.00 kA Ib (max): 0.00 kA Vr (max): 1.02 kV Vy (max): 0.72 kV Vb (max): 0.69 kV DR is incomplete |

- A) PMU Analysis:

From the PMU plot, dip in B-phase voltage is observed indicating B-G fault during the event with no delayed fault clearance.

B) SCADA Analysis:  Nil

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| TATA | Non furnishing of complete DR at TP Saurya end |
| INDIGRID | Non furnishing of FIR, DR, EL at Koppal end |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| TATA | Transmission line inspection done and no abnormalities are found |

- RLDC Analysis/Observations (Based on Simulation Studies):

Nil

- Restoration Details:

17/03/2026 23:20

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | TATA |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | INDIGRID, TATA |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

Nil

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: