# Draft Report on grid event Complete Outage of 400kV YTPS Generating Station of KPCL, 400kV Kalaburagi SS, 220 kV Aheri, Nimbarga, Vaishali, Shahbad, Kapnoor, Humnabad, Gulbarga, and Santhapur and tripping of 220 kV Bijapur Bus-2, Shahpur Bus-2, Sedam Bus-2 of KPTCL in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 13-04-2026 17:34

# Event Summary (घटना का सारांश):

# 400kV YTPS Generating Station , 400kV Kalaburagi SS, 220 kV Aheri, Nimbarga, Vaishali, Shahbad, Kapnoor, Humnabad, Gulbarga, and Santhapur ,220 kV Bijapur Bus-2, Shahpur Bus-2, Sedam Bus-2 are being radially connected through 400kV BPS YTPS Line-1&2. As per the reports submitted, 400kV BPS YTPS Line-1 tripped on R-G fault at 20:27hrs and 400kV BPS YTPS Line-2 tripped on RY fault at 22:26hrs. Tripping of both lines led to complete outage of all radial connected stations.

- Time and Date of the Event (घटना का समय और दिनांक:  17-03-2026 20:27

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): KARNATAKA

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Karnataka State Demand (MW) | 10421 | 10481 |
| Karnataka State Generation (MW) | 6327 | 5413 |
| Grid Frequency (Hz) | 49.98 | 50.03 |
| SR Demand (MW) | 52137 | 52169 |
| SR Generation (MW) | 48720 | 48204 |

*Pre and post data of 1 minute before and after the event

| Elements under outage | - 400KV-BPS-YTPS-1 - 220KV-SEDAM-FEROZABAD-1 - KAPNOOR - 220KV - Bus 1 - KAPNOOR - 220KV - Bus 2 - 220KV-HUMNABAD-HALBURGA-1 - 220KV-FEROZABAD-NIMBARGA-1 - 220KV-FEROZABAD-NIMBARGA-2 - NIMBARGA - 220KV |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Rainy , Thunders , Windy |

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 975.0 MW | 66.0 MW |

- Duration of interruption (रुकावट की अवधि):  1 hours, 59 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 400KV-BPS-YTPS-2

      - 420KV/27KV YTPS-GT-1

      - 420KV/27KV YTPS-GT-2

      - 220KV-SEDAM-FEROZABAD-1

      - ORIENT_SEDAM - 220KV - Bus 1

      - 400KV-BPS-YTPS-1

      - NIMBARGA - 220KV

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

400kV YTPS Generating Station , 400kV Kalaburagi SS, 220 kV Aheri, Nimbarga, Vaishali, Shahbad, Kapnoor, Humnabad, Gulbarga, and Santhapur, 220 kV Bijapur Bus-2, Shahpur Bus-2, Sedam Bus-2 are being radially connected through 400kV BPS YTPS Line-1&2. As per the reports submitted, at 20:27hrs, R-G fault was sensed in 400kV BPS YTPS Line-1 . At both ends, the fault was sensed in zone-1. A/R operated and the line tripped on persistent fault. At 21:52hrs, R-Y fault was observed in 400kV BPS YTPS Line-2 . At YTPS end, the fault was sensed in zone-1. At BPS end, the fault was sensed in carrier aided zone-2 and the line tripped at both ends. Tripping of both lines led to complete outage of all radial connected stations.

- DR Analysis:

400KV-KALABURAGI-YTPS-1

|  | KALABURAGI - 400KV | YTPS - 400KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:17-03-2026 21:52:10.809 Dis.Pickup L1, Dis.Pickup L2, Dis. forward, Dis. Pickup Z3, Relay PICKUP, Relay PICKUP L1, Relay PICKUP L2 Dis. Pickup Z2 Ir (max): 0.59 kA Iy (max): 0.63 kA Ib (max): 0.20 kA Vr (max): 246.54 kV Vy (max): 247.10 kV Vb (max): 247.14 kV DR Trigger Time:17-03-2026 21:52:10.788 T1 Z2, Z3 Ir (max): 0.59 kA Iy (max): 0.62 kA Ib (max): 0.20 kA Vr (max): 250.50 kV Vy (max): 251.64 kV Vb (max): 250.67 kV |  |

400KV-KALABURAGI-YTPS-2

|  | KALABURAGI - 400KV | YTPS - 400KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:17-03-2026 21:52:10.819 Dis.Pickup L1, Dis.Pickup L2, Dis. forward, Dis. Pickup Z3, Relay PICKUP, Relay PICKUP L1, Relay PICKUP L2 Dis. Pickup Z2 Ir (max): 0.59 kA Iy (max): 0.63 kA Ib (max): 0.20 kA Vr (max): 246.08 kV Vy (max): 247.14 kV Vb (max): 246.62 kV | DR Trigger Time:17-03-2026 21:52:11.080 Any Start Any Trip, DIST Trip A, DIST Trip B, DIST Trip C, Z1, Z2, Z3, RL6-B-PH TO 86M1, RL19-OV/BC/SOTF RL7-A/R LOCK OUT, A/R Lockout, AR Lockout Shot> L12-A/R BLOCK Ir (max): 7.69 kA Iy (max): 6.64 kA Ib (max): 1.22 kA Vr (max): 239.66 kV Vy (max): 234.64 kV Vb (max): 268.99 kV DR Trigger Time:17-03-2026 21:52:11.090 Any Trip, Trip Output A, Trip Output B, Trip Output C, Zone 1 Trip, Aided 1 Send, R24-OV/DEF/STRUB AR Start CB NoAR Ir (max): 7.77 kA Iy (max): 6.70 kA Ib (max): 1.23 kA Vr (max): 242.58 kV Vy (max): 237.51 kV Vb (max): 269.58 kV |

400KV/220KV KALABURAGI-ICT-1

|  | KALABURAGI - 400KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:17-03-2026 20:27:34.245 67/67N pickedup, Relay PICKUP Ir (max): 0.69 kA Iy (max): 0.22 kA Ib (max): 0.23 kA Vr (max): 235.58 kV Vy (max): 236.91 kV Vb (max): 235.37 kV |

400KV/220KV KALABURAGI-ICT-2

|  | KALABURAGI - 400KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:17-03-2026 20:27:34.256 67/67N pickedup, Relay PICKUP Ir (max): 0.70 kA Iy (max): 0.23 kA Ib (max): 0.23 kA Vr (max): 235.36 kV Vy (max): 239.37 kV Vb (max): 236.53 kV DR Trigger Time:17-03-2026 20:27:35.376 67/67N pickedup, Relay PICKUP Ir (max): 0.66 kA Iy (max): 0.24 kA Ib (max): 0.28 kA Vr (max): 228.88 kV Vy (max): 235.88 kV Vb (max): 227.77 kV |

SEDAM - 220KV

|  | SEDAM - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis |  |

YTPS - 400KV

|  | YTPS - 400KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis |  |

HUMNABAD - 220KV

|  | HUMNABAD - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis |  |

SHAHABAD - 220KV

|  | SHAHABAD - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis |  |

KAPNOOR - 220KV

|  | KAPNOOR - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis |  |

KALABURAGI - 400KV

|  | KALABURAGI - 400KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:17-03-2026 20:27:34.249 EF Pickup, EF 3I0p Pickup, Relay PICKUP, Relay PICKUP L1, Relay PICKUP E Ir (max): 0.70 kA Iy (max): 0.26 kA Ib (max): 0.26 kA Vr (max): 234.63 kV Vy (max): 237.86 kV Vb (max): 234.69 kV DR Trigger Time:17-03-2026 20:27:34.239 T1 T1 Ir (max): 0.71 kA Iy (max): 0.26 kA Ib (max): 0.28 kA Vr (max): 240.10 kV Vy (max): 241.67 kV Vb (max): 240.56 kV |

HALBURGA - 220KV

|  | HALBURGA - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis |  |

NIMBARGA - 220KV

|  | NIMBARGA - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:17-03-2026 21:51:33.189 Any Start IN>1 Start, IN>2 Start Ir (max): 0.23 kA Iy (max): 0.17 kA Ib (max): 0.33 kA Vr (max): 137.87 kV Vy (max): 138.16 kV Vb (max): 137.72 kV DR Trigger Time:17-03-2026 21:51:33.191 Any Start IN>1 Start, IN>2 Start Ir (max): 0.23 kA Iy (max): 0.16 kA Ib (max): 0.33 kA Vr (max): 137.70 kV Vy (max): 138.03 kV Vb (max): 137.68 kV DR Trigger Time:17-03-2026 23:18:05.271 Any Start IN>1 Start, IN>2 Start I>2 Start, I>3 Start Any Start IN>1 Start, IN>2 Start Ir (max): 1.04 kA Iy (max): 0.38 kA Ib (max): 0.53 kA Vr (max): 149.71 kV Vy (max): 151.33 kV Vb (max): 150.06 kV DR Trigger Time:17-03-2026 23:18:05.271 Any Start IN>1 Start, IN>2 Start I>2 Start, I>3 Start Any Start IN>1 Start, IN>2 Start Ir (max): 1.03 kA Iy (max): 0.38 kA Ib (max): 0.53 kA Vr (max): 149.49 kV Vy (max): 151.41 kV Vb (max): 150.17 kV |

400KV-BPS-YTPS-1

|  | BPS - 400KV | YTPS - 400KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis |  |  |

400KV-BPS-YTPS-2

|  | BPS - 400KV | YTPS - 400KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis |  |  |

- A) PMU Analysis:

From PMU, dip in R-phase is observed at 20:57hrs indicating R-G fault indicating fault in 400kV BPS YTPS Line-1. At 21:52hrs, dip in and R and Y-phases is observed indicating RY fault during the event in 400kV BPS YTPS Line-2.

B) SCADA Analysis:

From SCADA, tripping of 400kV BPS YTPS Line-1&2 can be observed.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| KPTCL | 1. Tripping of 400V BPS YTPS Line-1&2 2. Radial connectivity of so many RE plants through 400kV YTPS BPS Line-1&2 |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):  Nil

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

17-03-2026 22:26

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | KPCL, KPTCL |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | KPCL, KPTCL |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) | KPTCL |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: