# Draft Report on grid event Complete Outage 220kV Renew_Surya_Koppal of RENEW in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 26-03-2026 17:28

# Event Summary (घटना का सारांश):

# 220kV Renew_Surya_Koppal is connected radially to KOPPAL through 220KV-KOPPAL-Renew_Surya_Koppal-1. The triggering incident is the R-G fault in the 220KV-KOPPAL-Renew_Surya_Koppal-1 line and tripping of the only line connected to 220kV Renew_Surya_Koppal led to the Complete Outage 220kV Renew_Surya_Koppal of RENEW

- Time and Date of the Event (घटना का समय और दिनांक:  18-03-2026 22:28

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): KARNATAKA

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Karnataka State Demand (MW) | 9822 | 9765 |
| Karnataka State Generation (MW) | 6211 | 6147 |
| Grid Frequency (Hz) | 50.02 | 50.03 |
| SR Demand (MW) | 48319 | 48207 |
| SR Generation (MW) | 47211 | 46937 |

*Pre and post data of 1 minute before and after the event

| Elements under outage | - Renew_Surya_Koppal - 220KV |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Rainy , Thunders |

At RSOPL :

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 301.0 MW | 0.0 MW |

- Duration of interruption (रुकावट की अवधि):  1 hours, 35 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - Renew_Surya_Koppal - 220KV

      - 220KV-KOPPAL-Renew_Surya_Koppal-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

220kV Renew_Surya_Koppal is connected radially to KOPPAL through 220KV-KOPPAL-Renew_Surya_Koppal-1. The triggering incident is the R-G fault in the 220KV-KOPPAL-Renew_Surya_Koppal-1 line during heavy rain and lightening. At both ends, the fault was sensed in differential protection. At Koppal end, A/R operated and the line was holding. At RSRPL end, A/R did not trip and the line tripped. Tripping of the only line connected to 220kV Renew_Surya_Koppal led to the Complete Outage 220kV Renew_Surya_Koppal of RENEW.

- DR Analysis:

220KV-KOPPAL-Renew_Surya_Koppal-1

|  | KOPPAL - 220KV | Renew_Surya_Koppal - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR is not available | DR Trigger Time:18-03-2026 22:28:11.819 Any Dist Start Any Trip, Diff Trip, Trip Output A, Trip Output B, R-ph Trip Relay, Spare Zone P Trip Diff InterTrip Carr Rec CH-1, Carr Rec CH-1 Aid 1 Dist Trip A/R Block 86.1 Trip Relay, 86.2 Trip Relay, 87L1 Optd To PMU CB B-ph Open Ir (max): 0.99 kA Iy (max): 0.39 kA Ib (max): 0.41 kA Vr (max): 141.24 kV Vy (max): 138.42 kV Vb (max): 139.96 kV DR Trigger Time:18-03-2026 22:28:11.819 Any Dist Start Any Trip, Diff Trip, Trip Output A, Trip Output B, R-ph Trip Relay, Spare Zone P Trip Diff InterTrip Carr Rec CH-1, Carr Rec CH-1 Aid 1 Dist Trip A/R Block 86.1 Trip Relay, 86.2 Trip Relay, 87L1 Optd To PMU CB B-ph Open Ir (max): 0.99 kA Iy (max): 0.39 kA Ib (max): 0.41 kA Vr (max): 141.24 kV Vy (max): 138.42 kV Vb (max): 139.96 kV |

Renew_Surya_Koppal - 220KV

|  | Renew_Surya_Koppal - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:18-03-2026 22:28:11.819 Any Dist Start Any Trip, Diff Trip, Trip Output A, Trip Output B, R-ph Trip Relay, Spare Zone P Trip Diff InterTrip Carr Rec CH-1, Carr Rec CH-1 Aid 1 Dist Trip A/R Block 86.1 Trip Relay, 86.2 Trip Relay, 87L1 Optd To PMU CB B-ph Open Ir (max): 0.99 kA Iy (max): 0.39 kA Ib (max): 0.41 kA Vr (max): 141.24 kV Vy (max): 138.42 kV Vb (max): 139.96 kV |

- A) PMU Analysis:

From PMU, dip in R-phase is observed indicating R-G fault during the event.

B) SCADA Analysis:

From SCADA, generation loss of 151MW is observed during the evnet.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| INDIGRID | Non submission of FIR, EL and DR at Koppal end |
| RENEW POWER PVT LTD | 1. Non operation of A/R at RSRPL end |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| RENEW POWER PVT LTD | At the time of tripping, heavy rain and lightning were observed in the area. Post‑fault patrolling and inspection of the transmission line and associated PSS / protection system have been completed, and no abnormalities were observed. |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

Renew_Surya_Koppal - 220KV tripped at 18-03-2026 22:28 and restored at 19-03-2026 00:03

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | RENEW POWER PVT LTD |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | INDIGRID |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: