# Draft Report on grid event Complete Outage of 220kV ZENATARIS_PSS in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 16-04-2026 15:26

# Event Summary (घटना का सारांश):

# 220kV Zenataris_PSS is connected to Hiriyur through 220KV-HIRIYUR-ZENATARIS_PSS-1. As per the reports submitted, the triggering incident was YB fault in 220KV-HIRIYUR-ZENATARIS_PSS-1 and the line tripped. Tripping of the only connected line led to complete outage of ZENATARIS_PSS - 220KV

- Time and Date of the Event (घटना का समय और दिनांक:  21-03-2026 14:09

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): KARNATAKA

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Karnataka State Demand (MW) | 14862 | 14925 |
| Karnataka State Generation (MW) | 9293 | 9344 |
| Grid Frequency (Hz) | 49.86 | 49.81 |
| SR Demand (MW) | 61816 | 61812 |
| SR Generation (MW) | 49815 | 49884 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) |  | Load Loss (MW) |
| --- | --- | --- |
| Solar | 0.0 MW | 0.0 MW |
| Wind | 0.5 MW |  |
| Others | 0.0 MW |  |
| Total | 0.5 MW |  |

- Duration of interruption (रुकावट की अवधि):  4 hours, 53 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 220KV-HIRIYUR-ZENATARIS_PSS-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

220kV Zenataris_PSS is connected to Hiriyur through 220KV-HIRIYUR-ZENATARIS_PSS-1. 220 kV Hiriyur is connected to 220 kV Zenataris. The triggering incident was Y-B fault in the line which was located from 42.3 km away from Hiriyur end. At Hiriyur end fault was sensed in Zone 1 and 3ph tripped. At Zenataris end fault was not sensed. Tripping of the only connected line led to complete outage of ZENATARIS_PSS - 220KV

- DR Analysis:

220KV-HIRIYUR-ZENATARIS_PSS-1

|  | HIRIYUR - 220KV | ZENATARIS_PSS - 220KV |
| --- | --- | --- |
| Time Sync Issue | Yes | No |
| DR Analysis | DR Trigger Time:21-03-2026 14:09:55.615 MAIN_Z1_OPTD, MAIN_Z2_START, MAIN_Z3_START, START_AR MAIN1_TRIP, MAIN CB AR LO, TIE_CB_LO, M1/2_CARR_SEND, FAULT_LOOP_B FAULT_LOOP_Y MAIN2_TRIP MAIN_CB_B_OPEN MAIN_CB_R_OPEN, TIE_CB_R_OPEN MAIN_CB_Y_OPEN, TIE_CB_Y_OPEN TIE_CB_B_OPEN PREP_3PH_TR_M/T Ir (max): 0.03 kA Iy (max): 3.37 kA Ib (max): 3.36 kA Vr (max): 138.70 kV Vy (max): 134.47 kV Vb (max): 130.51 kV DR Trigger Time:21-03-2026 15:09:55.127 STARTAR 65501, 3PH TRIP 65499, M2_TRIP 65493, M2Z1_OP 65492, M2Z2_ST 65491, M2Z3_ST 65489 M1_TRIP 65494 M CB_BO 65508 M CB_RO 65510 M CB_YO 65509 PR3P_TR 65442 T CB_RO 65504 T CB_YO 65503 T CB_BO 65502 Ir (max): 0.03 kA Iy (max): 3.38 kA Ib (max): 3.36 kA Vr (max): 139.26 kV Vy (max): 134.59 kV Vb (max): 130.21 kV | Line Holding |

ZENATARIS_PSS - 220KV

|  | ZENATARIS_PSS - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | Supply Failure. No DR uploaded. |

- A) PMU Analysis:

From the PMU plot Y-B fault can be observed without any delayed clearance.

B) SCADA Analysis:

From the SCADA data tripping in the line can be observed.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):  Nil

- Action Taken/Remedial Measures (सुधारात्मक उपाय):  Nil

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

21/03/2026 19:02

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) |  |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | HIRIYUR_ZREPL |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) | HIRIYUR_ZREPL |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: