# Draft Report on grid event Complete Outage of 220kV Serentica_RI3PL_Gadag_Solar  and 220kV Serentica_RI3PL_Gadag_wind in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 02-04-2026 21:45

# Event Summary (घटना का सारांश):

# As per the reports submitted, the triggering incident was R-G fault in 220KV-GADAG_PSS-Serentica_RI3PL_Gadag_Solar-1 and the line tripped. Tripping of the only connected line led to complete outage of 220kV Serentica_RI3PL_Gadag_Solar and 220kV Serentica_RI3PL_Gadag_wind

- Time and Date of the Event (घटना का समय और दिनांक:  23-03-2026 21:58

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): KARNATAKA

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Karnataka State Demand (MW) | 11914 | 11871 |
| Karnataka State Generation (MW) | 6686 | 6703 |
| Grid Frequency (Hz) | 50.03 | 50.08 |
| SR Demand (MW) | 54935 | 54936 |
| SR Generation (MW) | 46145 | 46052 |

*Pre and post data of 1 minute before and after the event

| Elements under outage | - 220KV-GADAG_PSS-Serentica_RI3PL_Gadag_S-1 |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 0.0 MW | 0.0 MW |

- Duration of interruption (रुकावट की अवधि):  0 hours, 0 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 220KV-GADAG_PSS-Serentica_RI3PL_Gadag_S-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

As per the reports submitted, the triggering incident was R-G fault in 220KV-GADAG_PSS-Serentica_RI3PL_Gadag_Solar-1 and the line tripped. Tripping of the only connected line led to complete outage of 220kV Serentica_RI3PL_Gadag_Solar and 220kV Serentica_RI3PL_Gadag_wind

- DR Analysis:

220KV-GADAG_PSS-Serentica_RI3PL_Gadag_S-1

|  | Serentica_RI3PL_Gadag_S - 220KV | GADAG_PSS - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR is not uloaded | DR Trigger Time:23-03-2026 21:58:38.301 MAIN1_TRIP, MAIN2_TRIP, MAIN1_Z1_OPTD, M1/2_CARR_SEND MAIN_CB_R_OPEN Ir (max): 26.16 kA Iy (max): 0.32 kA Ib (max): 0.34 kA Vr (max): 147.60 kV Vy (max): 133.39 kV Vb (max): 132.59 kV |

Serentica_RI3PL_Gadag_S - 220KV

|  | Serentica_RI3PL_Gadag_S - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:23-03-2026 21:58:38.289 21_STFWL1, 21_STFWPE M1Z3_START M1Z2_START 67N_START Not Used, SPARE CB_OPEN_R CB_OPEN_Y, CB_OPEN_B BRC_START FSD1-BLKU Ir (max): 1.09 kA Iy (max): 0.31 kA Ib (max): 0.35 kA Vr (max): 138.63 kV Vy (max): 131.70 kV Vb (max): 130.80 kV |

Serentica_RI3PL_Gadag_W - 220KV

|  | Serentica_RI3PL_Gadag_W - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR is not available |

- A) PMU Analysis:

From the PMU, dip in R-phase is observed indicating R-G fault during the evnet

B) SCADA Analysis:

From the SCADA tripping of 20KV-GADAG_PSS-Serentica_RI3PL_Gadag_Solar-1 is observed

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):  Nil

- Action Taken/Remedial Measures (सुधारात्मक उपाय):  Nil

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

Serentica_RI3PL_Gadag_S - 220KV tripped at 23-03-2026 21:58 and restored at 23-03-2026 21:58

Serentica_RI3PL_Gadag_W - 220KV tripped at 23-03-2026 21:58 and restored at 24-03-2026 00:19

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | SERENTICA_RI1PL |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | GTL, SERENTICA_RI1PL |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram:

NA