# Draft Report on grid event Complete Outage of 220kV TP SAURYA of TATA POWER in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 10-04-2026 16:40

# Event Summary (घटना का सारांश):

# 220kV TP SAURYA is connected radially to KOPPAL through 220KV-TP SAURYA LIMITED-KOPPAL-1. The triggering incident is the R-G fault in the 220KV-TP SAURYA LIMITED-KOPPAL-1 line and tripping of the only line connected to 220kV TP SAURYA led to the Complete Outage of 220kV TP SAURYA of TATA POWER

- Time and Date of the Event (घटना का समय और दिनांक:  25-03-2026 16:23

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): KARNATAKA

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Karnataka State Demand (MW) | 15527 | 15516 |
| Karnataka State Generation (MW) | 8591 | 8590 |
| Grid Frequency (Hz) | 49.93 | 49.91 |
| SR Demand (MW) | 67144 | 67094 |
| SR Generation (MW) | 53758 | 53729 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

At Koppal SS:

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 7.0 MW | 0.0 MW |

- Duration of interruption (रुकावट की अवधि):  4 hours, 9 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 220KV-TP SAURYA LIMITED-KOPPAL-1

      - TP SAURYA LIMITED - 220KV

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

As per the reports submitted, the triggering incident was B-G fault in 220kV Koppal TP Sourya line. At TP Sourya end, the fault was sensed in line differential protection and the line tripped. However, the same could not be verified at Koppal end due to non submission of FIR, DR, EL and TR. Tripping of the only connected line led to complete outage of TP SAURYA LIMITED - 220kV.

- DR Analysis:

220KV-TP SAURYA LIMITED-KOPPAL-1

|  | TP SAURYA LIMITED - 220KV | KOPPAL - 220KV |
| --- | --- | --- |
| Time Sync Issue | Yes | No |
| DR Analysis | DR Trigger Time:25-03-2026 16:23:35.850 67N_START, 27_START L3CPDIF_START, L3CPDIF_STL3, L3CPDIF_BLK2H, L3CPDIF_BLK2HL3 ZMFCPDIS_STNDL3 R PH. TRIP, Y PH. TRIP, B PH. TRIP L3CPDIF_TRIP, L3CPDIF_TRL3, L3CPDIF_TRIPUNRE LDLPDIF_TRIP, LDLPDIF_TRL3, LDLPSCH_TRLOCAL, LDLPDIF_TRLOCL3, PROTECTION_TRIP, START AR AR01_INHIBIT, B_PH_FAULT 86A RELAY OPTD., 86B RELAY OPTD. L3CPDIF_TRIPRES LDLPSCH_TRREMOTE CB OPEN RPH, CB OPEN BPH CB OPEN YPH REM_CB_OPEN L3CPDIF_BLK2H, L3CPDIF_BLK2HL3 46_BRCPTOC_START CAR FL FROM DTPC Ir (max): 0.33 kA Iy (max): 0.34 kA Ib (max): 0.42 kA Vr (max): 131.93 kV Vy (max): 166.58 kV Vb (max): 129.83 kV | DR is not available |

TP SAURYA LIMITED - 220KV

|  | TP SAURYA LIMITED - 220KV |
| --- | --- |
| Time Sync Issue | Yes |
| DR Analysis | DR Trigger Time:25-03-2026 16:23:35.850 67N_START, 27_START L3CPDIF_START, L3CPDIF_STL3, L3CPDIF_BLK2H, L3CPDIF_BLK2HL3 ZMFCPDIS_STNDL3 R PH. TRIP, Y PH. TRIP, B PH. TRIP L3CPDIF_TRIP, L3CPDIF_TRL3, L3CPDIF_TRIPUNRE LDLPDIF_TRIP, LDLPDIF_TRL3, LDLPSCH_TRLOCAL, LDLPDIF_TRLOCL3, PROTECTION_TRIP, START AR AR01_INHIBIT, B_PH_FAULT 86A RELAY OPTD., 86B RELAY OPTD. L3CPDIF_TRIPRES LDLPSCH_TRREMOTE CB OPEN RPH, CB OPEN BPH CB OPEN YPH REM_CB_OPEN L3CPDIF_BLK2H, L3CPDIF_BLK2HL3 46_BRCPTOC_START CAR FL FROM DTPC Ir (max): 0.33 kA Iy (max): 0.34 kA Ib (max): 0.42 kA Vr (max): 131.93 kV Vy (max): 166.58 kV Vb (max): 129.83 kV |

- A) PMU Analysis:

From the PMU, dip in B-phase is observed indicating B-G fault during the event.

B) SCADA Analysis:

From the SCADA, generation loss during the event is observed to be 7MW and the 220kV Koppal TP Sourya was restored on 25-03-2026 21:15hrs.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| TATA | 1. Non operation of A/R at TP sourya end. |
| INDIGRID | 1. Non submission of FIR, DR, EL at Koppal end. |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| TATA | During the epriod of tripping heavy wind, thunder storm and rain occured at this area, Inspected the line for abnormalities and suspecting sag issues. Informed to SRLDC for for test charging and charged the line at 20:32 |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

Complete Outage of 220kV TP SAURYA of TATA POWER @ 25-03-2026 16:23 and restored at 25-03-2026 20:32

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | TATA |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | INDIGRID |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: