# Draft Report on grid event Complete Outage of  220kV SAEL2 in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 07-04-2026 20:26

# Event Summary (घटना का सारांश):

# The triggering incident was R-G fault in 220KV-KURNOOL_PG_III-SAEL2-1 and the line tripped. Tripping of the only connected line led to complete outage of 220kV SAEL2

- Time and Date of the Event (घटना का समय और दिनांक:  29-03-2026 15:55

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): ANDHRA PRADESH

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Andhra Pradesh State Demand (MW) | 12641 | 12585 |
| Andhra Pradesh State Generation (MW) | 7188 | 7136 |
| Grid Frequency (Hz) | 50.06 | 50.04 |
| SR Demand (MW) | 66014 | 65787 |
| SR Generation (MW) | 47569 | 47257 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 150.0 MW | 60.0 MW |

- Duration of interruption (रुकावट की अवधि):  1 hours, 59 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 220KV-SAEL1-KURNOOL_PG_III-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

As per the reports submitted, the triggering incident was R-G fault in 220kV Kurnool_PG_III SAEL2-1. At Kurnool end, the fault was sensed in differential protection, DT was received and the line tripped without A/R operation. At SAEL end, the fault was sensed in differential protection , R-pole opened and DT was sent to remote end. A/R operated at SAEL end but the RE plant could not survive due to non availability of reference voltage as it has grid following invereters. Tripping of only connected line led to complete outage of 220kV SAEL2

- DR Analysis:

220KV-KURNOOL_PG_III-SAEL2-1

|  | KURNOOL_PG_III - 220KV | SAEL2 - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | Yes |
| DR Analysis | DR Trigger Time:29-03-2026 15:52:40.610 87L_STL1, 87L_BLK2H, 87L_BLK5H 87L_STARTRES MAIN1_Z2_START, MAIN1_Z3_START, 21_STFWL1, 21_STFWPE, ZCPSCH_CS DEF_ST, 67N_START MAIN2_TRIP M1/2 CARR.SEND DIFF_OPTD, 87L_TRIP, 87L_TRL1 LDLPSCH_TRIP, LDLPSCH_TRL1, START_AR MAIN1_TRIP CARF_CH1 FAULT_LOOP_R DTRE_CH2 DT_REC_CH1/2, BLOCK_AR DTRE_CH1 LDLPSCH_TRREM GRA_OP, GRB_OP CARR_CH1 PR3_TR_M 3PH_GR_A/B_OPTD M2CAR_RE MAIN_CB_R_OPEN MAIN1/2_CARR_REC, CARR_AID_TRIP, PRE3_TR BRC START MAIN_CB_Y_OPEN MAIN_CB_B_OPEN DEF_ST, 67N_START PSD_ZIN, PSD_ZOUT Ir (max): 11.56 kA Iy (max): 0.42 kA Ib (max): 0.44 kA Vr (max): 122.84 kV Vy (max): 194.31 kV Vb (max): 193.23 kV | DR Trigger Time:29-03-2026 15:52:40.603 DIFF_START_RPH, DIFF_BLK_2H, DIFF_BLK_2H_RPH, DIFF_BLK_5H, DIFF_BLK_5H_RPH DEF_START_FW DIST_START_PE, DIST_START_ND_R DEF_START MAIN2_PROTN_OPTD CARR_RCV_CH-2 DT_SEND_CH-2 DT_SEND_CH-1 DIST_START_ND_B, CARR_RCV_CH-1 DIFF_START_RES DIFF_TRIP_RPH, DIFF_L_TRIP, DIFF_L_TRIP_RPH, DIFF_TRIP_REMOTE DIFF_TRIP_LOCAL ZONE-3_START DIFF_BLK_2H, DIFF_BLK_2H_RPH CB_RPH_OPEN DEF_START_RV PREPARE_3PH_TRIP AR LOCKOUT OPTD SOTF_INIT CB_CLS R Ir (max): 0.51 kA Iy (max): 0.42 kA Ib (max): 0.44 kA Vr (max): 123.35 kV Vy (max): 191.62 kV Vb (max): 190.38 kV |

SAEL2 - 220KV

|  | SAEL2 - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:29-03-2026 15:52:40.603 DIFF_START_RPH, DIFF_BLK_2H, DIFF_BLK_2H_RPH, DIFF_BLK_5H, DIFF_BLK_5H_RPH DEF_START_FW DIST_START_PE, DIST_START_ND_R DEF_START MAIN2_PROTN_OPTD CARR_RCV_CH-2 DT_SEND_CH-2 DT_SEND_CH-1 DIST_START_ND_B, CARR_RCV_CH-1 DIFF_START_RES DIFF_TRIP_RPH, DIFF_L_TRIP, DIFF_L_TRIP_RPH, DIFF_TRIP_REMOTE DIFF_TRIP_LOCAL ZONE-3_START DIFF_BLK_2H, DIFF_BLK_2H_RPH CB_RPH_OPEN DEF_START_RV PREPARE_3PH_TRIP AR LOCKOUT OPTD SOTF_INIT CB_CLS R Ir (max): 0.51 kA Iy (max): 0.42 kA Ib (max): 0.44 kA Vr (max): 123.35 kV Vy (max): 191.62 kV Vb (max): 190.38 kV |

- A) PMU Analysis:

From PMU dip in R-phase voltage is observed indicating R-G fault during the event.

B) SCADA Analysis:  Nil

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| PGCIL SR-1 | 1. Non operation of A/R at Kurnool end. |
| SAEL | 1. Reason for sending DT from SAEL end after differential protection operation |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| SAEL | Will plan for detailed Settings of the relays and will ensure if any abnormalities |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

SAEL2 - 220KV tripped at 29-03-2026 15:55 and restored at 30-03-2026 14:18

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | SAEL |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | SAEL |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: