# Draft Report on grid event Complete Outage of 220kV Renew_Surya_Koppal of RENEW in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 15-04-2026 18:13

# Event Summary (घटना का सारांश):

# As per the reports submitted, the triggering incident was tripping of 220kV Koppal-RSRPL line while charging 220/33kV ICT-2 at 220kV Renew_Surya_Koppal and DT was sent to Koppal end and the line tripped. Tripping of the only connected line led to complete outage of 220kV Renew_Surya_Koppal.

- Time and Date of the Event (घटना का समय और दिनांक:  30-03-2026 14:11

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): KARNATAKA

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Karnataka State Demand (MW) | 16170 | 16304 |
| Karnataka State Generation (MW) | 9807 | 9826 |
| Grid Frequency (Hz) | 50.11 | 50.14 |
| SR Demand (MW) | 69162 | 69411 |
| SR Generation (MW) | 53026 | 52971 |

*Pre and post data of 1 minute before and after the event

| Elements under outage | - 220KV/33KV Renew_Surya_Koppal-ICT-2 |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) |  | Load Loss (MW) |
| --- | --- | --- |
| Solar | 1.0 MW | 0.0 MW |
| Wind | 0.0 MW |  |
| Others | 0.0 MW |  |
| Total | 1.0 MW |  |

- Duration of interruption (रुकावट की अवधि):  1 hours, 5 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 220KV-KOPPAL-Renew_Surya_Koppal-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

220kV Renew_Surya_Koppal (RSRPL) is radially connected to Koppal through 220kV Koppal-RSRPL. As per the reports submitted, the triggering incident was tripping of 220kV Koppal-RSRPL line while charging 220KV/33KV Renew_Surya_Koppal-ICT-2 at 220kV Renew_Surya_Koppal on suspected DEF protection. However, the same could not be verified from DR and EL. At the same time DT was sent to Koppal end and the line tripped at both ends. Tripping of the only connected line led to complete outage of 220kV Renew_Surya_Koppal.

- DR Analysis:

220KV-KOPPAL-Renew_Surya_Koppal-1

|  | KOPPAL - 220KV | Renew_Surya_Koppal - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:30-03-2026 14:11:51.200 T1 Any Start L18 CR REC CH2, DIST UNB CR L8 DT REC CH1, R7 GRP-A TRIP, R8 GRP-B TRIP L22 GRP A OPTD 3PH GR B OPTD T1 L1 M CB R OPN, L3 M CB B OPN L2 M CB Y OPN Ir (max): 0.13 kA Iy (max): 0.86 kA Ib (max): 0.69 kA Vr (max): 133.60 kV Vy (max): 144.26 kV Vb (max): 129.19 kV DR Trigger Time:30-03-2026 14:11:52.274 L1 DT REC CH1 R9 GRP-A TRIP, R10 GRP-B TRIP L15 86B OPTD, L15 86B OPTD Ir (max): 0.05 kA Iy (max): 0.35 kA Ib (max): 0.27 kA Vr (max): 134.70 kV Vy (max): 144.42 kV Vb (max): 129.99 kV | DR Trigger Time:30-03-2026 14:11:52.233 Any Trip, Trip Output A, Trip Output B, 86.1 Trip Relay, 86.2 Trip Relay, 87L1 Optd To PMU, DT Send CH-2 DT Send CH-1 A/R Block CB B-ph Open Ir (max): 0.07 kA Iy (max): 0.38 kA Ib (max): 0.29 kA Vr (max): 135.28 kV Vy (max): 145.62 kV Vb (max): 129.80 kV |

Renew_Surya_Koppal - 220KV

|  | Renew_Surya_Koppal - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:30-03-2026 14:11:52.233 Any Trip, Trip Output A, Trip Output B, 86.1 Trip Relay, 86.2 Trip Relay, 87L1 Optd To PMU, DT Send CH-2 DT Send CH-1 A/R Block CB B-ph Open Ir (max): 0.07 kA Iy (max): 0.38 kA Ib (max): 0.29 kA Vr (max): 135.28 kV Vy (max): 145.62 kV Vb (max): 129.80 kV |

- A) PMU Analysis:

From the PMU dip in voltages is observed indicating transformer inrush current during the event.

B) SCADA Analysis:

From SCADA, tripping of 220kV Koppal Renew_Surya_Koppal is observed.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| INDIGRID | 1. Tripping of 220kV Koppal Renew Surya Koppal line at Renew Surya Koppal line while charging the ICT-2 at Renew Surya Koppal end. |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| INDIGRID | Post‑fault patrolling and inspection of the transmission line and associated PSS / protection system have been completed, and no abnormalities were observed. it was happened due to a DT operation while Energizing the ICT-2. |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

220KV-KOPPAL-Renew_Surya_Koppal-1 tripped at 30-03-2026 14:11 and restored at 30-03-2026 15:16

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | RENEW POWER PVT LTD |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | INDIGRID, RENEW POWER PVT LTD |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) | RENEW POWER PVT LTD |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: