# Draft Report on grid event Tripping of 230kV TTPS Bus-2 of TNPGCL in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 17-04-2026 15:44

# Event Summary (घटना का सारांश):

# The triggering incident is the Y-G fault in TTPS-Kayathar, where in breaker failed to trip and LBB operated leading to tripping of Bus-2 at TTPS.

- Time and Date of the Event (घटना का समय और दिनांक:  17-03-2026 15:15

- Event Category (ग्रिड घटना का प्रकार):  GI-1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): TAMILNADU

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| TamilNadu State Demand (MW) | 17397 | 17417 |
| TamilNadu State Generation (MW) | 8597 | 8566 |
| Grid Frequency (Hz) | 50.06 | 50.1 |
| SR Demand (MW) | 70380 | 70592 |
| SR Generation (MW) | 53540 | 53449 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

Bus-2 configuration at TTPS

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 0.0 MW | 0.0 MW |

- Duration of interruption (रुकावट की अवधि):  0 hours, 53 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 230KV-KAYATHAR(TN)-TTPS-1

      - 230KV-KUDANKULAM-TTPS

      - TTPS - 230KV - Bus 2

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

The triggering incident was the fault in Y-ph fault followed by B-ph fault in 230 kV TTPS-Kayathar line where Kayathar line connected to Bus 2 of TTPS station. At Kayathar end, the Y-G fault was sensed in Z1 and Y-pole opened, then after around 200ms within the dead time, the fault developed into B-G fault and 3ph tripped. At TTPS end, the fault was sensed initially in Zone 2 and then Zone 1, but the breaker failed to open due to SF6 contamination (as per FIR). After around 200 ms LBB operated (electromechanical relay) at TTPS end and led to the Tripping of 230kV Bus-2 at TTPS end. DT was sent to Kayathar end but the DT was not sent to KKNP from TTPS.

- DR Analysis:

TTPS - 230KV

|  | TTPS - 230KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | No DR uploaded. |

230KV-KAYATHAR(TN)-TTPS-1

|  | KAYATHAR(TN) - 230KV | TTPS - 230KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:17-03-2026 15:15:05.585 Any Trip, Zone 1 B Trip, R2 CONT MX 21Y, R10 CR1 SEND, R11 CR2 SEND CB ARIP L8 PROTN BLOCK L2 CB OPN B Any Pole Dead L14 CR2 RECVD L11 CR1 RECVD Any Trip, Zone 1 C Trip, Aid 1 Dist Trip, R1 CONT MX 21R, R2 CONT MX 21Y, R3 CONT MX 21B, R10 CR1 SEND, R11 CR2 SEND A/R Lockout, R6 M 86A TRIP, R9 M 86B TRIP L8 PROTN BLOCK L13 DT1 RECVD, L15 DT2 RECVD L3 CB OPN C L1 CB OPN A All Poles Dead Ir (max): 1.09 kA Iy (max): 15.33 kA Ib (max): 16.25 kA Vr (max): 144.29 kV Vy (max): 138.27 kV Vb (max): 148.20 kV | DR Trigger Time:17-03-2026 15:15:05.579 Any Start, IN>1 Start T1 DIST Fwd Z2 Any Trip, Any Trip B, DIST. Chan Recv A/R 1P In Prog CB Aux B Any Pole Dead PD INPUT EXT TRIP Y Z1, DIST Sig. Send tBF1 Trip A/R Lockout Any Trip A, Any Trip C, 3P Trip, BAR CB Aux C CB Aux A All Pole Dead tBF2 Trip VN>1 Start DIST. Chan Recv Ir (max): 1.09 kA Iy (max): 4.88 kA Ib (max): 0.84 kA Vr (max): 148.30 kV Vy (max): 134.01 kV Vb (max): 133.33 kV |

230KV-KUDANKULAM-TTPS

|  | KUDANKULAM - 230KV | TTPS - 230KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | No DR uploaded. Line Holding. | No DR uploaded. |

- A) PMU Analysis:

From the PMU plot Y-G fault can be observed with delayed clearance.

B) SCADA Analysis:

From the SCADA data TTPS-KUNDANKULAM line tripping and TTPS Bus 2 can be observed.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| TNPGCL | 1. CB failure at TTPS end needs review |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):  Nil

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

17/03/2026 16:08

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | TNPGCL |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | TNPGCL |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) | TNPGCL |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: