# Draft Report on grid event Tripping of 400kV Bus-1 of 400kV Kalaburagi SS in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 13-04-2026 18:30

# Event Summary (घटना का सारांश):

# As per the reports submitted, while opening the bus reactor 400kV Bus-1 of Kalaburagi got tripped tripping all elements connected to the 400kV Bus-1

- Time and Date of the Event (घटना का समय और दिनांक:  18-03-2026 07:51

- Event Category (ग्रिड घटना का प्रकार):  GI-2

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): KARNATAKA

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Karnataka State Demand (MW) | 14007 | 14053 |
| Karnataka State Generation (MW) | 7414 | 7414 |
| Grid Frequency (Hz) | 50.04 | 50.05 |
| SR Demand (MW) | 60882 | 60871 |
| SR Generation (MW) | 50945 | 50942 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

At Kalaburagi SS:

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 0.0 MW | 0.0 MW |

- Duration of interruption (रुकावट की अवधि):  0 hours, 17 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - KALABURAGI - 400KV - Bus 1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

As per the reports submitted, while opening the bus reactor 400kV Bus-1 of Kalaburagi got tripped tripping all elements connected to the 400kV Bus-1

- DR Analysis:

KALABURAGI - 400KV

|  | KALABURAGI - 400KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | No DR was uploaded |

- A) PMU Analysis:

From PMU, no fault is observed during the event.

B) SCADA Analysis:

From SCADA, tripping of 400kV Bus-1 is observed and restored at 8:07hrs.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| KPTCL | 1. Reason for tripping of 400kV Bus-1 while hand tripping the Bus reactor |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):  Nil

- RLDC Analysis/Observations (Based on Simulation Studies):

- Restoration Details:

YTPS line 1,2 charged at 08:08hrs and 08:23 hrs respectively and ICT-2 charged at 08:24 hrs.

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) |  |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 |  |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) | KPTCL |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: