# Draft Report on grid event Tripping of 220kV Bus-2 at Idduku PH of KSEB in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 30-03-2026 20:30

# Event Summary (घटना का सारांश):

# Triping of IDDUKI - 220KV

- Time and Date of the Event (घटना का समय और दिनांक:  18-03-2026 15:26

- Event Category (ग्रिड घटना का प्रकार):  GI-1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): KERALA

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Kerala State Demand (MW) | 3959 | 3962 |
| Kerala State Generation (MW) | 919 | 810 |
| Grid Frequency (Hz) | 49.91 | 49.92 |
| SR Demand (MW) | 65843 | 65658 |
| SR Generation (MW) | 56031 | 55695 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 102.0 MW | 0.0 MW |

- Duration of interruption (रुकावट की अवधि):  1 hours, 0 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 220KV-IDDUKI-KALAMASSERY-2

      - 220KV-IDDUKI-KOTHAMANGALAM-1

      - 220KV-LOWER PERIYAR-IDDUKI-2

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

As per the reports submitted, the triggering incident was a flashover of the R-phase Line PT of 220kV Idukki Kalamassery Line-2, located within the Bus Bar protection zone at the Idukki 220 kV switchyard. Consequently, the 220kv Bus-2 BBPcorrectly detected this as an internal fault, leading to the operation of Bus Bar Zone-2 protection and tripping of all elements connected to Bus No. 2.

It is further submitted that 220kV Idukki PH is an aged generating station, where the existing switchyard configuration has PTs installed ahead CTs, thereby inherently placing them within the protected zone of the Bus Bar protection scheme.

In view of space constraints, existing layout limitations, and operational considerations, relocation or modification of the PT placement is presently not feasible without undertaking major switchyard reconfiguration.

- DR Analysis:

IDDUKI - 220KV

|  | IDDUKI - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:18-03-2026 15:26:17.987 Any Start L1-DT SEND CH-1, L2-DT SEND CH-2 DIST Rev, DIST Start A Z4 DIST. Chan Recv Any Start DIST Rev, Z4, DIST Start B DIST. Chan Recv Ir (max): 2.91 kA Iy (max): 3.15 kA Ib (max): 0.21 kA Vr (max): 223.89 kV Vy (max): 146.34 kV Vb (max): 149.04 kV |

- A) PMU Analysis:

From PMU, dip in R-phase is observed indicating R-G fault during the event

B) SCADA Analysis:  Nil

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| KSEB | 1. Reason for PT flashover |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):  Nil

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

Sl. No

Element

Trip Time

Restoration Time

Remarks

1

2IDKM

15:26

16:34

PT flash

2

2IDLP-2

15:26

16:26

PT flash

3

2IDKL-2

15:26

20.03.2026, 01:57

PT replaced

4

Generator Unit #2

15:26

16:06(Reserve Shutdown)

PT flash

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | KSEB |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 |  |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 | KSEB |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: