# Draft Report on grid event Tripping of 400kV Bus-2 of 400kV Doni S of KPTCL in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 28-03-2026 21:02

# Event Summary (घटना का सारांश):

# As per the reports submitted, the triggering incident was B-G fault in 400kV Bus-2 due to B-phase limb flashover during Bus reactor CB operation. Immediately, 400kV Bus-2 BBP operated and all main breakers connected to 400kV Bus-2 tripped resulting is loss of power supply to 400kV Dhoni Bus-2.

It is reported that the Tie breaker of 400kV/220kV Dhoni ICT-1 was hand tripped by the shift engineer during fault. This led to the loss of power supply to tripping of 400kV/220kV Dhoni ICT-1.

- Time and Date of the Event (घटना का समय और दिनांक:  20-03-2026 08:03

- Event Category (ग्रिड घटना का प्रकार):  GI-2

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): KARNATAKA

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Karnataka State Demand (MW) | 13125 | 13170 |
| Karnataka State Generation (MW) | 6667 | 6825 |
| Grid Frequency (Hz) | 50.05 | 50.02 |
| SR Demand (MW) | 58069 | 58290 |
| SR Generation (MW) | 45939 | 46300 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

At 400kV Doni SS:

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 0.0 MW | 0.0 MW |

- Duration of interruption (रुकावट की अवधि):  1 hours, 35 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - DONI - 400KV - Bus 2

      - 400KV/220KV DONI-ICT-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

As per the reports submitted, the triggering incident was B-G fault in 400kV Bus-2 due to B-phase limb flashover during Bus reactor CB operation. Immediately, 400kV Bus-2 BBP operated and all main breakers connected to 400kV Bus-2 tripped resulting is loss of power supply to 400kV Dhoni Bus-2.

It is reported that the Tie breaker of 400kV/220kV Dhoni ICT-1 was hand tripped by the shift engineer during fault. This led to the loss of power supply to tripping of 400kV/220kV Dhoni ICT-1.

- DR Analysis:

400KV/220KV DONI-ICT-1

|  | DONI - 400KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:20-03-2026 08:01:46.728 Device trip G, Trip L3 G, Trip BBP G BUS2 BB OP DR Trigger Time:20-03-2026 08:01:46.731 Device trip G, Trip L3 G, Trip BBP G, Trip B2 L3 BUS2 BB OP |

DONI - 400KV

|  | DONI - 400KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:20-03-2026 08:01:46.728 Device trip G, Trip L3 G, Trip BBP G BUS2 BB OP DR Trigger Time:20-03-2026 08:01:46.731 Device trip G, Trip L3 G, Trip BBP G, Trip B2 L3 BUS2 BB OP |

- A) PMU Analysis:

From PMU voltage at 400kV Guttur, dip in B-pole is observed indicating B-G fault during the event with no delayed fault clearance.

B) SCADA Analysis:

From SCADA plot, tripping of 400kV Bus-2 is observed

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| KPTCL | 1. Reason for Bus reactor breaker limb flashover . 2. Hand tripping of Tie breaker of 400kV/220kV Dhoni ICT-1 |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| KPTCL | Isolated the faulty section of Bus Reactor bay and charged the 400kV bus-2 and ICT-1. Need to replace the faulty breaker. |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

DONI - 400KV tripped at 20-03-2026 08:03 and restored at 20-03-2026 09:38

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | KPTCL |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | KPTCL |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: