# Draft Report on grid event Tripping of 230kV Bus-1 of Karaikudi SS of TANTRANSCO in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 07-04-2026 19:23

# Event Summary (घटना का सारांश):

# As per the reports submitted, the triggering incident was B-G fault in 230kV Karaikudi Bus-1 and BBP operated tripping all elements connected to the 230kV Karaikudi Bus-1. 230kV Bus-2 and 110kV side was in service during the event.

- Time and Date of the Event (घटना का समय और दिनांक:  26-03-2026 17:57

- Event Category (ग्रिड घटना का प्रकार):  GI-1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): TAMILNADU

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| TamilNadu State Demand (MW) | 18705 | 18717 |
| TamilNadu State Generation (MW) | 6303 | 6248 |
| Grid Frequency (Hz) | 49.99 | 50.09 |
| SR Demand (MW) | 58654 | 58367 |
| SR Generation (MW) | 50363 | 50368 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

At Karaikudi SS:

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 0.0 MW | 0.0 MW |

- Duration of interruption (रुकावट की अवधि):  3 hours, 50 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 230KV-KARAIKUDI(TN)-KAVANUR-1

      - 230KV-KARAIKUDI(TN)-KAVANUR-3

      - 230KV-KARAIKUDI(TN)-KAVANUR-4

      - 230KV-KARAIKUDI-KARAIKUDI(TN)-1

      - 230KV-KARAIKUDI(TN)-KARAMBAYAM-1

      - KARAIKUDI(TN) - 230KV - Bus 1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

As per the reports submitted, the triggering incident is the B-ph jumper cut in Bus-1 in 230kV NT Kudy Bay and Kavanur-3 line (as per FIR) which led to the Bus-1 fault. However, from the DR data, it can be observed that the BBP did not operate immediately and operated almost after around 350ms.

It can also be observed that after tripping of F7 (exact line to be confirmed by TANTRANSCO), where in after around 2 cycles BBP operated in Z1 and all the elements connected to Bus-1 tripped. This led to the Tripping of 230kV Bus-1 of Karaikudi SS. 230kV Bus-2 and 110kV side was in service during the event.

- DR Analysis:

KARAIKUDI(TN) - 230KV

|  | KARAIKUDI(TN) - 230KV |
| --- | --- |
| Time Sync Issue | Yes |
| DR Analysis | DR Trigger Time:26-03-2026 17:57:21.444 DR TRIP ON (VO4), B27 KAVANOOR 3 INI ON (VO102) B28 KAVANOOR 4 INI ON (VO103) B27 CB OPN ON (DI41) Z1 BB OP ON (VO5), Z-1 TRIP ON (VO46), B21 KAVANOOR 1 TRIP ON (VO49), B25 PGCIL 1 TRIP ON (VO52), B26 NT KUDI 1 TRIP ON (VO53), B27 KAVANOOR 3 TRIP ON (VO54), B28 KAVANOOR 4 TRIP ON (VO55), 2HV1 TRIP ON (VO57), BC TRIP ON (VO59) B28 CB OPN ON (DI47) B21 KAVANOOR 1 INI ON (VO93), B25 PGCIL 1 INI ON (VO97), B26 NT KUDI 1 INI ON (VO98), 2HV1 LBB INI ON (VO105), BC LBB INI ON (VO101) B25 CB OPN ON (DI29), B26 CB OPN ON (DI35) B21 CB OPN ON (DI11), 2HV1 CB OPN ON (DI60) Ir (max): 0.58 kA Iy (max): 0.12 kA Ib (max): 0.58 kA |

- A) PMU Analysis:

From the PMU analysis, B-G fault can be observed during the event with delayed fault clearance

B) SCADA Analysis:

From the SCADA data, it can be observed that Bus-1 tripped at Karaikudi

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| TANTRANSCO | 1. Delayed operation of BBP protection needs review 2. Non availability of SCADA SOE at KARAIKUDI(TN) needs review |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):  Nil

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) |  |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 |  |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 | TANTRANSCO |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: