# Draft Report on grid event Tripping of 400kV Bus-2 at Dichipally of TGTRANSCO in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 23-04-2026 16:14

# Event Summary (घटना का सारांश):

# The triggering incident is the R-G Bus fault in 400 kV Bus-2 due to bus post insulator failure leading to Bus Bar protection Operation and leading to the tripping of 400kV Bus-2 at Dichipally due to inclement weather conditions. 400 kV Dichipally-Nirmal line and 400 kV/220 kV Dichipally ICT-4 got tripped during the event.

- Time and Date of the Event (घटना का समय और दिनांक:  04-04-2026 22:26

- Event Category (ग्रिड घटना का प्रकार):  GI-2

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): TELANGANA

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Telangana State Demand (MW) | 9867 | 9864 |
| Telangana State Generation (MW) | 5569 | 5550 |
| Grid Frequency (Hz) | 50.09 | 50.08 |
| SR Demand (MW) | 56826 | 56628 |
| SR Generation (MW) | 48716 | 48469 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Thunders , Windy |

Bus configuration at Dichipally :

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 0.0 MW | 0.0 MW |

- Duration of interruption (रुकावट की अवधि):  20 hours, 0 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 400KV-DICHPALLY-NIRMAL-1

      - 400KV/220KV DICHPALLY-ICT-4

      - DICHPALLY - 400KV - Bus 2

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

Due to inclement weather multiple faults can be observed from the PMU.

Event at 22:30:56 Hrs :

As per the reports submitted, the first fault which was triggered in 400kV Dichpally-Nirmal line was B-G fault within the substation and subsequent Y-G fault during the AR dead time due to isolator damage. At Nirmal end the first B-G fault was sensed in Zone 1 and B pole opened and during the subsequent Y-G fault was sensed in Z2 carrier aided protection and Y-pole opened, but the R-pole was in service until it tripped on suspected PD operation after around 3.1s from the initial fault (as per EL). At Dichipally end the first B-G fault was sensed in Zone 1 and B pole opened and during the subsequent Y-G fault was sensed in Z1 and 3 ph tripped.

Event at 22:31:08 Hrs :

The triggering incident is the R-G fault within the ICT differential zone due to failure of Bus post insulator and differential protection operated leading to the tripping of 400/220kV Dichipally ICT-4

Event at 22:31:16 Hrs :

The triggering incident is the R-G fault in 400kV Bus-2 due to failure of Bus post insulator and Bus Bar protection operated and all the main breakers connected to Bus-2 tripped and led to the tripping of 400kV Bus-2 at Dichipally. 400kV Bus-1 was in service during the event and all other elements were in service through tie breakers due to one and half breaker scheme.

The sequence of tripping is as shown below :

| Element Name with fault | Time of Trip |
| --- | --- |
| 1. B-G fault in Dichpally-Nirmal Line | 1. 04/04/2026 22:30:56:880 |
| 2. Y-G fault in Dichpally-Nirmal Line | 2. 04/04/2026 22:30:57:560 |
| 3. R-G fault in Dichpally ICT-4 | 3. 04/04/2026 22:31:08:720 |
| 4. R-G fault in Dichpally Bus-2 | 4. 04/04/2026 22:31:16:520 |

The location of fault with the SLD is as shown below:

The faults within the substation

- DR Analysis:

400KV-DICHPALLY-NIRMAL-1

|  | DICHPALLY - 400KV | NIRMAL - 400KV |
| --- | --- | --- |
| Time Sync Issue | Yes | Yes |
| DR Analysis | DR Trigger Time:04-04-2026 22:28:23.454 1pole open L3 Relay PICKUP, Relay PICKUP L1 Dis.Pickup L2, Dis.Pickup E, Dis. forward, Relay PICKUP L2, Relay PICKUP E, Relay TRIP L1, Relay TRIP L2, Relay TRIP L3 Relay TRIP 86B OPTD >Trig.Wave.Cap. Ir (max): 0.65 kA Iy (max): 28.23 kA Ib (max): 0.03 kA Vr (max): 279.64 kV Vy (max): 241.18 kV Vb (max): 69.21 kV | DR Trigger Time:04-04-2026 22:30:32.838 OSC TRIGGER ON (VO64), GND DIST Z1 OP, PUTT TX1 L12 T B CLS OFF (CI12) L19 M B CLS OFF (CI19) PH DIR1 BLK PUTT OP, L6 CR RX-1/2 ON (CI6) L18 M Y CLS OFF (CI18) L11 T Y CLS OFF (CI11) L1 GR-B OPTD ON (CI1) L17 M R CLS OFF (CI17) Ir (max): 0.64 kA Iy (max): 7.25 kA Ib (max): 8.05 kA Vr (max): 241.56 kV Vy (max): 242.55 kV Vb (max): 241.30 kV |

400KV/220KV DICHPALLY-ICT-4

|  | DICHPALLY - 400KV |
| --- | --- |
| Time Sync Issue | Yes |
| DR Analysis | DR Trigger Time:04-04-2026 22:29:54.451 Idiff Trip A L11 IV GRP A TR L10 IV GRP B TR L8 GRP A TRIP L9 GRP B TRIP L9 GRP B TRIP L9 GRP B TRIP Ir (max): 26.57 kA Iy (max): 0.75 kA Ib (max): 0.94 kA |

DICHPALLY - 400KV

|  | DICHPALLY - 400KV |
| --- | --- |
| Time Sync Issue | Yes |
| DR Analysis | DR Trigger Time:04-04-2026 21:32:34.621 Any Trip, 87BB Fault Ph A, Trip 87BB Trip Zone 2 Ext. 3 ph Trip, BB TRP RLY OPTD CB Aux. 3ph(52b) Ir (max): 22.54 kA Iy (max): 0.27 kA Ib (max): 0.41 kA DR Trigger Time:04-04-2026 21:32:34.621 Fault Check Zone Fault Phase A, Flt 87BB Zone 2, Trip 87BB Zone 2 Ir (max): 27.51 kA Iy (max): 0.11 kA Ib (max): 0.05 kA |

- A) PMU Analysis:

From the PMU data multiple faults can be observed during the event and prior to the event

B) SCADA Analysis:

From the SCADA data, tripping of the 400kV Nirmal-Dichpally-1 can be observed

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| TGTRANSCO | 1. 400KV-DICHPALLY-NIRMAL-1 non opening of R-ph pole after Y-ph fault in dead time at NIRMAL end needs review. 2. Sensing of Fault in the substation at DICHPALLY as Z1 for 400KV-DICHPALLY-NIRMAL-1 at NIRMAL end needs review. 3. Different Fault distance for 400KV-DICHPALLY-NIRMAL-1 at NIRMAL in M1(61km sensed in Z2) and M2 (39km sensed in Z1) needs review |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| TGTRANSCO | a) Restored the Bus - 2 and ICT - 4 by replacing the damaged Bus Post Insulator (BPIs) with spare BPIs at 18:26Hrs on 05-04-2026. b) Replaced the damaged Line Isolator with spare and charged the 400kV Dichpally – Nirmal – 1 feeder. c) New GPS server was drawn from the stores for replacement of the damaged GPS server and commissioning of the same will be done in 3-4 weeks. d) Non operation of Auto recloser on 400kV Dichpally – Nirmal – 1feeder will be studied. |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

05/04/2026 18:26

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | TGTRANSCO |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | TGTRANSCO |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) | TGTRANSCO |
| 4 | Any other non-compliance | IEGC section 17.3 | TGTRANSCO |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: