## P-Rec (Pending)
Status of Pending Implementation of PCSC Recommendations
Meeting Index | Details of Event | Date & Time | Reason | PCSC Recommendations | Utility Responsible for Implementation | Consolidated Status of Implementation | Individual Compliance Status | Consolidated Compliance Status
MULTI-UTILITIES
66/II/10 | Tripping of 400/ 220 kV ICTs 3 & 4 at Ramagundam STPS | 11-06-2017 at 19:46hrs | Triggering incident was failure of 220 kV B-phase LA in ICT-3 LV extension feeder (220KV line-2) at Malayalapalli substation | 1. NTPC to disable high-set of DEFR on the 220 kV lines emanating from their Ramagundam STPS. 2. NTPC/ TSTRANSCO to provide Line Differential Protection (with or without pilot) on 220 kV Ramagundam Malayalapalli lines 1 & 2 & 3. | NTPC-Ramagundam/ TSTRANSCO | srpcadmin:SRPC: 24/11/2023 17:23:11: Discused in bilateral meeting held on 05.06.2023: NTPC mail dated 22.06.2023 1. NTPC Ramagundam disabled high-set of DEFR on the 220 kV lines emanating from Ramagundam STPS. 2. NTPC Ramagundam commissioned Line Differential Protection Relays on 220 kV Ramagundam â Malayalapalli lines â 1 & 2 & 3; LDP will be enabled when Optical Fibre Cable is made available TSTRANSCO: Mail dated 28-08-2023 LDPs commissioned at 220kV RSS end and there are no pending works at RSS end. | Complied | Complied
93/II/1 | Tripping of 400 kV Bus-2 at 400 kV Yelahanka SS of PGCIL-SR2 | 03-08-2020 at 17:32 Hr. | During antecedent conditions, ICT2 at Yelahanka was under outage since 09:09Hr. due to AMP works. As per the information received, while charging ICT2 at 17:36Hr., Bus-2 BBP operated due to failure of R-phase bus isolator of ICT2. This resulted in the tripping of all the elements connected to Bus2 along with bus coupler. | i. PGCIL SR-2 to share the findings of the OEM on VFT over voltage referred to and remedial measures thereof. ii. KPTCL to review & correct Zone settings on 400 kV Nelamangala Yelahanka line at Nelamangala end. iii. KPTCL to ensure time synchronization of relays at Nelamangala SS. | PGCIL(Sr-2)/ KPTCL | srpcadmin:SRPC: 24/11/2023 17:26:01: Discussed in bilateral meeting held on 02.06.2023 (PGCIL): OEM visited Yelahanka SS on 6th and 7th Sept. 2022. No other modifications suggested by OEM and has requested to be kept under observation. Point may be closed. Discussed in bilateral meeting held on 12.05.2023 (KPTCL): Out of 12 nos of 220kV lines emanating from Nelamangala, AR enabled for 4 no.s of lines(Anchepalya, Nittur, Magadi and Dobaspet) . 220kV AN Halli and KB Cross are temporarily reconfigured and these lines are not connected to Nelamangala bus at present. For 4 numbers of Peenya connected 220kV lines passing through dense populated city limits in Bangalore (Peenya1,2,3 and 4) for which exemption is sought. The issue was discussed during 105th PCSC meeting of SRPC. Remaining two lines connecting to DB Pura AR will be enabled , delayed due to M1 relay (SEL) OEM issue. Puspha:KPTCL: 17/02/2025 16:38:08: During the incident, for the bus fault at Yelahanka, Yelahanka line tripped at Nelamangala on Zone-1. To ascertain the zone reaches adopted, actual line length was verified using offline fault locator. Line length considered for setting calculation was 38.5km.80 % of the protected line length is considered for ZOne-1 as per protection philosophy. Measured line length was around 40km. Hence, the zone-1 settings adopted are not revised. In view of this SRPC is requested to close this recommendations. | Complied | Complied
93/II/15 | Multiple Tripping at 400/220 kV Ramagundam GS | 02-08-2020 at 13:07 Hr. | Triggering incident was R-N fault in 220 kVRamagundam- Malayalapalli line-3. At the same time, 400 kVRamagundam -Dichipalli line tripped only at Ramagundam end on OV Stage 2 operation. | i. NTPC- Ramagundam to submit a report after thoroughchecking of CVT circuit, to sort out the issue of faultyCVT secondary voltage measurement. ii. NTPC- Ramagundam in coordination with TSTRANSCO to perform PLCC end to end testing for 400 kV Ramagundam Dichipalli line. | NTPC-Rmgdm/TSTRANSCO | deprotection1:TGTRANSCO: 01/04/2024 16:46:21: TSTRANSCO: PLCC end to end testing was carried out long back. However, recently on 06-07-2023, Channel-2 was taken into service duly availing LC and carrying out end to end testing. This update was mailed to SRPC on 30-08-2023. | Complied | Complied
108/I/13 | Complete Outage of 230kV JSW_Vilathikulam_Wind | 07-05-2023 00:33 | . | To enable A/R for the 230kV TTGS-JSW_VILATHIKULAM_WIND line at both ends. | JSW/ PGCIL SR-II | rtamcsr2:PGCIL (SR-II): 13/03/2025 12:44:55: AR enabled in all 220 kv Lines @ TUTICORIN GIS | Complied | Complied
108/I/14 | Complete Outage of 220kV Rychalu SS-2 of KSPDCL | 08-05-2023 05:10 | . | 1. KSPDCL to disable the Overvoltage protection for the 220 kV feeders connected between 220 kV KSPDCL Pooling Stations & PGCIL Pavagada SS or else keep it at higher side. 2. KSPDCL/PGCIL SR-II to resolve the software issues and to review the relay settings.. | KSPDCL/PGCIL SR-II | rtamcsr2:PGCIL (SR-II): 24/04/2024 19:30:17: Software handed over to KSPDCL rtamcsr2:PGCIL (SR-II): 13/03/2025 12:46:31: OV Settings are Disabled @ POWERGRID end ceokspdcl:KSPDCL: 01/04/2025 14:07:58: In the 220kVline protection relay, over voltage protection got disabled on 20.07.2023. ceokspdcl:KSPDCL: 01/04/2025 14:25:40: As per the PCSC recommendation, In the 220kV line protection relay, over voltage protection is disabled on 20.07.2023. | Complied | Complied
108/I/4 | Complete Outage of 220kV/66kV Tirumani SS-1, 220kV/66kV Tirumani SS-2 and 220kV/66kV Rychalu_1 SS of KSPDCL | 15-04-2023 18:01 | . | 1. KSPDCL to disable the Overvoltage protection for the 220 kV feeders connected between 220 kV KSPDCL Pooling Stations & PGCIL Pavagada SS or else keep it at higher side. 2. KSPDCL/PGCIL SR-II to resolve the software issues and to review the relay settings. | KSPDCL/PGCIL SR-II | rtamcsr2:PGCIL (SR-II): 24/04/2024 19:30:17: Software handed over to KSPDCL ceokspdcl:KSPDCL: 01/04/2025 14:07:58: As per the PCSC recommendation, In the 220kV line protection relay, over voltage protection is disabled on 20.07.2023. ceokspdcl:KSPDCL: 01/04/2025 14:26:23: As per the PCSC recommendation, In the 220kV line protection relay, over voltage protection is disabled on 20.07.2023. | Complied | Complied
112/I/1 | Tripping of 230kV Bus-2 of 400kV/230kV Alamathy SS of TANTRANSCO and Complete Outage of 230kV OPG_CPP SS | 02-10-2023 10:40 | The triggering incident was B-N fault in 230kV Alamathy OPG Line-1. Consequently, 230kV Alamathy OPG Line-2 got overloaded leading to the failure of the B-phase jumper connected to the 230kV Alamathy Bus-2 causing a fault in Bus-2. Tripping of both connected lines to 230kV OPG resulted in a complete outage of the SS. At the same time, NTECL Vallur Unit-3 tripped on Low forward power protection. | 1.OPG to enable delayed A/R at OPG end. TANTRANSCO needs to take up with OPG. 2.TANTRANSCO to check the second main relay behaviour and whether breaker was at lockout condition.Reason for the three phase trip needs to be furnished. 3. NTECL Vallur to furnish the turbine vibrations range details to SRPC. | TANTRANSCO/ NTECL Vallur | Anupama:NTECL: 01/08/2024 15:11:07: NTECL complied via mail on 30.07.2024 | Complied | Complied
112/III/9 | TRIPPING OF 400KV/230KV VELLALAVIDUTHI-ICT - 4 and 400KV-PUGALUR - VELLALAVIDUTHI-1 | 11-10-2023 16:28 | As per the report submitted, triggering incident was R-N fault in 400KV Pugalur Vellalaviduthi line. During this fault 400KV/230KV Vellalaviduthi ICT-4 also tripped on REF. | TANTRANSCO and PGCIL SR-II to carry out end- to end testing. | TANTRANSCO / PGCIL SR-II | cepc:TANTRANSCO: 20/01/2025 15:19:30: carrier send & receive checked | Complied | Complied
112/III/10 | TRIPPING OF 400kV RAMADUGU SINGARENI-1 | 18-10-2023 13:05 | As per the reports submitted, the triggering incident was a B-N fault in the line. Multiple AR attempts at Singareni needs review. Tripping is not in order | 1.SCCL to check the Tie BCU A/R logic and take necessary action. 2.TSTRANSCO to maintain/clear the ROW of SCCL-Ramadugu line on regular basis. | SCCL/TSTRANSCO | deprotection1:TGTRANSCO: 03/06/2024 12:01:34: TGTRANSCO is maintaining the ROW clearances on regular basis. | Complied | Complied
113/I/1 | Complete Outage of 220kV/110kV Bagewadi SS of KPTCL, 220kV Baluthi, 220kV Fortune SS, 220kV Atria SS and 220kV RBRK SS | 15-10-2023 09:42 | As per the reports submitted, the triggering incident was a failure of the 220kV Bus coupler at 220kV/110kV Bagewadi SS causing R-N fault in 220kV Bus-1 and 220kV Bus-2. The BBP failed to clear the fault and all the elements connected to the buses tripped from remote ends resulting in a complete outage of 220kV/110kV Bagewadi SS. Since 220kV Baluthi, 220kV Fortune SS, 220kV Atria SS and 220kV RBRK SS are radially connected with 220kV/110kV Bagewadi SS outage of 220kV/66kV Bagewadi SS resulted in a complete outage of these stations. Since the final report is not submitted, further details are still awaited. | 1.KPTCL to resolve the Communication issue at Nandihal Substation and inform the same to SRPC & SRLDC. 2.KPCL to rectify the non-operation of Zone-2 at Almatti end. And to replace Electromechanical relay with Numerical relay. | KPTCL / KPCL |  | Pending | Pending
116/II/2 | Tripping of 230kV Bus-2 of 230kV Neyveli TS-2 | 02-01-2024 04:49 | As per the reports submitted, the triggering incident was R-N fault in 230kV Neyveli TS-II Ulundurpet line. At Neyveli end, A/R was in disabled condition and 3 phase trip was given to the circuit breaker. Bpole of the circuit breaker failed to open causing LBB to operate and all the lines connected to the 230kV Bus-1 of 230kV Neyeli TS-II tripped. At Ulundurpet end, the fault was sensed in zone-1. A/R operated and the line was holding. | NLCIL to expedite the process of replacement / repair of the breaker and inform to TANTRANSCO for enabling of A/R after Breaker replacement / repair. | NLCIL TPS-II | NLCI/TS2:NLCIL: 04/04/2025 16:31:42: CB OH is completed by OEM, Relay retrofitting completed. LBB logic pending, will be enabled next outage. NLCI/TS2:NLCIL: 07/11/2025 10:08:21: "A/R function tested and enabled at both ends. The point shall be closed" | Complied | Complied
116/II/2 | Tripping of 230kV Bus-2 of 230kV Neyveli TS-2 | 02-01-2024 04:49 | As per the reports submitted, the triggering incident was R-N fault in 230kV Neyveli TS-II Ulundurpet line. At Neyveli end, A/R was in disabled condition and 3 phase trip was given to the circuit breaker. Bpole of the circuit breaker failed to open causing LBB to operate and all the lines connected to the 230kV Bus-1 of 230kV Neyeli TS-II tripped. At Ulundurpet end, the fault was sensed in zone-1. A/R operated and the line was holding. | TANTRANSCO to disable the A/R at Ulundurpet end from 06.03.2024 till the replacement of breaker at NLC TS-II end. | TANTRANSCO | cepc:TANTRANSCO: 20/01/2025 15:19:30: complied | Complied | Complied
116/III/7 | Multiple Trippings at Bhavini SS | 09-02-2024 21:21 | Tripping of 230kV Bhavini Siruseri Line-2 and 230kV Bhavini Arni Line-1 for an external fault. | BHAVINI and TANTRANSCO to furnish the relay settings details of all the feeders from BHAVINI end to PSSG for review of settings. | M/s BHAVNI TANTRANSCO | cepc:TANTRANSCO: 20/01/2025 15:19:30: setting furnished | Pending | Pending
117/I/2 | Complete Outage of 400kV MEPL | 23-02-2024 18:22 | As per the reports submitted, 400kV MEPL NPS Line-2 was taken on shutdown at 10:37 hrs for rectification of jamming and sparking at contacts of tie bay Isolator. After completing the works, the line was charged at NPS end at 18:20Hrs. While closing the breaker at MEPL end, only Y and B-poles closed and R-pole failed to close. Immediately, pole discrepancy operated and the line tripped at MEPL end. At the same time, 400kV MEPL-SEPL line tripped on earth fault protection due to imbalance current in neutral and DT was sent to the SEPL end. | 1.MEPL and SEPL to implement IDMT DEF at both ends. 2.MEPL to ensure healthiness of the circuit breakers and other substation equipment. 3.MEPL and SEPL to furnish the SCADA SOE to SRLDC. | MEPL & SEPL |  | Pending | Pending
117/I/5 | Complete Outage of 220kV Bagalkot | 19-03-2024 10:37 | In the antecedent conditions, 220kV Bagalkot is connected with 220kV Bagalkot-Vajramathi-1&2, 220kV Bagalkot-Alamatti-1&2, 220kV Bagalkot-Gadag-1&2 with lines-1 connected to Bus-1 and lines-2 connected to Bus-2. 220kV Vajramathi is connected with 220kV Bagalkot-Vajramathi-1&2, 220kV Kudgi-Vajramathi-1&2, 220kV Mahalingapura-Vajramathi-1&2 with lines-1 connected to Bus-1 and lines-2 connected to Bus-2. | 1.KPTCL to expedite to provide bus bar protection at Bagalkot station. 2.KPTCL to check/review the Zone overreach at Vajramatti end. 3.Protection audit to be carried out at 220 kV Bagalkot substation by a team comprising of PGCIL SR-II, SRLDC and SRPC Secretariat. | KPTCL |  | Pending | Pending
117/I/5 | Complete Outage of 220kV Bagalkot | 19-03-2024 10:37 | In the antecedent conditions, 220kV Bagalkot is connected with 220kV Bagalkot-Vajramathi-1&2, 220kV Bagalkot-Alamatti-1&2, 220kV Bagalkot-Gadag-1&2 with lines-1 connected to Bus-1 and lines-2 connected to Bus-2. 220kV Vajramathi is connected with 220kV Bagalkot-Vajramathi-1&2, 220kV Kudgi-Vajramathi-1&2, 220kV Mahalingapura-Vajramathi-1&2 with lines-1 connected to Bus-1 and lines-2 connected to Bus-2. | KPCL to expedite to replace the older version of relays with new version of relays at Almatti end. | KPCL |  | Pending | Pending
117/I/5 | Complete Outage of 220kV Bagalkot | 19-03-2024 10:37 | In the antecedent conditions, 220kV Bagalkot is connected with 220kV Bagalkot-Vajramathi-1&2, 220kV Bagalkot-Alamatti-1&2, 220kV Bagalkot-Gadag-1&2 with lines-1 connected to Bus-1 and lines-2 connected to Bus-2. 220kV Vajramathi is connected with 220kV Bagalkot-Vajramathi-1&2, 220kV Kudgi-Vajramathi-1&2, 220kV Mahalingapura-Vajramathi-1&2 with lines-1 connected to Bus-1 and lines-2 connected to Bus-2. | NTPC Kudgi to review the zone settings at Kudgi end. | NTPC- Kudgi | gpremshankar:NTPC: 13/03/2025 16:27:29: Setting reviewed, No modification advised by NTPC Engineering team. | Complied | Pending
117/III/3 | Tripping of 400kV Narnoor-Srisailam and 220kV BC and station transformers at Srisailam | 02-03-2024 14:26 | During the fault in 400kV Narnoor-Sri- sailam line, 220kV Bus Coupler and station transformers at Srisailam got tripped and needs review | SRLDC to analyze the event in details (after receipt of data from TSGENCO) and furnish the detailed for deliberation in the next meeting. | SRLDC | ArthiV~1776856274:SRLDC: 02/07/2025 19:02:04: Detailed Report sent on 08-05-2024. Discussed during 118th PCSC meeting 08-05-2024. Proof for the same is attached. The point may be closed. | Complied | Pending
117/III/3 | Tripping of 400kV Narnoor-Srisailam and 220kV BC and station transformers at Srisailam | 02-03-2024 14:26 | During the fault in 400kV Narnoor-Sri- sailam line, 220kV Bus Coupler and station transformers at Srisailam got tripped and needs review | TSGENCO to furnish the DR/EL of the event (tripping of Station Transformer due to Earth fault) to SRLDC & SRPC. | TSGENCO |  | Pending | Pending
118/I/5 | Complete Outage of 220kV/33kV Gopalpura SS of SUZLON_KA | 13-04-2024 18:10 | - | KPTCL to address the non-availability issue of SCADA SOE of 220kV Gopalpura and 220kV Tubinakere ends. | KPTCL |  | Pending | Pending
118/I/5 | Complete Outage of 220kV/33kV Gopalpura SS of SUZLON_KA | 13-04-2024 18:10 | - | KPTCL to resolve the time sync issues of 220kV Tubinkere-Gopalpura line at Tubinkere end. | KPTCL |  | Pending | Pending
118/I/5 | Complete Outage of 220kV/33kV Gopalpura SS of SUZLON_KA | 13-04-2024 18:10 | - | M/s Suzlon to carry out third party protection audit of their Substation and submit report to SRPC within one month. Also to look into DR/EL issues at 220kV Gopalpura SS. | M/s Suzlon |  | Pending | Pending
118/I/5 | Complete Outage of 220kV/33kV Gopalpura SS of SUZLON_KA | 13-04-2024 18:10 | - | M/s Suzlon to comply to CEA Regulations and substations to be managed by trained staff as per IEGC Regulations. | M/s Suzlon |  | Pending | Pending
118/I/5 | Complete Outage of 220kV/33kV Gopalpura SS of SUZLON_KA | 13-04-2024 18:10 | - | M/s Suzlon to submit the protection performance indices without fail. | M/s Suzlon |  | Pending | Pending
118/I/6 | Complete Outage of 220kV/110kV Acharapakkam SS, 220kV/110kV Villupuram SS, 220kV/110kV Cuddalore SS, 220kV/110kV Thiruvanammali SS of TANTRANSCO and Multiple trippings at 200kV/110kV NNTPP Generating station | 14-04-2024 18:19 | - | NPCIL-MAPS to disable the overcurrent protection for 220kV lines.. | NPCIL MAPS |  | Pending | Pending
118/I/6 | Complete Outage of 220kV/110kV Acharapakkam SS, 220kV/110kV Villupuram SS, 220kV/110kV Cuddalore SS, 220kV/110kV Thiruvanammali SS of TANTRANSCO and Multiple trippings at 200kV/110kV NNTPP Generating station | 14-04-2024 18:19 | - | TANTRANSCO to review the Zone-3 Settings for Main-I & Main- II of all feeders at Singarpet end and check the load encroachment settings. | TANTRANSCO | cepc:TANTRANSCO: 20/01/2025 15:19:30: complied | Complied | Pending
118/II/2 | Tripping of 230kV Bus of 230kV/110kV Kadalangudy SS of TANTRANSCO | 22-04-2024 15:53 | 230kV/110kV Kadalangudy is operating with Single bus with Transfer Bus scheme at 230kV level. As per the reports submitted, the triggering incident was failure of Y-Phase CVT connected to 230kV Bus at Kadalangudy SS. Immediately, 230kV BBP operated and all the elements connected to the 230kV Bus tripped. 110kV Bus was intact during the event. At the same time, zone-1 protection operated in 230kV Neyveli Kadalangudy Line at Neyveli end and the line tripped at both ends. | NLC TS-2 to review the Zone settings at their end | NLC TS-2 | NLCI/TS2:NLCIL: 05/04/2025 15:08:34: Relay reach settings modified and relay testing done found in order. kept in observation. NLCI/TS2:NLCIL: 07/11/2025 10:10:12: After modification of reach settings, there is no mal-operation in past 6 months. Hence the point shall be closed. | Complied | Complied
118/II/2 | Tripping of 230kV Bus of 230kV/110kV Kadalangudy SS of TANTRANSCO | 22-04-2024 15:53 | 230kV/110kV Kadalangudy is operating with Single bus with Transfer Bus scheme at 230kV level. As per the reports submitted, the triggering incident was failure of Y-Phase CVT connected to 230kV Bus at Kadalangudy SS. Immediately, 230kV BBP operated and all the elements connected to the 230kV Bus tripped. 110kV Bus was intact during the event. At the same time, zone-1 protection operated in 230kV Neyveli Kadalangudy Line at Neyveli end and the line tripped at both ends. | TANTRANSCO to check the healthiness of other PTs in the 230kV Kadalngudy SS. | TANTRANSCO | cepc:TANTRANSCO: 20/01/2025 15:19:30: complied | Complied | Complied
118/I/5 | Complete Outage of 220kV/33kV Gopalpura SS of SUZLON_KA | 13-04-2024 18:10 | The triggering incident is the suspected failure of 220/33kV Auxiliary transformer at 220kV Gopalpura station at around 18:08:52.560. Due to the suspected DC supply failure at the station, the breakers failed to clear the fault. | 1.KPTCL to resolve the time sync issues of 220kV Tubinkere-Gopalpura line at Tubinkere end. 2.KPTCL to address the non-availability issue of SCADA SOE of 220kV Gopalpura and 220kV Tubinakere ends. | KPTCL |  | Pending | Pending
118/I/5 | Complete Outage of 220kV/33kV Gopalpura SS of SUZLON_KA | 13-04-2024 18:10 | The triggering incident is the suspected failure of 220/33kV Auxiliary transformer at 220kV Gopalpura station at around 18:08:52.560. Due to the suspected DC supply failure at the station, the breakers failed to clear the fault. | 1.M/s Suzlon to carry out third party protection audit of their Substation and submit report to SRPC within one month. Also to look into DR/EL issues at 220kV Gopalpura SS. 2.M/s Suzlon to submit the protection performance indices without fail. 3.M/s Suzlon to comply to CEA Regulations and substations to be managed by trained staff as per IEGC Regulations. | M/s Suzlon |  | Pending | Pending
118/I/6 | Complete Outage of 220kV/110kV Acharapakkam SS, 220kV/110kV Villupuram SS, 220kV/110kV Cuddalore SS, 220kV/110kV Thiruvanammali SS of TANTRANSCO and Multiple trippings at 200kV/110kV NNTPP Generating station | 14-04-2024 18:19 | The triggering incident is the tripping of 400/230kV NNTPP ICT-1 on PRD operation at 18:18:43.886 due to suspected moisture in PRD device. | 1.TANTRANSCO to review the Zone-3 Settings for Main-I & Main- II of all feeders at Singarpet end and check the load encroachment settings. | TANTRANSCO | cepc:TANTRANSCO: 20/01/2025 15:19:30: checked & complied | Complied | Complied
118/I/6 | Complete Outage of 220kV/110kV Acharapakkam SS, 220kV/110kV Villupuram SS, 220kV/110kV Cuddalore SS, 220kV/110kV Thiruvanammali SS of TANTRANSCO and Multiple trippings at 200kV/110kV NNTPP Generating station | 14-04-2024 18:19 | The triggering incident is the tripping of 400/230kV NNTPP ICT-1 on PRD operation at 18:18:43.886 due to suspected moisture in PRD device. | NPCIL-MAPS to disable the overcurrent protection for 220kV lines.. | NPCIL MAPS | NPCIL_MAPS:NPCIL: 05/07/2025 15:44:24: Disabling of over current planned along with line shutdown. It is planned to configure for alarm purpose only. ECD September 2025 NPCIL_MAPS:NPCIL: 04/09/2025 16:42:13: Over current protection was disabled in 220kV lines and recommendation is complied. NPCIL_MAPS:NPCIL: 07/01/2026 10:17:18: over current protection has been disabled in 220kV lines Acharapakkam feeder in the month of september 2025 during the line outage. For other lines it is in disable state | Complied | Complied
118/II/2 | Tripping of 230kV Bus of 230kV/110kV Kadalangudy SS of TANTRANSCO | 22-04-2024 15:53 | 230kV/110kV Kadalangudy is operating with Single bus with Transfer Bus scheme at 230kV level. As per the reports submitted, the triggering incident was failure of Y-Phase CVT connected to 230kV Bus at Kadalangudy SS. Immediately, 230kV BBP operated and all the elements connected to the 230kV Bus tripped. 110kV Bus was intact during the event. At the same time, zone 1 protection operated in 230kV Neyveli Kadalangudy Line at Neyveli end and the line tripped at both ends. | 1.NLC TS-2 to review the Zone settings at their end | NLCIL | NLCI/TS2:NLCIL: 05/04/2025 15:08:34: After modification in reach settings. relay testing done. found in order and kept in observation NLCI/TS2:NLCIL: 05/04/2025 15:17:16: zone setting reviewed. found in order NLCI/TS2:NLCIL: 07/11/2025 10:31:09: After modification of reach settings, there is no mal-operation past 6 months. Hence the point shall be closed. | Complied | Complied
118/II/2 | Tripping of 230kV Bus of 230kV/110kV Kadalangudy SS of TANTRANSCO | 22-04-2024 15:53 | 230kV/110kV Kadalangudy is operating with Single bus with Transfer Bus scheme at 230kV level. As per the reports submitted, the triggering incident was failure of Y-Phase CVT connected to 230kV Bus at Kadalangudy SS. Immediately, 230kV BBP operated and all the elements connected to the 230kV Bus tripped. 110kV Bus was intact during the event. At the same time, zone 1 protection operated in 230kV Neyveli Kadalangudy Line at Neyveli end and the line tripped at both ends. | 1.TANTRANSCO to check the healthiness of other PTs in the 230kV Kadalngudy SS. | TANTRANSCO | cepc:TANTRANSCO: 20/01/2025 15:19:30: complied | Complied | Complied
119/I/12 | Complete Outage of 400kV Kudgi SS of PGCIL SR-2, 400kV/220kV Koppal SS of WKTL, 400kV Kudgi Generating station of NTPC_Kudgi, 220kV Nadhihal Pooling Station, 220kV GM Navar SS, 220kV/110kV Bijapur SS, 220kV/110kV Indi SS, and 220kV/110kV Aheri220kV RSOPL, 220kV RSRPL, 220kV Ayana | 11-05-2024 15:13 | 400kV Koppal station is only connected to 400kV Kudgi (PG) through 2 feeders. 220kV RSRPL, 220kV RSOPL and 220kV Ayana is radially connected to 220kV Koppal station as shown in the figure. Hence 220kV RSOPL, 220kV RSRPL, 220kV Ayana power is being evacuated through 400kV Kudgi (PG)-Koppal-1&2 | 1.NTPC Kudgi to furnish the detailed report of the event and present in the next meeting. 2.NTPC Kudgi to review the average cycles for frequency measurement | NTPC - KUDGI | gpremshankar:NTPC: 05/08/2024 16:15:07: Detailed report submitted through mail after giving presentation in 120th PCSC meeting and Average cycles for freqency measurement revised to 10 cycles as discussed in 120th PCSC meeting | Complied | Pending
119/I/12 | Complete Outage of 400kV Kudgi SS of PGCIL SR-2, 400kV/220kV Koppal SS of WKTL, 400kV Kudgi Generating station of NTPC_Kudgi, 220kV Nadhihal Pooling Station, 220kV GM Navar SS, 220kV/110kV Bijapur SS, 220kV/110kV Indi SS, and 220kV/110kV Aheri220kV RSOPL, 220kV RSRPL, 220kV Ayana | 11-05-2024 15:13 | 400kV Koppal station is only connected to 400kV Kudgi (PG) through 2 feeders. 220kV RSRPL, 220kV RSOPL and 220kV Ayana is radially connected to 220kV Koppal station as shown in the figure. Hence 220kV RSOPL, 220kV RSRPL, 220kV Ayana power is being evacuated through 400kV Kudgi (PG)-Koppal-1&2 | 1.PGCIL SR-II/ Renew to check the requirements for lightning masts at Kudgi PG substation. 2.PGCIL SR-II and M/s Renew to furnish the relevant details for further analysis of the event. | PGCIL SR-2 | rtamcsr2:PGCIL (SR-II): 07/08/2024 15:18:59: As discussed in 119& 120 PCSC mentioned in MOM, point may be closed for PGCIL SR-2 | Complied | Pending
119/I/12 | Complete Outage of 400kV Kudgi SS of PGCIL SR-2, 400kV/220kV Koppal SS of WKTL, 400kV Kudgi Generating station of NTPC_Kudgi, 220kV Nadhihal Pooling Station, 220kV GM Navar SS, 220kV/110kV Bijapur SS, 220kV/110kV Indi SS, and 220kV/110kV Aheri220kV RSOPL, 220kV RSRPL, 220kV Ayana | 11-05-2024 15:13 | 400kV Koppal station is only connected to 400kV Kudgi (PG) through 2 feeders. 220kV RSRPL, 220kV RSOPL and 220kV Ayana is radially connected to 220kV Koppal station as shown in the figure. Hence 220kV RSOPL, 220kV RSRPL, 220kV Ayana power is being evacuated through 400kV Kudgi (PG)-Koppal-1&2 | M/s Renew to implement weakend infeed logic at Koppal end. | M/s Renew |  | Pending | Pending
122/IV/9 | 220KV-NAGARJUNASAGAR_AP-NAGARJUNASAGAR_TS-2 | 19-08-2024 18:35 | In the digital signal of Main-1 DR instead of R-phase open, B-Phase open was observed during the first fault, however tripping is in order. | APTRANSCO to rectify the digital signal issue at Nagarjunasagar (AP) end. | APTRANSCO | dee2sp:APTRANSCO: 04/10/2024 11:31:50: Completed on 30-09-2024. | Complied | Complied
122/IV/9 | 220KV-NAGARJUNASAGAR_AP-NAGARJUNASAGAR_TS-2 | 19-08-2024 18:35 | In the digital signal of Main-1 DR instead of R-phase open, B-Phase open was observed during the first fault, however tripping is in order. | TGGENCO to furnish the report on non-operation of Auto reclosure at TG end | TGGENCO | MRT.NSHES:TGGENCO: 26/10/2024 21:53:02: During the incident, Main-1 Relay (P442) has issued 1-ph trip and Auto Re-closure gets initiated. Whereas, Main-2 relay (REL 670) issued 3-ph trip due to relay configuration issue. Hence, Auto Re-closure configuration & settings in Main-2 Relay (REL 670) has modified as follows to enable for proper operation of Auto Re-closure for SLG faults: i) 1-phase trip will be issued for 1-ph faults (SLG) and Auto Re-closure will get initiated. ii) 3-phase trip will be issued for multi phase faults (LL & LLL) and Auto Re- closure will get blocked. MRT.NSHES:TGGENCO: 26/10/2024 22:00:05: During the incident, Main-1 Relay (P442) has issued 1-ph trip and Auto Re-closure gets initiated. Whereas, Main-2 relay (REL 670) issued 3-ph trip due to relay configuration issue. Hence, all 3 poles of CB opened and Auto Re-closure did not get operated. Hence, Auto Re-closure configuration & settings in Main-2 Relay (REL 670) has modified as follows to enable for proper operation of Auto Re-closure for SLG faults: i) 1-phase trip will be issued for 1-ph faults (SLG) and Auto Re-closure will get initiated. ii) 3-phase trip will be issued for multi phase faults (LL & LLL) and Auto Re- closure will get blocked. | Complied | Complied
124/I/15 | Tripping of 220kV Bus-4 at 400kV/220kV Koppal SS and Complete Outage of 220kV Renew_Surya_Ojas_Koppal_W and 220kV Ayana_Six_Koppal | 13-10-2024 15:01 | The triggering incident was 220kV Bus-4 fault at the Koppal end resulting in the tripping of all the elements connected to 220kV Bus-4 of 400kV/220kV Koppal SS. At the same time, 220kV-RSOPL_Koppal-1 and 220kV Ayana Koppal line tripped only at RSOPL and Ayana ends respectively due to suspected maloperation of SOTF protection. This resulted in the complete outage of 220kV Renew_Surya_Ojas_Koppal_W and 220kV Ayana_Six_Koppal. | Ayana Six, Koppal to furnish the detailed report regarding this event | M/s Ayana |  | Pending | Pending
124/I/15 | Tripping of 220kV Bus-4 at 400kV/220kV Koppal SS and Complete Outage of 220kV Renew_Surya_Ojas_Koppal_W and 220kV Ayana_Six_Koppal | 13-10-2024 15:01 | The triggering incident was 220kV Bus-4 fault at the Koppal end resulting in the tripping of all the elements connected to 220kV Bus-4 of 400kV/220kV Koppal SS. At the same time, 220kV-RSOPL_Koppal-1 and 220kV Ayana Koppal line tripped only at RSOPL and Ayana ends respectively due to suspected maloperation of SOTF protection. This resulted in the complete outage of 220kV Renew_Surya_Ojas_Koppal_W and 220kV Ayana_Six_Koppal. | RSOPL, Koppal and Ayana Six, Koppal to review the protection settings and to implement the settings in accordance with SR Protection Philosophy | RSOPL/ Renew |  | Pending | Pending
125/I/2 | Complete Outage of 220kV Vena_GadagPS | 22-10-2024 06:04 | As per the reports submitted, the triggering incident was R-N fault in 220kV Gadag Vena Line and the line tripped. Tripping of the only connected line led to complete outage of 220kV GadaPS. | 1. M/s Renew to reanalyse the event and submit the detailed report w.r.t the event along with DR or EL event details. The orderliness of Main-1 & Main-2 relays may also be checked. | 1.M/s Renew |  | Pending | Pending
125/I/2 | Complete Outage of 220kV Vena_GadagPS | 22-10-2024 06:04 | As per the reports submitted, the triggering incident was R-N fault in 220kV Gadag Vena Line and the line tripped. Tripping of the only connected line led to complete outage of 220kV GadaPS. | 2.M/s Vena Energy to consult with OEM to check the Auto reclosure settings, and make it functional. | 2.M/s Vena Energy |  | Pending | Pending
126/I/1 | Complete Outage of 230kV Sprng Pugalur | 17-11-2024 13:09 | As per the reports submitted, the triggering incident was LBB maloperation at 230kV Sprng Pugalur causing tripping of elements connected to 230kV Bus at 230kV Sprng Pugalur including 230kV Sprng Pugalur Pugalur line. Tripping of the only connected line led to complete outage of 230kV Sprng Pugalur | 1.M/s Spring Pugular to follow the SOP and furnish the revised SOP to SRPC & SRLDC. 2.M/s Spring Pugalur to check the healthiness of other insulators in the switchyard. | Spring Pugalur | ramakrishnang:Sprng Energy Ltd(Pugalur): 05/02/2025 11:11:54: 1.) 230KV Line Shutdown/Breakdown SOP submitted to SRPC & SRLDC. 2.) @30KV line Inspection carried out. Observation points were planned to attend on 19-02-2025 shutdown availing for annual PM activity. | Complied | Complied
126/I/1 | Complete Outage of 230kV Sprng Pugalur | 17-11-2024 13:09 | As per the reports submitted, the triggering incident was LBB maloperation at 230kV Sprng Pugalur causing tripping of elements connected to 230kV Bus at 230kV Sprng Pugalur including 230kV Sprng Pugalur Pugalur line. Tripping of the only connected line led to complete outage of 230kV Sprng Pugalur | PGCIL SR-II to rectify DR time synchronization at Pugalur end | PGCIL SR-2 | rtamcsr2:PGCIL (SR-II): 05/03/2025 11:52:03: As discussed .Not applicable for PGCIL SR-2, However Time synch checked @ Pugalur PGCIL SR-2 , Found ok. | Complied | Complied
126/I/6 | Complete Outage of 400kV Greenko CPSS, 400kV AMGEPL Wind Plant, and 400kV Pinnapuram PSP | 04-12-2024 17:44 | During antecedent conditions, 400kV Greenko CPSS, 400kV AMGEPL Wind Plant and 400kV Pinnapuram PSP were radially connected to 765kV/400kV Kurnool SS through 400kV Greenko CPSS Kurnool line-1. Triggering incident was inadvertent tripping of 400kV Greenko CPSS Kurnool line-1 at Greenko CPSS end during testing activity. This resulted in the complete outage of 400kV Greenko CPSS, 400kV AMGEPL Wind Plant, and 400kV Pinnapuram PSP. | 1.M/s AMEGPL to furnish detailed report regarding the Island formation. SRLDC may further analyse the cause for the island frequency of 42 Hz. 2.AMGEPL to rectify the DR time sync issue. | M/s AMEGPL | ravishekhawat:AMGEPL: 06/02/2025 11:22:50: Our response to SRPC was submitted on January 31, 2025, accompanied by the events recorded in the Wind Turbine connected as of that date. Detailed report under preparation, will be shared soon. | Complied | Complied
126/I/6 | Complete Outage of 400kV Greenko CPSS, 400kV AMGEPL Wind Plant, and 400kV Pinnapuram PSP | 04-12-2024 17:44 | During antecedent conditions, 400kV Greenko CPSS, 400kV AMGEPL Wind Plant and 400kV Pinnapuram PSP were radially connected to 765kV/400kV Kurnool SS through 400kV Greenko CPSS Kurnool line-1. Triggering incident was inadvertent tripping of 400kV Greenko CPSS Kurnool line-1 at Greenko CPSS end during testing activity. This resulted in the complete outage of 400kV Greenko CPSS, 400kV AMGEPL Wind Plant, and 400kV Pinnapuram PSP. | 1.M/s Greenko to furnish detailed report regarding the Island formation. SRLDC may further analyse the cause for the island frequency of 42 Hz. 2.M/s Greenko to follow SOP and furnish the revised SOP to SRPC & SRLDC. | M/s Greenko | kvchenchaiah:GREENKO: 21/02/2025 16:39:03: SOP is prepared & updated for Operation & Maintenance AP01 IREP PSP & CPSS GIS 400kV & Same was shared via email to Srldc & Srpc dated 21-02-2025. | Complied | Complied
128/I/5 | Complete Outage of 230kV JSW_Dharapuram-1 | 31-01-2025 15:27 | The triggering incident was tripping of 230kV Karur JSW_Dharapuram-1 line at Karur end on DEF protection and DT was received at Dharapuram end. Tripping of the only connected line led to complete outage of 230kV JSW_Dharapuram Wind Station. | 1.ATL/Karur to furnish the Detailed User report of the event 2.ATL/Karur to strictly adhere to the specified timelines as per Regulatory provision 3.ATL/Karur to review and revise the DEF settings at their end 4.ATL/Karur to consult OEM regarding the DEF operation during this incident and provide an update to SRPC & SRLDC 5.ATL/Karur to standardise DR as per FOLD recommendations | ATL/Karur |  | Pending | Pending
128/I/5 | Complete Outage of 230kV JSW_Dharapuram-1 | 31-01-2025 15:27 | The triggering incident was tripping of 230kV Karur JSW_Dharapuram-1 line at Karur end on DEF protection and DT was received at Dharapuram end. Tripping of the only connected line led to complete outage of 230kV JSW_Dharapuram Wind Station. | 1.JSWEL to rectify the time synch issue at JSW-Dharapuram | JSWEL |  | Pending | Pending
128/III/8 | Multiple tripping at 230kV MAPS | 01-02-2025 07:35 | In the antecedent conditions 230kV SP Koil-Oragadam was under forced outage and 230kV SP Koil-Veerapuram was under idle charged condition. Hence 230kV SP Koil is connected with 2 lines of MAPS and 1 line to Omega. As per the reports submitted, the triggering incident is the B-N fault in 230kV SP Koil-Omega line, during the auto reclose attempt, 230kV MAPS-SP Koil-1&2 tripped on Earth Fault protection. | 1.MAPS to furnish detailed analysis of the event 2.MAPS to review the DEF settings of all transmission lines | MAPS | NPCIL_MAPS:NPCIL: 05/06/2025 12:43:24: the setting are under review by HQ design NPCIL_MAPS:NPCIL: 05/07/2025 15:41:26: Revised settings were received from HQ. It will be implemented during shutdown. ECD. September 2025 NPCIL_MAPS:NPCIL: 07/01/2026 10:24:28: DEF setting coordination is under review. | Pending | Pending
128/III/8 | Multiple tripping at 230kV MAPS | 01-02-2025 07:35 | In the antecedent conditions 230kV SP Koil-Oragadam was under forced outage and 230kV SP Koil-Veerapuram was under idle charged condition. Hence 230kV SP Koil is connected with 2 lines of MAPS and 1 line to Omega. As per the reports submitted, the triggering incident is the B-N fault in 230kV SP Koil-Omega line, during the auto reclose attempt, 230kV MAPS-SP Koil-1&2 tripped on Earth Fault protection. | 1.TANTRANSCO to review the time sync issues at Oragadam and SP Koil SS | TANTRANSCO | cepc:TANTRANSCO: 07/05/2025 13:20:17: Checked Both SP koil & Orgadam end GPS is working & Time SYNC also found in order | Complied | Pending
129/I/1 | Complete outage of 220kV/110kV Kavoor SS, 220kV/110kV MSEZ(Bajpe) SS, tripping of 220kV Bus-1 of 220kV/110kV Kemar SS of KPTCL and tripping of 400kV Bus-1 and 220kV Bus-1 and 2 at 400kV/220kV UPCL of Adani | 19-02-2025 08:55 | During antecedent conditions, there was bus split operation at 220kV Kemar SS. The triggering incident was opening of Main Bay of 400kV/220kV ICT 1 at UPCL for planned maintenance coincided with the LV breaker tripping, leading to an overload on ICT 2. The UPCL SPS operated and tripped U 2 despite 400kV lines being in service, and 400kV/220kV ICT 2 later tripped on backup OC protection, causing complete outage of 220kV/110kV Kavoor SS, 220kV/110kV MSEZ (Bajpe) SS, tripping of 220kV Bus 1 of 220kV/110kV Kemar SS of KPTCL and tripping of 400kV Bus-1 and 220kV Bus-1 and 2 at 400kV/220kV UPCL of Adani. | APL-Udupi to furnish the detailed draft report. | APL-Udupi |  | Pending | Pending
129/I/1 | Complete outage of 220kV/110kV Kavoor SS, 220kV/110kV MSEZ(Bajpe) SS, tripping of 220kV Bus-1 of 220kV/110kV Kemar SS of KPTCL and tripping of 400kV Bus-1 and 220kV Bus-1 and 2 at 400kV/220kV UPCL of Adani | 19-02-2025 08:55 | During antecedent conditions, there was bus split operation at 220kV Kemar SS. The triggering incident was opening of Main Bay of 400kV/220kV ICT 1 at UPCL for planned maintenance coincided with the LV breaker tripping, leading to an overload on ICT 2. The UPCL SPS operated and tripped U 2 despite 400kV lines being in service, and 400kV/220kV ICT 2 later tripped on backup OC protection, causing complete outage of 220kV/110kV Kavoor SS, 220kV/110kV MSEZ (Bajpe) SS, tripping of 220kV Bus 1 of 220kV/110kV Kemar SS of KPTCL and tripping of 400kV Bus-1 and 220kV Bus-1 and 2 at 400kV/220kV UPCL of Adani. | SRLDC to furnish the detailed draft report. | SRLDC | ArthiV~1776856274:SRLDC: 02/07/2025 18:50:21: Detailed Report re-sent on 15-05-2025 with the required modifications and updating of remedial actions. The point may be closed. ArthiV~1776856274:SRLDC: 02/07/2025 18:50:46: Detailed Report re-sent on 15-05-2025 with the required modifications and updating of remedial actions. The point may be closed. | Complied | Pending
129/I/7 | Complete outage of 230kV/110kV Hosur_TN SS of TANTRANSCO and de-energization of Bus-2 of 220kV/66kV Yerrandahalli SS of KPTCL | 03-03-2025 18:17 | As per the reports submitted, 230kV Hosur_TN Hosur_PG line-1 and 2 tripped at 230kV Hosur_TN SS due to suspected maloperation of SPS at 230kV Hosur_TN SS which was envisaged during the radial assistance from 230kV Hosur_TN SS to 230kV Yerandahally SS during the shutdown period of 400kV Somanahally Mylasandra line. At the same time, tripping of 110kV feeders on operation of df/dt st-1 and st-2 at 230kV Hosur_TN SS were also reported. Subsequently, at 18:36hrs, YB-N fault was observed in 230kV Mettur_Auto Hosur line becuase of jumper cut at Loc No. 394. At both ends, zone-1 protection operated and the line tripped. Tripping of only connected source led to complete outage of 230kV/110kV Hosur_TN SS of TANTRANSCO and de energization of Bus-2 of 220kV/66kV Yerrandahalli SS of KPTCL. | 1.KPTCL/TANTRANSCO to resolve the non-availaibility of SCADA SOE from Hosur (TN) and Yerandahally SS. 2.KPTCL to furnish load relief details and resaons for non operation of SPS at their end. 3.SPS will be discussed in Special Meeting | KPTCL |  | Pending | Pending
129/I/7 | Complete outage of 230kV/110kV Hosur_TN SS of TANTRANSCO and de-energization of Bus-2 of 220kV/66kV Yerrandahalli SS of KPTCL | 03-03-2025 18:17 | As per the reports submitted, 230kV Hosur_TN Hosur_PG line-1 and 2 tripped at 230kV Hosur_TN SS due to suspected maloperation of SPS at 230kV Hosur_TN SS which was envisaged during the radial assistance from 230kV Hosur_TN SS to 230kV Yerandahally SS during the shutdown period of 400kV Somanahally Mylasandra line. At the same time, tripping of 110kV feeders on operation of df/dt st-1 and st-2 at 230kV Hosur_TN SS were also reported. Subsequently, at 18:36hrs, YB-N fault was observed in 230kV Mettur_Auto Hosur line becuase of jumper cut at Loc No. 394. At both ends, zone-1 protection operated and the line tripped. Tripping of only connected source led to complete outage of 230kV/110kV Hosur_TN SS of TANTRANSCO and de energization of Bus-2 of 220kV/66kV Yerrandahalli SS of KPTCL. | 1.TANTRANSCO to verify and confirm the relay settings/SPS logic implementation to be same as per the approved settings by HQ. | TANTRANSCO | cepc:TANTRANSCO: 07/05/2025 13:18:51: Any trip flex logic modified on 03-03-2025 revised logic will be implemented on or before 31.05.2025 | Complied | Pending
129/IV/11 | 400KV-KAIGA-GUTTUR-2 | 09-03-2025 05:30 | As per the reports submitted, the triggering incident was BN fault in the line. At both ends the line tripped on operation of Zone-1 distance protection. A/R didnt get operated. Tripping needs review. | 1.KPTCL & NPCIL Kaiga to furnish the reason for unsuccessful A/R. 2. KPTCL & NPCIL Kaiga to rectify the DR time sync issues. | KPTCL |  | Pending | Pending
129/IV/11 | 400KV-KAIGA-GUTTUR-2 | 09-03-2025 05:30 | As per the reports submitted, the triggering incident was BN fault in the line. At both ends the line tripped on operation of Zone-1 distance protection. A/R didnt get operated. Tripping needs review. | 1.KPTCL & NPCIL Kaiga to furnish the reason for unsuccessful A/R. 2. KPTCL & NPCIL Kaiga to rectify the DR time sync issues. | NPCIL Kaiga | KGS34:NPCIL: 05/05/2025 11:12:30: Initially fault was initiated in C-Phase and subsequently fault got extended to A&B phases also. CB-02B Auto reclose operation is not initiated due to fault in all three phases, as per scheme. KGS34:NPCIL: 05/05/2025 11:51:51: The DR time stamping of NPCIL Kaiga is correct and matching with PMU time stamping. Time sync issue is not applicable for NPCIL-Kaiga Recommendation may be closed. | Complied | Pending
130/I/10 | Complete Outage of 400kV/110kV Udangudi SS. | 01-04-2025 11:59 | During antecedent conditions, 400kV Ottapidaram Udangudi line-1 was under shutdown. As per the reports submitted, while carrying out precommissioning testing on 400kV Udangudi Ottapidaram LIne-1, 400kV Ottapidaram Udangudi line-1 line-2 got tripped at Ottapidaram end. Tripping of the only connected line led to complete outage of 400kV/110kV Udangudi SS. | 1.TANTRANSCO / TNPGCL to follow SOP during testing activities. 2.TANTRANSCO /TNPGCL to rectify the SCADA SOE issues at Udangusi SS | TANTRANSCO / TNPGCL | cepc:TANTRANSCO: 29/08/2025 10:53:53: 1.Letter addressed to Udangudi Head Quarters to follow SOP. 2. related to TNPGCL cepc:TANTRANSCO: 02/02/2026 14:17:03: Related to TNPGCL | Complied | Complied
130/I/10 | Complete Outage of 400kV/110kV Udangudi SS. | 01-04-2025 11:59 | During antecedent conditions, 400kV Ottapidaram Udangudi line-1 was under shutdown. As per the reports submitted, while carrying out precommissioning testing on 400kV Udangudi Ottapidaram LIne-1, 400kV Ottapidaram Udangudi line-1 line-2 got tripped at Ottapidaram end. Tripping of the only connected line led to complete outage of 400kV/110kV Udangudi SS. | SRLDC to furnish revised report incorporating all the details. | SRLDC | ArthiV~1776856274:SRLDC: 02/07/2025 19:07:16: Modified grid event report on the Complete Outage of 400kV/110kV Udangudi SS on 01-04-2025 at 11:59 was sent on 23-05-2025 | Complied | Complied
130/IV/10 | 400KVNIZAMABA DSHANKARA PALLY-2 | 03-04-2025 13:52 | As per the reports furnished, the triggering incident was a BN fault in the line at a distance of 15km from Shankarapally end. At Nizamabad end, fault was sensed in Zone-1, tie CB A/R operated and line was holding. However, Main CB B pole opened but didn't reclose, and subsequently Y and R poles of main CB opened on operation of pole discrepancy. At Shankarapally end, fault was sensed in Zone-1 and A/R not operated. Non- operation of A/R at Shankarapally end and non-operation of main CB at Nizamabad end need review. | 1.PGCIL SR-1 to review Non-operation of Main CB A/R | PGCIL SR-1 | Venkatasai:PGCIL (SR-I): 31/05/2025 12:52:27: At Nizamabad SS, Shankarpally Line1, Main BCU AR initiation cycle operated as per the logic. But it was observed that due to Communication failure Led blinking on the BCU front panel, the AR did not happen resulting in the tripping of Main Bay on PD. Further, all the IEDs that were publishing Goose to the BCU, communication patch cables were removed and reestablished. Now, the Communication fail alarm was reset on the BCU Front panel. Issue is rectified. | Complied | Complied
130/IV/10 | 400KVNIZAMABA DSHANKARA PALLY-2 | 03-04-2025 13:52 | As per the reports furnished, the triggering incident was a BN fault in the line at a distance of 15km from Shankarapally end. At Nizamabad end, fault was sensed in Zone-1, tie CB A/R operated and line was holding. However, Main CB B pole opened but didn't reclose, and subsequently Y and R poles of main CB opened on operation of pole discrepancy. At Shankarapally end, fault was sensed in Zone-1 and A/R not operated. Non- operation of A/R at Shankarapally end and non-operation of main CB at Nizamabad end need review. | 1.TGTRANSCO to review the Non- Operation of A/R at Shankarapally end. | TGTRANSCO | deprotection1:TGTRANSCO: 03/06/2025 15:06:48: OEM is yet to visit the site for rectification. deprotection1:TGTRANSCO: 02/03/2026 11:46:53: OEM visited the site and rectified the AR issue at Shankarpally end on 10-07-2025 | Complied | Complied
131/I/8 | Complete Outage 220kV Hiriyur ZENATARIS_PSS | 26-04-2025 00:35 | Triggering incident was fault in 220KVHIRIYURHiriyur ZENATARIS_PSS1. Due to the tripping of only connected line, there was complete outage of 220kV Hiriyur ZENATARIS_PSS. | 2. SRLDC to collect the test reports whenever PSSG forum recommended to conduct any tests/ inspections in relay settings recommendations. | SRLDC | ArthiV~1776856274:SRLDC: 02/07/2025 18:03:13: FTC procedure is being followed. Entities to furnish reports to SRLDC/SRPC if any inspections/tests are recommended. SRLDC to collect such reports, if any. | Complied | Complied
131/I/8 | Complete Outage 220kV Hiriyur ZENATARIS_PSS | 26-04-2025 00:35 | Triggering incident was fault in 220KVHIRIYURHiriyur ZENATARIS_PSS1. Due to the tripping of only connected line, there was complete outage of 220kV Hiriyur ZENATARIS_PSS. | Zentaris and PGCIL SR-II were informed to adhere to the recommendations given by PSSG forum. | M/s Zentarius & PGCIL SR-II | rtamcsr2:PGCIL (SR-II): 04/07/2025 16:58:12: Recommendation of CT polarity correction has been implemented and confirmed by Ecoren energy | Complied | Complied
131/III/3 | NCTPS VALLUR MUL TRIPPING | 24-04-2025 21:20 | As per the reports submitted, the triggering incident was B phase jumper cut in 400kV NCTPS Vallur Line-2 at location no.3 from NCTPS end. At NCTPS end, DEF protection operated and DT was sent to Vallur end and line tripped at both ends. At the same time, DEF protection operated in 400kV NCTPS Vallur Line-1 at NCTPS end in Main 1 Relay (P 543). IT is reported that at NCTPS end, directionality of DEF was inadverntantly converter to Non direnctional. As the Neutral current was around 320A, DEF | NTECL Vallur & TANGEDCO to furnish the detailed report | NTECL Vallur & TNPGCL | BrajeshKumarPandey:NTECL: 19/08/2025 16:03:33: detailed report already sent | Complied | Complied
132/I/4 | Complete Outage of 230kV/110kV Ulundurpet SS and tripping of 230kV Bus-2 at 230kV/110kV Cuddalore SS | 01-06-2025 15:20 | In the antecedent conditions, 230kV Cuddalore-Veerapuram-1&2 and 230kV Ulundurpet-Shankarapuram lines were in idle charged condition, and bus split condition was observed at 230kV Cuddalore where in 230kV Bus-2 is conected to Ulundurpet and STCMS and hence Bus-2 of Cuddalore and Ulundupet was fed through 230kV NLCTS2- Ulundurpet and 230kV STCMS-Cuddalore lines. The triggering incident is the B-N fault in 230kV Cuddalore-STCMS line. The line tripped at both ends. During the same fault, 230kV NLCTS2-Ulundurpet line tripped at NLC TS2 on Z3. With the tripping of both the lines (230kV Cuddalore-STCMS and 230kV NLCTS2-Ulundurpet) led to the Complete Outage 230kV/110kV Ulundurpet SS and tripping of 230kV Bus-2 at 230kV/110kV Cuddalore SS | NLC TS-2 to carry out Transplay of the event and furnish the report | NLC TS-2 | NLCI/TS2:NLCIL: 07/11/2025 10:27:40: Trans play conducted setting to be reviewed | Complied | Complied
132/I/4 | Complete Outage of 230kV/110kV Ulundurpet SS and tripping of 230kV Bus-2 at 230kV/110kV Cuddalore SS | 01-06-2025 15:20 | In the antecedent conditions, 230kV Cuddalore-Veerapuram-1&2 and 230kV Ulundurpet-Shankarapuram lines were in idle charged condition, and bus split condition was observed at 230kV Cuddalore where in 230kV Bus-2 is conected to Ulundurpet and STCMS and hence Bus-2 of Cuddalore and Ulundupet was fed through 230kV NLCTS2- Ulundurpet and 230kV STCMS-Cuddalore lines. The triggering incident is the B-N fault in 230kV Cuddalore-STCMS line. The line tripped at both ends. During the same fault, 230kV NLCTS2-Ulundurpet line tripped at NLC TS2 on Z3. With the tripping of both the lines (230kV Cuddalore-STCMS and 230kV NLCTS2-Ulundurpet) led to the Complete Outage 230kV/110kV Ulundurpet SS and tripping of 230kV Bus-2 at 230kV/110kV Cuddalore SS | NLC TS-2 to rectify DR time sync issues at their Station | NLC TS-2 | NLCI/TS2:NLCIL: 07/11/2025 10:27:40: The feasibility check for time synchronization with existing relays is under progress. | Complied | Complied
132/I/4 | Complete Outage of 230kV/110kV Ulundurpet SS and tripping of 230kV Bus-2 at 230kV/110kV Cuddalore SS | 01-06-2025 15:20 | In the antecedent conditions, 230kV Cuddalore-Veerapuram-1&2 and 230kV Ulundurpet-Shankarapuram lines were in idle charged condition, and bus split condition was observed at 230kV Cuddalore where in 230kV Bus-2 is conected to Ulundurpet and STCMS and hence Bus-2 of Cuddalore and Ulundupet was fed through 230kV NLCTS2- Ulundurpet and 230kV STCMS-Cuddalore lines. The triggering incident is the B-N fault in 230kV Cuddalore-STCMS line. The line tripped at both ends. During the same fault, 230kV NLCTS2-Ulundurpet line tripped at NLC TS2 on Z3. With the tripping of both the lines (230kV Cuddalore-STCMS and 230kV NLCTS2-Ulundurpet) led to the Complete Outage 230kV/110kV Ulundurpet SS and tripping of 230kV Bus-2 at 230kV/110kV Cuddalore SS | NLC TS-2 to review the Distance settings for Ulundurpet line | NLC TS-2 | NLCI/TS2:NLCIL: 07/11/2025 10:27:40: Trans play report conducted, the report will be mailed | Complied | Complied
132/I/4 | Complete Outage of 230kV/110kV Ulundurpet SS and tripping of 230kV Bus-2 at 230kV/110kV Cuddalore SS | 01-06-2025 15:20 | In the antecedent conditions, 230kV Cuddalore-Veerapuram-1&2 and 230kV Ulundurpet-Shankarapuram lines were in idle charged condition, and bus split condition was observed at 230kV Cuddalore where in 230kV Bus-2 is conected to Ulundurpet and STCMS and hence Bus-2 of Cuddalore and Ulundupet was fed through 230kV NLCTS2- Ulundurpet and 230kV STCMS-Cuddalore lines. The triggering incident is the B-N fault in 230kV Cuddalore-STCMS line. The line tripped at both ends. During the same fault, 230kV NLCTS2-Ulundurpet line tripped at NLC TS2 on Z3. With the tripping of both the lines (230kV Cuddalore-STCMS and 230kV NLCTS2-Ulundurpet) led to the Complete Outage 230kV/110kV Ulundurpet SS and tripping of 230kV Bus-2 at 230kV/110kV Cuddalore SS | TANTRANSCO to rectify DR time sync issues at SCTMS | TANTRANSCO | cepc:TANTRANSCO: 29/08/2025 10:47:24: Informed to STCMS. They replied that at present GPS provision is not available. cepc:TANTRANSCO: 18/09/2025 13:15:32: STCMS replied vide email dated 10.09.2025, After assessment of feasibility in the existing distance relays, GPS will be synchronized before Dec 2025 cepc:TANTRANSCO: 03/10/2025 17:02:45: Time line requested by STCMS upto 31.12.2025 cepc:TANTRANSCO: 06/11/2025 10:43:47: Time line requested by STCMS upto 31.12.2025 cepc:TANTRANSCO: 24/11/2025 14:27:30: STCMS has reported vide email dated 18.11.2025 that realtime clock of the switch yard protection relay system has been synchronized with GPS. The existing switchyard protection relay, main.2 (Micom P442) has been configured with the SANDS make GPS system separately for all four line feeders. cepc:TANTRANSCO: 29/12/2025 10:47:57: Complied by STCMS cepc:TANTRANSCO: 02/02/2026 14:15:23: Complied | Complied | Complied
133/I/2 | Complete outage of 220kV Ayana_Six_Kopal | 05-07-2025 12:13 | As per the reports submitted, the triggering incident was an R N fault on the 220kV AyanaKoppal line and the line tripped. Tripping of the only connected line led to complete outage of 220kV Ayana_Six_Koppal. | M/s Ayana to furnish the reason for non operation of Auto reclosure at their end. | M/s Ayana Koppal |  | Pending | Pending
133/I/2 | Complete outage of 220kV Ayana_Six_Kopal | 05-07-2025 12:13 | As per the reports submitted, the triggering incident was an R N fault on the 220kV AyanaKoppal line and the line tripped. Tripping of the only connected line led to complete outage of 220kV Ayana_Six_Koppal. | M/s Indigrid to furnish detail report regarding the non operation of A/r and I>4 trip signal seen at Koppal end | M/s Indigrid |  | Pending | Pending
133/I/6 | Complete Outage of 220kV MK Hubli SS of KPTCL | 12-07-2025 13:13 | As per the reports submitted, the triggering incident was R-N fault in 220V Narendra Hubli Line-2 and the line tripped. At the same time, 220kV Narendra MK Hubli Line-1 tripped only at Narendra end on DEF protection. Since, MK Hubli is radially fed through 220kV Narendra MK Hubli Line-1&2, tripping of both lines led to complete outage of 220kV MK Hubli SS. | KPTCL to rectify the DR time sync issue at MK Hubli End. | KPTCL |  | Pending | Pending
133/I/6 | Complete Outage of 220kV MK Hubli SS of KPTCL | 12-07-2025 13:13 | As per the reports submitted, the triggering incident was R-N fault in 220V Narendra Hubli Line-2 and the line tripped. At the same time, 220kV Narendra MK Hubli Line-1 tripped only at Narendra end on DEF protection. Since, MK Hubli is radially fed through 220kV Narendra MK Hubli Line-1&2, tripping of both lines led to complete outage of 220kV MK Hubli SS. | KPTCL to rectify the SCADA SOE issue at MK Hubli end. | KPTCL |  | Pending | Pending
133/I/6 | Complete Outage of 220kV MK Hubli SS of KPTCL | 12-07-2025 13:13 | As per the reports submitted, the triggering incident was R-N fault in 220V Narendra Hubli Line-2 and the line tripped. At the same time, 220kV Narendra MK Hubli Line-1 tripped only at Narendra end on DEF protection. Since, MK Hubli is radially fed through 220kV Narendra MK Hubli Line-1&2, tripping of both lines led to complete outage of 220kV MK Hubli SS. | PGCIL SR-2 to check the DEF logic for all relays at Narendra 220kV SS | PGCIL SR-2 | rtamcsr2:PGCIL (SR-II): 03/09/2025 06:21:31: DEF Settings and Logics are verified in all 220 kV lines @ Narendra SS on 28.07.2025. Found In order. | Complied | Pending
134/I/1 | Complete Outage of 220kV CSS_CS_PTR and 220kV KSPPL of Kleio_Solar | 31-07-2025 21:19 | 220kV CSS_CS_PTR (Kleio Solar CSS) and 220kV KSPPL are being radially connected through 220KV-KOPPAL-CSS_KS_PTR-1. As per the reports submitted, while carrying out bay changeover at 220kV Koppal SS, 220KV-KOPPAL-CSS_KS_PTR-1 line tripped. Tripping of the only connected line led to complete outage of 220kV CSS_CS_PTR and 220kV KSPPL | M/s Indigrid to follow SOP during Maintenance / testing activities. | M/s Indigrid |  | Pending | Pending
134/I/1 | Complete Outage of 220kV CSS_CS_PTR and 220kV KSPPL of Kleio_Solar | 31-07-2025 21:19 | 220kV CSS_CS_PTR (Kleio Solar CSS) and 220kV KSPPL are being radially connected through 220KV-KOPPAL-CSS_KS_PTR-1. As per the reports submitted, while carrying out bay changeover at 220kV Koppal SS, 220KV-KOPPAL-CSS_KS_PTR-1 line tripped. Tripping of the only connected line led to complete outage of 220kV CSS_CS_PTR and 220kV KSPPL | M/s Indigrid to furnish detailed report on the Event to SRPC & SRLDC. | M/s Indigrid |  | Pending | Pending
134/I/1 | Complete Outage of 220kV CSS_CS_PTR and 220kV KSPPL of Kleio_Solar | 31-07-2025 21:19 | 220kV CSS_CS_PTR (Kleio Solar CSS) and 220kV KSPPL are being radially connected through 220KV-KOPPAL-CSS_KS_PTR-1. As per the reports submitted, while carrying out bay changeover at 220kV Koppal SS, 220KV-KOPPAL-CSS_KS_PTR-1 line tripped. Tripping of the only connected line led to complete outage of 220kV CSS_CS_PTR and 220kV KSPPL | M/s Kleio Solar to rectify the DR Time sync issues at 220kV KSPPL | M/s Kleio Solar |  | Pending | Pending
134/I/2 | Complete Outage of 220kV JSW Savalperi of JSW_RE | 02-08-2025 05:42 | 220kV JSW_Savalperi is connected to TTGS only through 220kV JSW_Savalperi-TTGS line. The triggering incident was B-N fault in the line. The line tripped on differential protection at both ends. Tripping of the only line connected to JSW_Savalperi led to the Complete Outage of 220kV JSW Savalperi | JSW-Savalperi to verify the AR logic at TTGS & JSW end | JSW-Savalperi | jeganraj:JSW Vilathikulam: 07/11/2025 13:39:09: our team is planning to verify the above functionality at Both Ends with support of Relay OEM team. completion by 15th Dec-25 | Pending | Pending
134/I/2 | Complete Outage of 220kV JSW Savalperi of JSW_RE | 02-08-2025 05:42 | 220kV JSW_Savalperi is connected to TTGS only through 220kV JSW_Savalperi-TTGS line. The triggering incident was B-N fault in the line. The line tripped on differential protection at both ends. Tripping of the only line connected to JSW_Savalperi led to the Complete Outage of 220kV JSW Savalperi | PGCIL SR-2 to verify the AR logic at TTGS & JSW end | PGCIL SR-2 | jeganraj:JSW Vilathikulam: 07/11/2025 13:39:09: our team is planning to verify the above functionality at Both Ends with support of Relay OEM team. completion by 15th Dec-25 | Pending | Pending
134/III/1 | Multiple Trippings at Koppal | 24-07-2025 08:31 | As per the reports submitted, the triggering incident was R-N fault in 400KV-KOPPAL-KUDGI_PG-1. At both ends, the fault was sensed in zone-1. A/R operated and the line tripped on persistent fault. At the same time, 400KV/220KV KOPPAL-ICT-4 tripped due to issue in 64IV PSL logic. At the same time, 220KV/33KV KSPPL-ICT-1 &2 tripped on single phase over flux protection instantaneously for around 1.24 V/F ratio as per the settings. Consequently, the R-N fault during A/R in 400KV-KOPPAL-KUDGI_PG-1 was also sensed in 400KV-KOPPAL-KUDGI_PG-2 suspected zone-1 over reach at Kudgi end. A/R operated and was successful. The line was holding at Koppal end. | M/s Indigrid to furnish detailed report on the tripping of 400/220 kV Koppal ICT-4 on PSL issue | M/s Indigrid |  | Pending | Pending
134/III/1 | Multiple Trippings at Koppal | 24-07-2025 08:31 | As per the reports submitted, the triggering incident was R-N fault in 400KV-KOPPAL-KUDGI_PG-1. At both ends, the fault was sensed in zone-1. A/R operated and the line tripped on persistent fault. At the same time, 400KV/220KV KOPPAL-ICT-4 tripped due to issue in 64IV PSL logic. At the same time, 220KV/33KV KSPPL-ICT-1 &2 tripped on single phase over flux protection instantaneously for around 1.24 V/F ratio as per the settings. Consequently, the R-N fault during A/R in 400KV-KOPPAL-KUDGI_PG-1 was also sensed in 400KV-KOPPAL-KUDGI_PG-2 suspected zone-1 over reach at Kudgi end. A/R operated and was successful. The line was holding at Koppal end. | M/s Kleio Solar to consult the OEM and submit a detailed report regarding the tripping of ICTs on instantaneous overflux protection. | M/s Kleio Solar |  | Pending | Pending
136/I/3 | Complete Outage of 400kV Guttur SS of KPTCL | 27-09-2025 09:30 | As per the reports submitted, the triggering incident was R-N fault in 400kv Bus-2. Immediately, 400kV Bus-1 and Bus-2 operated and all elements connected to the buses tripped. This led to complete outage of 400kV Guttur SS. | 1.NPCIL-KGS to furnish the reasons and remedial mesures taken for Zone-1 overreach observed during the incident. 2.NPCIL-KGS to configure the DR as per FOLD committee recommendations | NPCIL-KAIGA | KGS34:NPCIL: 04/12/2025 14:40:54: 1.The Distance protection scheme of KAIGA GUTTUR LINE-2 is reviewed and found correct only. Scheme is given as PUPZ2. Mutual compensation is given (values are kZm 371.0 e-3 and kZm Angle -5.3 deg). The reading on the event in both M1 & M2 relays are checked and found that the fault current was high around 1.75 kA and 2.0 kA respectively. 2. DR settings are under review as per FOLD committee recommendation. | Pending | Pending
136/I/3 | Complete Outage of 400kV Guttur SS of KPTCL | 27-09-2025 09:30 | As per the reports submitted, the triggering incident was R-N fault in 400kv Bus-2. Immediately, 400kV Bus-1 and Bus-2 operated and all elements connected to the buses tripped. This led to complete outage of 400kV Guttur SS. | KPTCL to rectify the DR time sync issue at Guttur end. | KPTCL |  | Pending | Pending
136/I/12 | Complete Outage of 220kV Chalakurthy SS, 220kV Puttamgandi SS, 220kV Puliyantanda SS of TGTRANSCO | 08-10-2025 21:36 | 220V PuliyantandaSS and 220kV Puttamgandi SS are being radially fed from 220kV Chalakurthy SS. 220kV Chalakurthy SS is operating with Single bus configuration. As per the reports submitted, the triggering incident was R N fault in 220kV Chalakurthy KM Palli Line 1 while charging the line from Chalakurthy end due to Rphase discs flashover and conductor fallen on Yphase cross arm in the line. At Chalakurthy end, the fault was sensed in zone 1 & SOTF operated and the line tripped. At the same time, 220kV Chalakurthy BB operated on suspected CT saturation in 220kV Chalakurthy KM Palli Line 1. All elements connected to 220kV Chalakurthy Bus tripped leading complete outage of 220kV Chalakurthy SS which inturn led to complete outage of 220kV Puliyantanda SS and 220kV Puttamgandi SS. | 1.APTRANSCO to rectify DR time sync at Nagarjunsagar. | APTRANSCO | dee2sp:APTRANSCO: 08/12/2025 09:44:16: Rectified on 06-12-2025. | Complied | Complied
136/I/12 | Complete Outage of 220kV Chalakurthy SS, 220kV Puttamgandi SS, 220kV Puliyantanda SS of TGTRANSCO | 08-10-2025 21:36 | 220V PuliyantandaSS and 220kV Puttamgandi SS are being radially fed from 220kV Chalakurthy SS. 220kV Chalakurthy SS is operating with Single bus configuration. As per the reports submitted, the triggering incident was R N fault in 220kV Chalakurthy KM Palli Line 1 while charging the line from Chalakurthy end due to Rphase discs flashover and conductor fallen on Yphase cross arm in the line. At Chalakurthy end, the fault was sensed in zone 1 & SOTF operated and the line tripped. At the same time, 220kV Chalakurthy BB operated on suspected CT saturation in 220kV Chalakurthy KM Palli Line 1. All elements connected to 220kV Chalakurthy Bus tripped leading complete outage of 220kV Chalakurthy SS which inturn led to complete outage of 220kV Puliyantanda SS and 220kV Puttamgandi SS. | 1.TGTRANSCO to consult OEM regarding the operation of BBP for through faults. 2.TGTRANSCO to rectify DR time sync at Chalakurthy SS . 3.TGTRANSCO may make arrangements for double bus operation at Chalakurthy SS. 4.TGTRANSCO to follow SOP and is suggested to take quick remedial actions on trippings to avoid unwanted trippings for same issues. 5.Inputs to the relays such as CT-Knee point voltage fed to the relay may be comprehensively verified in the internal protection audit and the same may be captured in the SOP as well. | TGTRANSCO | deprotection1:TGTRANSCO: 03/02/2026 11:05:43: 1. As informed suspected bus fault for which Bus bar has operated. 2.Time synchronization completed. 3. At this stage double bus bar is not feasible due to field constraints. 4.Informed field staff to follow SOPs 5.Informed the field staff to incorporate the knee points voltages of CTs in the PUs. The points may be dropped. | Complied | Complied
139/I/1 | Complete Outage of 220kV Koramangala, 220kV NIMHANS, 220kV HSR, 220kV Nagnathapura and Tripping of 220kV Mylasandra Bus-2, 400kV Bus-1 & Bus-2 of Mylasandra SS of KPTCL | 25-12-2025 12:45 | Due to LC on the 400 kV Somanahalli Mylasandra line, the 220 kV Mylasandra substation was operated in a bus-split configuration with 220kV EDC NIMHANS and 220kV HSR-EPIP under idle charged condition. Under this condition, 220 kV Koramangala, NIMHANS, Nagnathapura, and HSR were radially fed from 220 kV Mylasandra Bus 2. The 400 kV Kolar Mylasandra line was energising both 400 kV Bus 1 and Bus 2 at Mylasandra, which in turn supplied 220 kV Mylasandra Bus-2 through ICT1, ICT2, and ICT3. Consequently, 220 kV Koramangala, NIMHANS, HSR, and Nagnathapura were radially connected to 220 kV Mylasandra Bus2 with the 400 kV Kolar Mylasandra line as the radial source of supply. The triggering incident was BN fault in 400kV Kolar Mylasandra line and the line tripped. This led to loss of power supply to all radial connected buses and 220kV stations. The triggering incident was BG fault in 400kV Kolar Mylasandra line and the line tripped. This led to loss of power supply to all radial connected buses and 220kV stations. | KPTCL to review the Main-1 distance zone reaches at Mylasandra end. | KPTCL | Puspha:KPTCL: 05/03/2026 13:34:54: The settings extracted from the relays are compared with the settings approved by this office earlier, no mismatch is observed. There is no change in network configuration also. In view of the above, to update the existing settings to PMMS database DMNS ticket has been raised(Ticket no. 6021) | Complied | Pending
139/I/1 | Complete Outage of 220kV Koramangala, 220kV NIMHANS, 220kV HSR, 220kV Nagnathapura and Tripping of 220kV Mylasandra Bus-2, 400kV Bus-1 & Bus-2 of Mylasandra SS of KPTCL | 25-12-2025 12:45 | Due to LC on the 400 kV Somanahalli Mylasandra line, the 220 kV Mylasandra substation was operated in a bus-split configuration with 220kV EDC NIMHANS and 220kV HSR-EPIP under idle charged condition. Under this condition, 220 kV Koramangala, NIMHANS, Nagnathapura, and HSR were radially fed from 220 kV Mylasandra Bus 2. The 400 kV Kolar Mylasandra line was energising both 400 kV Bus 1 and Bus 2 at Mylasandra, which in turn supplied 220 kV Mylasandra Bus-2 through ICT1, ICT2, and ICT3. Consequently, 220 kV Koramangala, NIMHANS, HSR, and Nagnathapura were radially connected to 220 kV Mylasandra Bus2 with the 400 kV Kolar Mylasandra line as the radial source of supply. The triggering incident was BN fault in 400kV Kolar Mylasandra line and the line tripped. This led to loss of power supply to all radial connected buses and 220kV stations. The triggering incident was BG fault in 400kV Kolar Mylasandra line and the line tripped. This led to loss of power supply to all radial connected buses and 220kV stations. | PGCIL SR-II to update the Main-1 relay settings at Kolar end in DMNS portal. | PGCIL SR-II | rtamcsr2:PGCIL (SR-II): 07/03/2026 10:11:30: Dear Sir, Mylasandra Line data Updated in DMNS Portal on 07.03.2026 Vide Ticket ID- 6022 is created. Request to Close the status of pending data. | Complied | Pending
139/I/1 | Complete Outage of 220kV Koramangala, 220kV NIMHANS, 220kV HSR, 220kV Nagnathapura and Tripping of 220kV Mylasandra Bus-2, 400kV Bus-1 & Bus-2 of Mylasandra SS of KPTCL | 25-12-2025 12:45 | Due to LC on the 400 kV Somanahalli Mylasandra line, the 220 kV Mylasandra substation was operated in a bus-split configuration with 220kV EDC NIMHANS and 220kV HSR-EPIP under idle charged condition. Under this condition, 220 kV Koramangala, NIMHANS, Nagnathapura, and HSR were radially fed from 220 kV Mylasandra Bus 2. The 400 kV Kolar Mylasandra line was energising both 400 kV Bus 1 and Bus 2 at Mylasandra, which in turn supplied 220 kV Mylasandra Bus-2 through ICT1, ICT2, and ICT3. Consequently, 220 kV Koramangala, NIMHANS, HSR, and Nagnathapura were radially connected to 220 kV Mylasandra Bus2 with the 400 kV Kolar Mylasandra line as the radial source of supply. The triggering incident was BN fault in 400kV Kolar Mylasandra line and the line tripped. This led to loss of power supply to all radial connected buses and 220kV stations. The triggering incident was BG fault in 400kV Kolar Mylasandra line and the line tripped. This led to loss of power supply to all radial connected buses and 220kV stations. | SRLDC to study and give detailed report on the findings of the event for operation of TOR. | SRLDC | ArthiV~1776856274:SRLDC: 04/04/2026 17:50:34: The same has been further analyzed and the operation of AR at Mylasandra has been checked. A revised detailed report has been sent for the event on 01-04-2026. | Pending | Pending
139/III/5 | 400KV-ALAMATHY-NCTPS_STAGE_II-1 | 01-01-2026 02:22 | As per the reports submitted, the triggering incident was Y-N fault in the line. The fault distance from Alamathy end was 15.71kms and from NCTPS_STAGE_II end was 12.04kms. At Alamathy end, the fault was sensed in Zone-1 and 3ph trip without AR operation. At NCTPS_STAGE_II end, the fault was sensed in Zone-1 Distance protection operated AR operated and tripped due to persistent fault. | TANTRANSCO to review the AR Scheme & Direct trip scheme at Alamathy end. | TANTRANSCO | cepc:TANTRANSCO: 04/03/2026 15:34:01: Line clear awaited cepc:TANTRANSCO: 30/03/2026 16:06:26: Direct trip initiated due to DTPC issue. It is programmed to replace the defective DTPC with spare one during next Line clear. | Pending | Pending
139/III/5 | 400KV-ALAMATHY-NCTPS_STAGE_II-1 | 01-01-2026 02:22 | As per the reports submitted, the triggering incident was Y-N fault in the line. The fault distance from Alamathy end was 15.71kms and from NCTPS_STAGE_II end was 12.04kms. At Alamathy end, the fault was sensed in Zone-1 and 3ph trip without AR operation. At NCTPS_STAGE_II end, the fault was sensed in Zone-1 Distance protection operated AR operated and tripped due to persistent fault. | TNPGCL to review the logic for adaptive AR at NCTPS Stage II end. | TNPGCL |  | Pending | Pending
140/I/3 | Complete Outage of 765kV NCPS of TANTRANSCO and NCTPS ST3 of TANGEDCO | 24-01-2026 16:32 | 765kV NCTPS is connected radially to 765kV NCPS through 765kV NCPS-NCTPS-1&2 which is in turn radially connected to Ariyalur with 765kV Ariyalur NCPS-1&2. In the antecedent condition, 765kV Ariyalur NCPS-1 was under outage and 765kV NCPS and NCTPS ST3 were only radially connected through 765kV Ariyalur NCPS-2. The triggering incident is the Y-ph fault in the line leading to the tripping of the line. Tripping of the only connected line led to the Complete Outage of 765kV NCPS of TANTRANSCO and NCTPS ST3 of TANGEDCO and the running unit of NCTPS ST3 tripped and led to a generation loss of around 800MW | TANTRANSCO to verify the A/R reclaim time of all feeders at Ariyalur SS. | TANTRANSCO | cepc:TANTRANSCO: 30/03/2026 16:06:26: reclaim time revised in all feeders on 18.02.2026. Complied | Pending | Pending
140/I/3 | Complete Outage of 765kV NCPS of TANTRANSCO and NCTPS ST3 of TANGEDCO | 24-01-2026 16:32 | 765kV NCTPS is connected radially to 765kV NCPS through 765kV NCPS-NCTPS-1&2 which is in turn radially connected to Ariyalur with 765kV Ariyalur NCPS-1&2. In the antecedent condition, 765kV Ariyalur NCPS-1 was under outage and 765kV NCPS and NCTPS ST3 were only radially connected through 765kV Ariyalur NCPS-2. The triggering incident is the Y-ph fault in the line leading to the tripping of the line. Tripping of the only connected line led to the Complete Outage of 765kV NCPS of TANTRANSCO and NCTPS ST3 of TANGEDCO and the running unit of NCTPS ST3 tripped and led to a generation loss of around 800MW | TNPGCL to submit detailed report on Tripping of generator during the event | TNPGCL |  | Pending | Pending
140/I/4 | Complete outage of 230kV Betam and NTPC Ettayapuram | 30-01-2026 14:47 | 230kV NTPC Ettayapuram and Betam is connected to TTGS radially. The triggering incident is the Y-B fault in the 230kV TTGS-NTPC Ettayapuram line due to conductor snapping leading to the tripping the line on line differential protection. During the same time, the fault was sensed in Z1 at Betam end only and 3ph tripped. Tripping of the radial lines led to the complete outage of 230kV Betam and NTPC Ettayapuram | 1. PGCIL SR-II to periodic maintaince activities at TTGS SS. 2. PGCIL SR-II to report equipment failure to CEA. | PGCIL SR-II |  | Pending | Pending
140/I/4 | Complete outage of 230kV Betam and NTPC Ettayapuram | 30-01-2026 14:47 | 230kV NTPC Ettayapuram and Betam is connected to TTGS radially. The triggering incident is the Y-B fault in the 230kV TTGS-NTPC Ettayapuram line due to conductor snapping leading to the tripping the line on line differential protection. During the same time, the fault was sensed in Z1 at Betam end only and 3ph tripped. Tripping of the radial lines led to the complete outage of 230kV Betam and NTPC Ettayapuram | M/s Betam Wind to consult OEM and submit report regarding the over reach observed during the event. | M/s Betam Wind |  | Pending | Pending
140/I/9 | Complete outage of 220kV Chintur of APTRANSCO and Tripping of Bus-2 at Lower Sileru of APGENCO | 11-02-2026 14:08 | In the antecedent conditions, at 220kV Lower Sileru is under Bus split condition where in 220kV Lower Sileru-Bommuru, 220kV Lower Sileru-Donkarayi is in Bus-1 and 220kV Lower Sileru-Asupaka and 220kV Lower Sileru-Chintur is in Bus-2 and 220kV Lower Sileru-Asupaka was under planned outage due to Tree Cutting works leading to Bus-2 being radially connected through 220kV Lower Sileru-Chintur which was inturn connected through 220kV Lower Sileru-Chintur-BG Kothur segment. The triggering incident is the R-B fault in 220kV Chintur-BG Kothur line and tripping of the line led to the Complete outage of 220kV Chintur of APTRANSCO and Tripping of Bus-2 at Lower Sileru of APGENCO. | APGENCO to provide the detailed report on the genarator frequency/speed variations during the incident and generator tripping values for over frequency protection. | APGENCO |  | Pending | Pending
140/I/9 | Complete outage of 220kV Chintur of APTRANSCO and Tripping of Bus-2 at Lower Sileru of APGENCO | 11-02-2026 14:08 | In the antecedent conditions, at 220kV Lower Sileru is under Bus split condition where in 220kV Lower Sileru-Bommuru, 220kV Lower Sileru-Donkarayi is in Bus-1 and 220kV Lower Sileru-Asupaka and 220kV Lower Sileru-Chintur is in Bus-2 and 220kV Lower Sileru-Asupaka was under planned outage due to Tree Cutting works leading to Bus-2 being radially connected through 220kV Lower Sileru-Chintur which was inturn connected through 220kV Lower Sileru-Chintur-BG Kothur segment. The triggering incident is the R-B fault in 220kV Chintur-BG Kothur line and tripping of the line led to the Complete outage of 220kV Chintur of APTRANSCO and Tripping of Bus-2 at Lower Sileru of APGENCO. | APTRANSCO to validate the relay settings of Chintur SS in the PDMS portal. | APTRANSCO | dee2sp:APTRANSCO: 07/04/2026 14:53:22: On 25/03/26, settings calculations were emailed to SRPC along with the following information, Zone-3 element in P444 relay act as Zone-4 protection and Zone-4 element in P444 relay act as Zone-5 element. Hence, the calculated settings are inline with the protection philosophy. At Chinturu end, Main-2 relay (ABB make REL670) settings are communicated to PRDC by MRT wing/Rajamahendravaram and same was confirmed with PRDC. | Complied | Pending
140/I/9 | Complete outage of 220kV Chintur of APTRANSCO and Tripping of Bus-2 at Lower Sileru of APGENCO | 11-02-2026 14:08 | In the antecedent conditions, at 220kV Lower Sileru is under Bus split condition where in 220kV Lower Sileru-Bommuru, 220kV Lower Sileru-Donkarayi is in Bus-1 and 220kV Lower Sileru-Asupaka and 220kV Lower Sileru-Chintur is in Bus-2 and 220kV Lower Sileru-Asupaka was under planned outage due to Tree Cutting works leading to Bus-2 being radially connected through 220kV Lower Sileru-Chintur which was inturn connected through 220kV Lower Sileru-Chintur-BG Kothur segment. The triggering incident is the R-B fault in 220kV Chintur-BG Kothur line and tripping of the line led to the Complete outage of 220kV Chintur of APTRANSCO and Tripping of Bus-2 at Lower Sileru of APGENCO. | TGTRANSCO to validate the relay settings of BG Kothuru SS in the PDMS portal. | TGTRANSCO | deprotection1:TGTRANSCO: 04/04/2026 14:36:00: Already verified and the settings are found to be in order. The same is mailed to SRPC on 04-04-2026. The point may be dropped. | Complied | Pending
140/I/10 | Complete outage of 220kV Chintur of APTRANSCO and Tripping of Bus-2 at Lower Sileru of APGENCO | 13-02-2026 12:20 | In the antecedent conditions, at 220kV Lower Sileru is under Bus split condition where in 220kV Lower Sileru-Bommuru, 220kV Lower Sileru-Donkarayi is in Bus-1 and 220kV Lower Sileru-Asupaka and 220kV Lower Sileru-Chintur is in Bus-2 and 220kV Chintur-BG Kothur was under planned outage due to Tree Cutting works leading to Bus-2 being radially connected through 220kV Lower Sileru-Asupaka. The triggering incident is the Y-G fault in 220kV Lower Sileru-Asupaka and tripping of the line led to the Complete outage of 220kV Chintur of APTRANSCO and Tripping of Bus-2 at Lower Sileru of APGENCO. | APGENCO to review the A/R logic at Lower Sileru. | APGENCO |  | Pending | Pending
140/I/10 | Complete outage of 220kV Chintur of APTRANSCO and Tripping of Bus-2 at Lower Sileru of APGENCO | 13-02-2026 12:20 | In the antecedent conditions, at 220kV Lower Sileru is under Bus split condition where in 220kV Lower Sileru-Bommuru, 220kV Lower Sileru-Donkarayi is in Bus-1 and 220kV Lower Sileru-Asupaka and 220kV Lower Sileru-Chintur is in Bus-2 and 220kV Chintur-BG Kothur was under planned outage due to Tree Cutting works leading to Bus-2 being radially connected through 220kV Lower Sileru-Asupaka. The triggering incident is the Y-G fault in 220kV Lower Sileru-Asupaka and tripping of the line led to the Complete outage of 220kV Chintur of APTRANSCO and Tripping of Bus-2 at Lower Sileru of APGENCO. | TGTRANSCO to configure the DR at Asupaka SS asper the FOLD recommendations. | TGTRANSCO |  | Pending | Pending
140/ii/2 | Tripping of 400kV Bus-1 of Simhadri TPS of NTPC | 30-01-2026 11:08 | The triggering incident is the Y-ph CT failure of 412Bay (Main Bay connected to 400kV Simhadri-Kalpakka-3) at Simhadri leading to Bus Bar protection operation and tripping of all the breakers connected to 400kV Bus-1 of Simhadri TPS. During which due to the delay in tripping of TEED protection led to the delay in clearing of the fault and also Z2 was sensed in remote end. During the same time 400kV Khammam-Kalpakka tripped only at Khammam end on Z2 due to the delay in clearing of fault. Subsequently 400kV Simhadri-Kalpakka-3 line tripped on Z2 at Kalpakka end. After which due to OPGW cable cut 400kV Simhadri-Kalpakka-4 and 400kV Gazuwaka-Kalpakka tripped. During the event Hinduja unit 2 tripped due to flame failure. | 1.APTRANSCO to indentify all such locations of towers, where separate earth wire is not layed. and to immediately start laying earth wire in such locations. Specifically on tower spans numbered 5 &6, 6&7, and 7&8, works for laying of separate earth wire on the tower should be taken up on immediate basis. 2.APTRANSCO to take appropriate actions in avoiding the interruptions in power communication through OPGW for known and rectifiable issues. | APTRANSCO | dee2sp:APTRANSCO: 07/04/2026 14:53:22: 1. 400kV/O&M wing informed that , laying of earth wire between loc.5-6 in line-3 was done on 10/03/26,laying of earth wire between loc 3-4 of Kalapaka- Vemagiri line completed on 13/03/26, in between loc 7-8 earth wire is existing. 2. To avoid OPGW/Earth wire failures on the existing EHT lines, alternative Optical route path was established with ADSS cable and is in service for both voice/protection. | Pending | Pending
140/ii/2 | Tripping of 400kV Bus-1 of Simhadri TPS of NTPC | 30-01-2026 11:08 | The triggering incident is the Y-ph CT failure of 412Bay (Main Bay connected to 400kV Simhadri-Kalpakka-3) at Simhadri leading to Bus Bar protection operation and tripping of all the breakers connected to 400kV Bus-1 of Simhadri TPS. During which due to the delay in tripping of TEED protection led to the delay in clearing of the fault and also Z2 was sensed in remote end. During the same time 400kV Khammam-Kalpakka tripped only at Khammam end on Z2 due to the delay in clearing of fault. Subsequently 400kV Simhadri-Kalpakka-3 line tripped on Z2 at Kalpakka end. After which due to OPGW cable cut 400kV Simhadri-Kalpakka-4 and 400kV Gazuwaka-Kalpakka tripped. During the event Hinduja unit 2 tripped due to flame failure. | 1.NTPC Simhadri to pursue the root cause analysis report with the OEM (GE) for recurring surface tracking failures of GE ICTs and share with SRPC/SRLDC and NTPC is suggested all the procedures need to be strictly followed while performing hotline washing. 2.NTPC Simhadri to conduct comprehensive testing of TEED protection for Simhadri-Kalpakka lines 2, 3, and 4 and confirm actual operating time and behaviour in coordination with APTRNASCO. 3.NTPC simhadri to verify and ensure that TEED protection is configured to transmit Direct Transfer Trip (DT) to remote end, in addition to the existing tie-breaker based DT logic. 4.NTPC may explore planned offline cleaning (with line shutdown) as an alternative to hotline washing for the Kalpakka lines. 5.NTPC Simhadri to share final third-party protection audit report (ERDS) with SRPC and SRLDC upon receipt. | NTPC Simhadri |  | Pending | Pending
140/ii/2 | Tripping of 400kV Bus-1 of Simhadri TPS of NTPC | 30-01-2026 11:08 | The triggering incident is the Y-ph CT failure of 412Bay (Main Bay connected to 400kV Simhadri-Kalpakka-3) at Simhadri leading to Bus Bar protection operation and tripping of all the breakers connected to 400kV Bus-1 of Simhadri TPS. During which due to the delay in tripping of TEED protection led to the delay in clearing of the fault and also Z2 was sensed in remote end. During the same time 400kV Khammam-Kalpakka tripped only at Khammam end on Z2 due to the delay in clearing of fault. Subsequently 400kV Simhadri-Kalpakka-3 line tripped on Z2 at Kalpakka end. After which due to OPGW cable cut 400kV Simhadri-Kalpakka-4 and 400kV Gazuwaka-Kalpakka tripped. During the event Hinduja unit 2 tripped due to flame failure. | SRLDC agreed to carry out a fresh short circuit modelling study (single-phase and three-phase fault levels) for the Simhadri/Kalpakka region incorporating the current network, to determine whether equipment ratings require upgrading and for further review of protection settings. | SRLDC | ArthiV~1776856274:SRLDC: 04/04/2026 17:48:05: The same has been communicated to the concerned team. A meeting may be scheduled with NTPC Simhadri in this regards for the requirements and the same will be updated further | Pending | Pending
141/I/1 | Complete outage of 230kV SR Pudur SS of TANTRANSCO SS. | 22-02-2026 04:15 | As per the reports submitted, 230kV SR Pudur SS is operating with single bus configuration. At 4:15hrs Y-G fault was observed in 230kv SR Pudur Sanganeri line and the line tripped. At 4:57hrs, R-G fault was observed in 230kV Kudankulam SR Pudur line and the line tripped. After tripping of both 230kV ines, 230kV SR Pudur bus was charged through 110kV lines from Udayathur and Sanganeri SS. Eventually, 110kV lines tripped on over loading at remote ends and this led to complete outage of 230kV SR Pudur SS. | 1.TANTRANSCO to revise A/r dead time of all feeders at 230kV Sanganeri SS to 1 Sec. 2.TANTRANSCO to ensure Double bus operation of all 220kV & Substations. 3.TANTRANSCO to rectify the DR time sychronization issue at SR Pudur 4.TANTRANSCO to furnish DR at Sangareni end during the incident | TANTRANSCO |  | Pending | Pending
141/I/1 | Complete outage of 230kV SR Pudur SS of TANTRANSCO SS. | 22-02-2026 04:15 | As per the reports submitted, 230kV SR Pudur SS is operating with single bus configuration. At 4:15hrs Y-G fault was observed in 230kv SR Pudur Sanganeri line and the line tripped. At 4:57hrs, R-G fault was observed in 230kV Kudankulam SR Pudur line and the line tripped. After tripping of both 230kV ines, 230kV SR Pudur bus was charged through 110kV lines from Udayathur and Sanganeri SS. Eventually, 110kV lines tripped on over loading at remote ends and this led to complete outage of 230kV SR Pudur SS. | NPCIL KKNPP to furnish DR at KKNPP end during the incident | NPCIL KKNPP |  | Pending | Pending
141/II/1 | Tripping of 400kV Bus-2 of 400kV Yelahanka_PG SS of PGCIL SR-2 | 12-02-2026 07:26 | As per the reports submitted, the triggering incident was Y-G fault in 400kV Bus-2 of 400kV Yelahanka_PG SS. Immediately, 400kV Bus-2 BBP operated and all the elements connected to the bus tripped | KPTCL to rectify the DR time sync issue at Neelamanga SS and Yelahanka SS. | KPTCL |  | Pending | Pending
141/II/1 | Tripping of 400kV Bus-2 of 400kV Yelahanka_PG SS of PGCIL SR-2 | 12-02-2026 07:26 | As per the reports submitted, the triggering incident was Y-G fault in 400kV Bus-2 of 400kV Yelahanka_PG SS. Immediately, 400kV Bus-2 BBP operated and all the elements connected to the bus tripped | PGCIL SR-II to report Equipment failure to CEA. | PGCIL SR-II |  | Pending | Pending
141/II/1 | Tripping of 400kV Bus-2 of 400kV Yelahanka_PG SS of PGCIL SR-2 | 12-02-2026 07:26 | As per the reports submitted, the triggering incident was Y-G fault in 400kV Bus-2 of 400kV Yelahanka_PG SS. Immediately, 400kV Bus-2 BBP operated and all the elements connected to the bus tripped | SRLDC to furnsih the reasons for Inphase currents observed during the event and necessary remedial actions to be taken to the forum. | SRLDC |  | Pending | Pending
141/II/4 | Tripping of 400kV Bus-1 and 2 at Simhadri TPS of NTPC | 25-02-2026 16:03 | The triggering incident is the R-ph CT tracking in 400KV-SIMHADRI-KALPAKKA-4 main bay leading to BBP operation and tripping of all the main breakers connected to Bus-2 and 400KV-SIMHADRI-KALPAKKA-4. Subsequently, after around 5s, Bus-1 BBP operated due to R-ph CT tracking in 400KV-SIMHADRI-KALPAKKA-3 main bay leading to tripping of all elements connected to 400kV Bus-1 and 2 at Simhadri TPS of NTPC. This led to the tripping of Unit-2 and generation loss of around 420MW. During the event, 400kV Bus-3 and 4 were in service at Simhadri TPS | 1.NTPC Simhadri to expecite the process of replacing porcelien insulator with Polymer insulator. 2.NTPCSimhadri to verify the AR logic at their end and ensure single pole AR operation. | NTPC-Simhadri |  | Pending | Pending
141/II/4 | Tripping of 400kV Bus-1 and 2 at Simhadri TPS of NTPC | 25-02-2026 16:03 | The triggering incident is the R-ph CT tracking in 400KV-SIMHADRI-KALPAKKA-4 main bay leading to BBP operation and tripping of all the main breakers connected to Bus-2 and 400KV-SIMHADRI-KALPAKKA-4. Subsequently, after around 5s, Bus-1 BBP operated due to R-ph CT tracking in 400KV-SIMHADRI-KALPAKKA-3 main bay leading to tripping of all elements connected to 400kV Bus-1 and 2 at Simhadri TPS of NTPC. This led to the tripping of Unit-2 and generation loss of around 420MW. During the event, 400kV Bus-3 and 4 were in service at Simhadri TPS | APTRANSCO to expedite the OPGW replacement works on Simhadri Kalpakka Line. | APTRANSCO |  | Pending | Pending
141/IV/2 | 400KV-KAIGA-GUTTUR-2 | 24-02-2026 15:45 | As per the reports submitted, the triggering incident is the B-G fault in the line. At both ends the fault was sensed in Z1 and at both ends AR did not operate and 3ph tripped. | KPTCL to review the non-operation of Auto reclosure at Guttur end of 400KV-KAIGA-GUTTUR-line 2. | KPTCL |  | Pending | Pending
141/IV/2 | 400KV-KAIGA-GUTTUR-2 | 24-02-2026 15:45 | As per the reports submitted, the triggering incident is the B-G fault in the line. At both ends the fault was sensed in Z1 and at both ends AR did not operate and 3ph tripped. | NPCIL Kaiga to review the non-operation of Auto reclosure at Kaiga end of 400KV-KAIGA-GUTTUR- line 2. | NPCIL Kaiga |  | Pending | Pending
ANDHRA PRADESH
109/II/5 | Tripping of 220kV Bus-2 of 220kV Vizag Switching Station of APTRANSCO | 17-06-2023 13:43:00 | The triggering incident was YN fault in 220kV Bus-2 at 220kV Vizag Switching Station. Immediately, 220kV Bus-2 BBP operated and all the elements connected to 220kV Bus-2 tripped. | 1.APTRANSCO to furnish all DR/ELs for all the trippings involved in the grid event to SRPC & SRLDC within a week time. | APTRANSCO | dee2sp:APTRANSCO: 08/09/2023 11:20:38: Detailed report was submitted by APTRANSCO on 07/09/2023 . | Complied | Complied
109/II/5 | Tripping of 220kV Bus-2 of 220kV Vizag Switching Station of APTRANSCO | 17-06-2023 13:43:00 | The triggering incident was YN fault in 220kV Bus-2 at 220kV Vizag Switching Station. Immediately, 220kV Bus-2 BBP operated and all the elements connected to 220kV Bus-2 tripped. | 2.APTRANSCO HQ to have site visits of all substations involved in the grid event and submit a detailed analysis report to SRPC within 15 days. 3.PSAG will be formed to analyze the event further after receipt of details and detailed analysis report from APTRANSCO HQ. | APTRANSCO |  | Complied | Complied
107/II/5 | . | 09-02-2023 11.00.00 PM | . | APGENCO to verify the distance protection at VTPS end and revert back | APGENCO | APG_NTTPS4001:APGENCO: 14/02/2025 12:15:44: Settings verified with the settings given by APTRANSCO and found ok. Relay tested for reach settings and found ok | Complied | Complied
108/II/17 | . | 15-05-2023 15:14 | . | APGENCO/VTPS to implement the logic (with consultation of OEM) - CB opening/close status to LBB so that the LBB operates only when CB fails to open. | APGENCO | APG_NTTPS2202:APGENCO: 01/06/2024 09:36:37: As per the recommendations of SRPC we have referred the problem to M/s SIEMENS. M/s SIEMENS could not give an ideal solution. Each logic is having its own merits and demerits. If we put a CB contact in series with the LBB initiation, mal-operation of CB auxiliary switch may lead to non-operation LBB and it may damage the Generator. We have seen the cases where CB status has shown OPEN but current persisted. We cannot depend upon Aux. CB contact, so we would like to keep the logic unchanged. In the 108th PCSC meeting forum felt the same. Hence it is requested to drop the point. | Complied | Complied
113/I/8 | Complete Outage of 220kV Tallapalli SS of APTRANSCO | 13-11-2023 07:59 | As per the reports submitted, the triggering incident is the R-phase CVT failure for 220kV Tallapally Srisailam RB 2 at Tallapally end. Since VT fuse fail was observed before the eventual failure of the CVT in the line, the zone protection was blocked in the line. The fault in R-phase was observed to have a fault current of 32kA and developed into a RY-N fault after around 250ms. Since the zone protection was blocked in the line of 220kV Tallapally Srisailam RB 2, the lines tripped at remote end on Z2 or in Z4 at Tallapally end. 1. 220kv Tallapally Srisailam RB Line2 was holding at Tallapally end and tripped at Srisailam RB end on Z2 time trip 2. 220kV Nagarjunasagar AP Nagarjunasagar TS 1,2,3 tripped at Tallapally end on Z4 and at Nagarjunasagar TS in Z2 time trip 3. 220kV Talapally Chalakurthy only tripped at Tallapally end on Z4 and was holding at Chalakurthy end 4. 220kV Talapally Piduguralla-1 and 220kV Talapally VTPS did not trip at Tallapally end and tripped only at remote end 5. 220kV Tallapalli Rentachintala and 220kV Tallapalli Srisailam 1 tripped at Tallapalli end on Z4 The 400/220kV N Sagar ICTs were feeding the fault while sensing Z2 (Back up impedance) and have sensed after around 600ms, the ICTs tripped on Z2. With the tripping of all the elements connected to 220kV Tallapalli SS led to complete outage of the station. | APTRANSCO to enable Zone - 4 in both Main-I and Main-II protection of all lines connected to Tallapally SS | APTRANSCO | dee2sp:APTRANSCO: 01/01/2024 15:51:15: At Tallapalli end, Reverse zone is already in enabled condition for 3 no.s feeders ( i.e. Inapararajupalli-1&2,VTPS feeders) in both Main-1&2 relays. For remaining 7 feeders ( N.Sagar-1,2,3, Srisailam-1,2, Rentachintala & Chalakurthy feeders) reverse zone ( i.e. Zone-5) in Main-1 (Sifang make CSC101 relay) was kept in disabled condition and in enabled condition in Main-2 relay. The same was kept enabled in the above seven no.s feeders( N.Sagar-1,2,3, Srisailam-1,2, Rentachintala & Chalakurthy feeders) in the Main-I relays (Sifang make CSC101 relay) on 14/12/2023.Now, reverse zone is in enabled condition for all Main-1&2 relays at Tallapalli end. | Complied | Complied
114/II/4 | 400 kV KRISHNAPATNAM - NELLORE -2 | 05-12-2023 01:58 | Line was tripped due to over voltage stage-1 operation at the KRISHNAPATNAM end and DT was received at the NELLORE-AP end. Tripping is not in order since R-phase voltage is higher than Y and B phases and maloperation of Over voltage protection is suspected. | APGENCO to check the OVR settings and submit the compliance report. | APGENCO | APP_SDSTPS4002:APGENCO: 05/06/2025 11:07:17: checked the settings & found as per SRPC recommendations. Obseved CVT error in R-phase. Line CT R-phase is replaced with new one to reduce voltage error. APP_SDSTPS4002:APGENCO: 05/06/2025 11:08:06: checked the settings & found as per SRPC recommendations. Obseved CVT error in R-phase. Line CT R-phase is replaced with new one to reduce voltage error. APP_SDSTPS4002:APGENCO: 19/01/2026 15:36:04: CVT IS REPLACED NOW VOLTAGE MEASURING ERROR IS NULL.. PLEASE DROP THESE POINT | Complied | Complied
114/III/3 | 400 kV KRISHNAPATNAM - RACHAGUNERI LINE-2 | 10-Dec-2023 12:45:00 | As per reports submitted, the triggering incident was B-N fault in the line. At both ends, the line was tripped on Zone-1 distance protection. At SDSTPS end, AR operated but again the line tripped due to persistent fault. At Rachagunneri end, AR not operated. Non-operation of AR at Rachagunneri end needs review. | APTRANSCO to test Main-2 ABB make REL670 relay | APTRANSCO | dee2sp:APTRANSCO: 19/01/2024 11:48:55: On 10/01/2024 LC availed on 400kV Rachagunneri-Krishnapatnam line-2 and modified the Main-2(REL670) relay configuration suitably and carried out complete testing of all zones in each phase and found satisfactory. Auto reclosure function also tested for Zone-1 and ZCOM for both Main & Tie CB and found satisfactory. | Complied | Complied
115/II/2 | Tripping of Bus-2 at 220kV Lower Sileru of APGENCO | 22-12-2023 15:03 | In the antecedent conditions U1 and U2 at Lower Sileru was in service and 220kV Asupaka-Lower Sileru, 220kV Chinturu -Lower Sileru and U2 was connected to Bus-2. As per the reports submitted, the triggering incident was LBB operation due to the non-opening of the Y-phase limb while de paralleling Unit-2 of 220kV Lower Sileru PH. Immediately, all the elements connected to 220kV Bus-2 tripped. | APGENCO to expedite the Breaker replacement work in the next available opportunity and intimate the same to SRPC/SRLDC. | APGENCO | APG_LSPH2:APGENCO: 01/04/2024 09:13:37: Already to pursue the APTRANSCO regard to the implementation of the DT signal.It may shortly rectified. APG_LSPH2:APGENCO: 03/05/2024 09:12:50: The Unit-2 breaker already replaced by new spare one. | Complied | Complied
115/II/2 | Tripping of Bus-2 at 220kV Lower Sileru of APGENCO | 22-12-2023 15:03 | In the antecedent conditions U1 and U2 at Lower Sileru was in service and 220kV Asupaka-Lower Sileru, 220kV Chinturu -Lower Sileru and U2 was connected to Bus-2. As per the reports submitted, the triggering incident was LBB operation due to the non-opening of the Y-phase limb while de paralleling Unit-2 of 220kV Lower Sileru PH. Immediately, all the elements connected to 220kV Bus-2 tripped. | APGENCO to rectify the PLCC communication at earliest. | APGENCO | APG_LSPH2:APGENCO: 01/04/2024 09:13:37: On Dt.18.03.2024,The Unit breaker replaced by new one. APG_LSPH2:APGENCO: 03/05/2024 09:12:50: Already pursue with the APTRANSCO, To implementation with the DT Signal. APG_LSPH2:APGENCO: 05/11/2024 15:27:34: except 220KV LS-Chinthuru feeder remaining all 220KV Feeders DT signal assignment completed,but not kept in service because present the LBB protection relays and busbar protection relays sperate APG_LSPH2:APGENCO: 28/12/2024 15:09:26: Direct Trip Signals assignment completed at Lower Sileru end and kept in service. | Complied | Complied
119/I/4 | Complete Outage of 220kV/132kV AP Carbides SS of APTRANSCO | 02-05-2024 23:22 | In the antecedent conditions, the connectivity of 220kV AP Carbide is as shown below. 220kV AP Carbide station is connected radially to 220kV Narnoor through 220kV Narnoor-AP Carbide-1&2 from 220kV level and at 132kV level AP Carbides are connected to 132kV Kurnool through 132kV AP Carbides-Kurnool-1&2 and 132kV AP Carbides-Yemmigannur | APTRANSCO to correct the Phase notation (R-Y-B) at Narnoor and AP carbides | APTRANSCO | dee2sp:APTRANSCO: 30/07/2024 13:07:50: Phase notation corrected. | Complied | Pending
119/I/4 | Complete Outage of 220kV/132kV AP Carbides SS of APTRANSCO | 02-05-2024 23:22 | In the antecedent conditions, the connectivity of 220kV AP Carbide is as shown below. 220kV AP Carbide station is connected radially to 220kV Narnoor through 220kV Narnoor-AP Carbide-1&2 from 220kV level and at 132kV level AP Carbides are connected to 132kV Kurnool through 132kV AP Carbides-Kurnool-1&2 and 132kV AP Carbides-Yemmigannur | APTRANSCO to expedite to provide Second DC supply at earliest | APTRANSCO | dee2sp:APTRANSCO: 30/07/2024 13:07:50: 2nd Battery set along with charger and DCDB commissioned on 03-07-2024. | Complied | Pending
119/I/4 | Complete Outage of 220kV/132kV AP Carbides SS of APTRANSCO | 02-05-2024 23:22 | In the antecedent conditions, the connectivity of 220kV AP Carbide is as shown below. 220kV AP Carbide station is connected radially to 220kV Narnoor through 220kV Narnoor-AP Carbide-1&2 from 220kV level and at 132kV level AP Carbides are connected to 132kV Kurnool through 132kV AP Carbides-Kurnool-1&2 and 132kV AP Carbides-Yemmigannur | DR time sync issue at 220kV AP Carbides shall be rectified | APTRANSCO | dee2sp:APTRANSCO: 30/07/2024 13:07:50: DR synchronization issue Will be rectified within 6 months dee2sp:APTRANSCO: 15/12/2025 11:08:26: GPS panels for time syncronization proposed under RMI 2024-25 and apporval accorded vide TOO.No.MS.3381, dt.21-08-2024 work will be completed after allotment of material. | Pending | Pending
119/I/5 | Complete Outage of 220kV/132kV Nandyal SS of APTRANSCO | 02-05-2024 14:25 | As per the reports submitted, the triggering incident was R-N fault due to suspected agricultural fire in the RoW of Nandyal Somayajulapally Line -1 at 14:15 Hrs. At Nandyal end, the fault was sensed in Zone-1 A/R operated and the line tripped on persistent fault. At Somayajulapally end, the fault was sensed in carrier aided Zone-2. A/R did not operate at Somayajulapally end and the line tripped. At 14:25hrs after around 10 min from fault in line-1, R-N fault was also observed in 220kV Nandyal Somayajulapally Line-2. At Nandyal end, the fault was sensed in Zone-1. At Somayajulapally end, the fault was sensed in carrier aided Zone-2. At both ends, A/R operated and was successful however the line tripped on fault in reclaim time. Tripping of both lines led to the Complete Outage of 220kV/66kV Chintamani SS and 220kV/66kV Srinivasa Pura SS of KPTCL. | DR time sync issue in 220kV Nandyal Somayajulapalli Line-1&2 at Nandyal end shall be rectified | APTRANSCO | dee2sp:APTRANSCO: 30/07/2024 13:07:50: Only time sync panel received at 220kV SS Nandyal and auxiliary's such as LIU, Ethernet switches patch cards etc. are yet to be received. After receipt of materials in full shape, the DR synchronization issue will be rectified within 3 months. dee2sp:APTRANSCO: 08/12/2025 12:32:41: Completed on 22/11/25. | Complied | Complied
119/I/7 | Complete Outage of 220kV Tallapally Switching Station of APTRANSCO | 07-05-2024 19:29 | 220kV Tallapally Switching station is connected to 400kV/220kV NSagar_PG through LV side of 400kV/220kV Nsagar_PG ICT-1,2&3. The LV side breakers of the ICTs are located in 400kV/220kV NSagar_PG SS wherein the LBB operation of these CBs lead to tripping of elements connected to the 220kV Bus in 220kV Tallapally Switching station to which the ICT is connected. As per the reports submitted the triggering incident was R-phase LA flashover in 220kV Tallapally NSagar_TS Line-1 at Tallapally end. At NSagar_TS end, the fault was sensed in Zone-2 and the line tripped with a delay of 400ms. At Tallapally end the fault was sensed in Zone-1. At the same time, spurious LBB trip was extended from LBB cables of 220kV side of 400kV/220kV NSagar ICT-1&2 causing LBB of 220kV side of 400kV/220kV NSagar ICT-1(connected to 220kV bus-2) & 400kV/220kV NSagar ICT-2(connected to 220kV Bus-1) to maloperate and all the elements connected to 220kV Bus-1 and Bus-2 tripped. Tripping of both buses led to complete outage of 220kV Tallapally Switching Station. | APTRANSCO to rectify the DR time sync issue at Nsagar_AP end | APTRANSCO | dee2sp:APTRANSCO: 06/08/2024 12:29:54: At Tallapally SS, new Time Synchronization panel was supplied and it is to be commissioned. APTRANSCO addressed to the supplier (M/s. Hitachi Energy Ltd) to arrange for the commissioning of the same. dee2sp:APTRANSCO: 13/08/2024 11:58:10: On 09-08-2024, DR Time synchronization of all relays at 220kV SWS, Tallapalli were completed. | Complied | Complied
120/I/6 | Complete Outage of 220kV/132kV Kakinada SS, 220kV/132kV Paravada SS, 220kV Anrak SWS of APTRANSCO | 05-06-2024 13:01 | Due to the tower collapse of 220kV VSS-Parawada, 220kV Parawada and 220kV Anrak SwS are being radially connected from 220kV/132 Kakinada SS through 220kV Kakinada-Bommuru and 220kV Kakinada Samarlakota.As per the reports submitted, the triggering incident was a high resistance B-N fault in the 220KV Kakinada-Bommuru line. The fault was sensed in Zone-1 at Bommuru end when the fault current was around 1.1kA and B-pole tripped. | APTRANSCO to check the relay (ABB make REL670LC) at Kakinda. OEM may be consulted if required. | APTRANSCO | dee2sp:APTRANSCO: 05/08/2024 13:13:04: REL670 relay at Samarlakota end on Kakinada feeder was Mal operated. DR & Events extracted from Main-2, REL 670 relay of 220KV Kakinada feeder at Samalkot substation sent to OEM (M/s. ABB) for recommendations. | Complied | Pending
120/I/6 | Complete Outage of 220kV/132kV Kakinada SS, 220kV/132kV Paravada SS, 220kV Anrak SWS of APTRANSCO | 05-06-2024 13:01 | Due to the tower collapse of 220kV VSS-Parawada, 220kV Parawada and 220kV Anrak SwS are being radially connected from 220kV/132 Kakinada SS through 220kV Kakinada-Bommuru and 220kV Kakinada Samarlakota.As per the reports submitted, the triggering incident was a high resistance B-N fault in the 220KV Kakinada-Bommuru line. The fault was sensed in Zone-1 at Bommuru end when the fault current was around 1.1kA and B-pole tripped. | APTRANSCO to rectify the DR time sync issue at Kakinada substation. | APTRANSCO | dee2sp:APTRANSCO: 05/08/2024 13:10:43: DR time sync complaint of Main-1, MiCOM P444 relay of 220KV Bommuru feeder at Kakinada substation rectified on 05.08.2024. | Complied | Pending
120/I/7 | Complete outage of 400kV RYTPP of APGENCO | 07-06-2024 23:31 | 400kV RYTPP is connected radially through 400KV Kalikiri-RYTPP-1&2 feeder. As per the reports submitted, the triggering incident is tripping of Rayalaseema U6 on generator protection operation at 22:00Hrs. With the tripping of the unit, high voltages were observed and 400KV Kalikiri-RYTPP-2 tripped on over voltage and DT was sent at remote end and subsequently at 23:31Hrs, 400KV Kalikiri-RYTPP-1 tripped on over voltage and DT was sent to remote end. With the tripping of both the lines led to the complete outage of 400kV RYTPP | APGENCO to rectify the DC earth leakage issues at RYTPP. | APGENCO | MARUTHIPRASAD:APGENCO: 03/09/2024 12:35:49: The earth leakage issue has been rectified and system is restored to normalcy | Complied | Complied
120/I/7 | Complete outage of 400kV RYTPP of APGENCO | 07-06-2024 23:31 | 400kV RYTPP is connected radially through 400KV Kalikiri-RYTPP-1&2 feeder. As per the reports submitted, the triggering incident is tripping of Rayalaseema U6 on generator protection operation at 22:00Hrs. With the tripping of the unit, high voltages were observed and 400KV Kalikiri-RYTPP-2 tripped on over voltage and DT was sent at remote end and subsequently at 23:31Hrs, 400KV Kalikiri-RYTPP-1 tripped on over voltage and DT was sent to remote end. With the tripping of both the lines led to the complete outage of 400kV RYTPP | APTRANSCO/APGENCO to finalise action plan to resolve high voltage issue at RYTPP. | APTRANSCO | dee2sp:APTRANSCO: 06/08/2024 16:11:41: As per CEA clearance issued on 09.10.2023, APTRANSCO issued revised administrative approval vide TOO Ms No.3214,Dt.28-03-2024 for construction of TMDC line from 400kV RTPP to 400kV SS, Jammalamadugu. Technical sanction and preparation of Tender document is under process. | Complied | Complied
120/I/8 | Complete Outage of 220kV/132kV Parawada SS of APTRANSCO | 10-06-2024 10:33 | 220kV VSS-Parawada line -1&2 tripped on tower collapse on 01.06.2024 at 01:16 Hrs and subsequently 220kV VSS-Parawada line -1 was revived. In the antecedent conditions, 220kV Parawada-Kakinda and 220kV Parawada-Anrak lines were under idle charged condition due to power regulation. Hence, 220kV/132kV Parawada SS was being radially through 220kV Parawada VSS Line-1 at 220kV level and 132kV Parawada-Koruprolu at 132kV level as 132kV Parawada-Gazuwaka was under idle charged condition. | APTRANSCO to report the tower failure event to CEA. | APTRANSCO | dee2sp:APTRANSCO: 06/08/2024 16:42:57: Preliminary report on failure of Tower was communicated to CEA from CE/Transmission/APTRANSCO on 04/06/2024 at 04:24:09PM by E-Mail. | Complied | Complied
120/II/7 | Tripping of 220kV Bus-2 of Vizag Switching Station of APTRANSCO | 01-06-2024 01:06 | As per the reports submitted, the triggering incident was B-N fault in 220kV VSS Paravada Line-2 at 01:15:32.894 due to tower collapse at Location No. 455. At both ends, the fault was sensed in Zone-1. A/R operated and the line tripped on persistent fault. Subsequently, at 01:16:03.809 R-N fault was observed in 220kV VSS Paravada Line-1 as both lines are on the same tower. At Paravada end the fault was sensed in Zone-1 distance protection with a fault current of 2.3kA, DT was received from the remote end and the line tripped. At VSS end , the fault was sensed in Zone-1. A/R was not in service due to issue with spring charge motor. B-phase of the breaker failed to open causing LBB of 220kV Bus-2 to operate and DT was sent to the remote end. Immediately all elements connected to 220kV Bus-2 of VSS including LV side of 400/220kV ICT at Gazuwaka-1 & 2 tripped. | APTRANSCO to ensure the healthiness of the CBs | APTRANSCO | dee2sp:APTRANSCO: 07/08/2024 15:30:45: After the incident, B-Ph trip coil-1&2 of Parawada-1 feeder at VSS end were replaced. R-Ph spring charge problem is rectified. CB Mechanism was lubricated and healthy CB operations were ensured. Healthiness of CBs will be ensured regularly. | Complied | Complied
120/II/7 | Tripping of 220kV Bus-2 of Vizag Switching Station of APTRANSCO | 01-06-2024 01:06 | As per the reports submitted, the triggering incident was B-N fault in 220kV VSS Paravada Line-2 at 01:15:32.894 due to tower collapse at Location No. 455. At both ends, the fault was sensed in Zone-1. A/R operated and the line tripped on persistent fault. Subsequently, at 01:16:03.809 R-N fault was observed in 220kV VSS Paravada Line-1 as both lines are on the same tower. At Paravada end the fault was sensed in Zone-1 distance protection with a fault current of 2.3kA, DT was received from the remote end and the line tripped. At VSS end , the fault was sensed in Zone-1. A/R was not in service due to issue with spring charge motor. B-phase of the breaker failed to open causing LBB of 220kV Bus-2 to operate and DT was sent to the remote end. Immediately all elements connected to 220kV Bus-2 of VSS including LV side of 400/220kV ICT at Gazuwaka-1 & 2 tripped. | APTRANSCO to resolve the DR time sync issue in 220kV VSS Paravada Line-2 at Paravada end. | APTRANSCO | dee2sp:APTRANSCO: 07/08/2024 12:40:19: It is proposed to provide Time synchronization in 15 Days. dee2sp:APTRANSCO: 21/08/2024 15:53:15: Completed on 19/08/2024. | Complied | Complied
120/II/7 | Tripping of 220kV Bus-2 of Vizag Switching Station of APTRANSCO | 01-06-2024 01:06 | As per the reports submitted, the triggering incident was B-N fault in 220kV VSS Paravada Line-2 at 01:15:32.894 due to tower collapse at Location No. 455. At both ends, the fault was sensed in Zone-1. A/R operated and the line tripped on persistent fault. Subsequently, at 01:16:03.809 R-N fault was observed in 220kV VSS Paravada Line-1 as both lines are on the same tower. At Paravada end the fault was sensed in Zone-1 distance protection with a fault current of 2.3kA, DT was received from the remote end and the line tripped. At VSS end , the fault was sensed in Zone-1. A/R was not in service due to issue with spring charge motor. B-phase of the breaker failed to open causing LBB of 220kV Bus-2 to operate and DT was sent to the remote end. Immediately all elements connected to 220kV Bus-2 of VSS including LV side of 400/220kV ICT at Gazuwaka-1 & 2 tripped. | APTRANSCO to submit the tower failure report to CEA | APTRANSCO | dee2sp:APTRANSCO: 06/08/2024 16:42:57: Preliminary report on failure of Tower was communicated to CEA from CE/Transmission/APTRANSCO on 04/06/2024 at 04:24:09PM by E-Mail. | Complied | Complied
120/II/8 | Tripping of 220kV Bus-1 of 220kV Srisailam RB Generating station of APGENCO | 03-06-2024 07:54 | In the antecedent conditions, both 220kV Srisailam-Tallapalli-1&2 was under forced outage. Both the lines (220kV Srisailam-Tallapalli-1&2) are in the same tower. The line configuration within the station is as shown below. In the antecedent conditions the bus side isolator was in closed condition but the line side isolator was in open condition and earthed. After the offline fault locator test on 220kV Srisailam-Tallapalli-2 where in the fault location was full length and the same was test charged | APGENCO to review the sensing of Zone-1 in 220kV Srisailam RB-Tallapalli-1 when Voltage was below dead band | APGENCO | APG_SRBSS2:APGENCO: 08/04/2025 12:10:30: The relay settings are verified and changed the VT fuse setting Hence plase drop the point | Complied | Complied
120/II/9 | Tripping of 220kV Bus-2 of 220kV Tallapalli SWS of APTRANSCO | 06-06-2024 00:59 | 220kV Tallapally Switching station is connected to 400kV/220kV NSagar_PG through LV side of 400kV/220kV Nsagar_PG ICT-1,2&3. The LV side breakers of the ICTs are located in 400kV/220kV NSagar_PG SS wherein the LBB operation of these CBs lead to tripping of elements connected to the 220kV Bus in 220kV Tallapally Switching station to which the ICT is connected. During antecedent conditions, 400kV/220kV NSagar ICT-1 & 3 are connected to 220kV Bus-2 and 400kV/220kV Sagar ICT-2 is connected to 220kV Bus-1 of 220kV Tallpally SWS and 400kV/220kV NSagar ICT-2 was under LC. As per the reports submitted, a spurious LBB trip was extended from LBB cables of 220kV side of 400kV/220kV NSagar ICT-1&2 causing LBB of 220kV side of 400kV/220kV NSagar ICT-1& 400kV/220kV NSagar ICT-2 to maloperate. Since 400kV/220kV NSagar ICT-2 was under LC, the LBB trip was not extended to 220kV Tallapally SWS Bus-1 I and all the elements connected to Bus-2 tripped | APTRANSCO to replace the existing control cables of the LBB operated signal of ICT-1 & 2 from the PGCIL end. | APTRANSCO | dee2sp:APTRANSCO: 06/08/2024 11:15:34: Completed on 11-07-2024. | Complied | Pending
120/II/9 | Tripping of 220kV Bus-2 of 220kV Tallapalli SWS of APTRANSCO | 06-06-2024 00:59 | 220kV Tallapally Switching station is connected to 400kV/220kV NSagar_PG through LV side of 400kV/220kV Nsagar_PG ICT-1,2&3. The LV side breakers of the ICTs are located in 400kV/220kV NSagar_PG SS wherein the LBB operation of these CBs lead to tripping of elements connected to the 220kV Bus in 220kV Tallapally Switching station to which the ICT is connected. During antecedent conditions, 400kV/220kV NSagar ICT-1 & 3 are connected to 220kV Bus-2 and 400kV/220kV Sagar ICT-2 is connected to 220kV Bus-1 of 220kV Tallpally SWS and 400kV/220kV NSagar ICT-2 was under LC. As per the reports submitted, a spurious LBB trip was extended from LBB cables of 220kV side of 400kV/220kV NSagar ICT-1&2 causing LBB of 220kV side of 400kV/220kV NSagar ICT-1& 400kV/220kV NSagar ICT-2 to maloperate. Since 400kV/220kV NSagar ICT-2 was under LC, the LBB trip was not extended to 220kV Tallapally SWS Bus-1 I and all the elements connected to Bus-2 tripped | APTRANSCO to resolve the DR time sync issue at Tallapally SWS end. | APTRANSCO | dee2sp:APTRANSCO: 06/08/2024 11:15:34: Time synchronization panel was supplied to the Tallapalli SWS and it is to be commissioned..APTRANSCO addressed to the supplier ( M/s. Hitachi Energy Ltd) to arrange for the commissioning of the same. dee2sp:APTRANSCO: 13/08/2024 11:01:06: On 09/08/2024, DR time synchronization completed for all relays at 220kV SWS, Tallapalli. | Pending | Pending
120/VI/3 | 220kV-Srisailam Right Bank-Dindi-1 | 03-06-2024 00:56 | Srisailam Right Bank | APGENCO to rectify the DR time synchronisation at Srisailam Right bank station | APGENCO | APG_SRBSS2:APGENCO: 08/04/2025 12:10:30: There is DR problem in the 220KV132KV Swutchyard, Dindi-I relays also enabled the DR and Time synchonisation. Hence please drop the point. | Complied | Complied
121/I/1 | Complete Outage of 220kV Dhone SWS, 220kV/11kV Kambalapadu SS, 220kV/11kV Lakkasagaram SS, 220kV/33kV/11kV Krishnagiri SS, 220kV/11kV Settypalli SS, 220kV/33kV/11kV Nansuralla SS, 220kV/33kV Aspiri SS, 220kV/33kV Molagaveli SS, 220kV/11kV Pendekolu SS of APTRANSCO | 25-06-2024 12:24 | 220kV Dhone Bus-1 and 220kV Dhone Kambalapadu Line were under LC and all elements were connected to 220kV Bus-2. Earth rods were closed at common jumper of Bus-I & Bus-II isolators of Kambalapadu feeder, by opening both the isolators. After attending rectification of fixed contact of Bus-I isolator of Kambalapadu feeder, to check the operation of bus-I isolator of Kambalapadu feeder, the operator has closed the Bus-2 Isolator of the line instead of the Bus-1 isolator. This caused a RY-N fault in Bus-2 which subsequently became a RYB-N fault. Immediately, few lines connected to Bus-2 tripped on zone-2 and zone-1 from remote ends and few lines tripped on zone-4 protection at Dhone SwS. The details of tripping are as follows. | APTRANSCO to rectify the phase notation in DR. | APTRANSCO | eesp:APTRANSCO: 05/09/2024 07:55:46: Phase notation in DR was rectified. | Complied | Pending
121/I/1 | Complete Outage of 220kV Dhone SWS, 220kV/11kV Kambalapadu SS, 220kV/11kV Lakkasagaram SS, 220kV/33kV/11kV Krishnagiri SS, 220kV/11kV Settypalli SS, 220kV/33kV/11kV Nansuralla SS, 220kV/33kV Aspiri SS, 220kV/33kV Molagaveli SS, 220kV/11kV Pendekolu SS of APTRANSCO | 25-06-2024 12:24 | 220kV Dhone Bus-1 and 220kV Dhone Kambalapadu Line were under LC and all elements were connected to 220kV Bus-2. Earth rods were closed at common jumper of Bus-I & Bus-II isolators of Kambalapadu feeder, by opening both the isolators. After attending rectification of fixed contact of Bus-I isolator of Kambalapadu feeder, to check the operation of bus-I isolator of Kambalapadu feeder, the operator has closed the Bus-2 Isolator of the line instead of the Bus-1 isolator. This caused a RY-N fault in Bus-2 which subsequently became a RYB-N fault. Immediately, few lines connected to Bus-2 tripped on zone-2 and zone-1 from remote ends and few lines tripped on zone-4 protection at Dhone SwS. The details of tripping are as follows. | APTRANSCO to rectify time sync issues in all lines connected to Dhone end. | APTRANSCO | dee2sp:APTRANSCO: 04/09/2024 22:07:07: DR time sync panels will be provided within 6 months dee2sp:APTRANSCO: 15/12/2025 11:13:11: GPS panels for time syncronization proposed under RMI 2025-26 and will be provided after allotment of material. | Pending | Pending
121/I/1 | Complete Outage of 220kV Dhone SWS, 220kV/11kV Kambalapadu SS, 220kV/11kV Lakkasagaram SS, 220kV/33kV/11kV Krishnagiri SS, 220kV/11kV Settypalli SS, 220kV/33kV/11kV Nansuralla SS, 220kV/33kV Aspiri SS, 220kV/33kV Molagaveli SS, 220kV/11kV Pendekolu SS of APTRANSCO | 25-06-2024 12:24 | 220kV Dhone Bus-1 and 220kV Dhone Kambalapadu Line were under LC and all elements were connected to 220kV Bus-2. Earth rods were closed at common jumper of Bus-I & Bus-II isolators of Kambalapadu feeder, by opening both the isolators. After attending rectification of fixed contact of Bus-I isolator of Kambalapadu feeder, to check the operation of bus-I isolator of Kambalapadu feeder, the operator has closed the Bus-2 Isolator of the line instead of the Bus-1 isolator. This caused a RY-N fault in Bus-2 which subsequently became a RYB-N fault. Immediately, few lines connected to Bus-2 tripped on zone-2 and zone-1 from remote ends and few lines tripped on zone-4 protection at Dhone SwS. The details of tripping are as follows. | APTRANSCO to strictly follow SOP during Testing and Maintenance works. | APTRANSCO | dee2sp:APTRANSCO: 04/09/2024 22:07:07: The SOP norms has been following at Dhone & also will be more vigilant in future during testing & Maintenance activities. | Complied | Pending
121/I/1 | Complete Outage of 220kV Dhone SWS, 220kV/11kV Kambalapadu SS, 220kV/11kV Lakkasagaram SS, 220kV/33kV/11kV Krishnagiri SS, 220kV/11kV Settypalli SS, 220kV/33kV/11kV Nansuralla SS, 220kV/33kV Aspiri SS, 220kV/33kV Molagaveli SS, 220kV/11kV Pendekolu SS of APTRANSCO | 25-06-2024 12:24 | 220kV Dhone Bus-1 and 220kV Dhone Kambalapadu Line were under LC and all elements were connected to 220kV Bus-2. Earth rods were closed at common jumper of Bus-I & Bus-II isolators of Kambalapadu feeder, by opening both the isolators. After attending rectification of fixed contact of Bus-I isolator of Kambalapadu feeder, to check the operation of bus-I isolator of Kambalapadu feeder, the operator has closed the Bus-2 Isolator of the line instead of the Bus-1 isolator. This caused a RY-N fault in Bus-2 which subsequently became a RYB-N fault. Immediately, few lines connected to Bus-2 tripped on zone-2 and zone-1 from remote ends and few lines tripped on zone-4 protection at Dhone SwS. The details of tripping are as follows. | APTRASNCO to refer the matter to OEM on overreach of relays at Nansuralla, Gooty and Krishnagiri ends. | APTRANSCO | dee2sp:APTRANSCO: 04/09/2024 22:07:07: The matter referred to OEMs (Siemens & ABB) vide email Dated.31-07-2024 on over reach of relays at 220kV SS, Nansuralla (Siemens) and 220kV SS, Krishnagiri (ABB). At Gooty end also referred to referred to OEM. | Complied | Pending
121/III/2 | Tripping at 400KV-GAZUWAKA-KALPAKKA-1 | 27-06-2024 11:34 | 400KV-GAZUWAKA-KALPAKKA-1 at Gajuwaka SS Y-Ph LA failed and Jumper isolated at LA. Fault current was not detected in Y-Phase due to jumper isolation | APTRANSCO to review the cause for the Detection of PSB at 400kV Gazuwaka end in P546 relay. | APTRANSCO | eesp:APTRANSCO: 05/09/2024 07:55:46: The Subject was referred to OEM. | Complied | Complied
121/VI/1 | 400 KV VTPS - NLR | 30-06-2024 03:17 | DR Time sync issue | APGENCO to submit the action taken report. | APGENCO | APG_NTTPS4001:APGENCO: 14/02/2025 12:22:32: Time synchronisation done (RJ45 port loose connection and rectified)and now its in time synch only | Complied | Complied
122/II/3 | Tripping of 220kV Bus-1 of 220kV Nagarjunasagar_AP SWS(Tallapalli SWS) | 31-07-2024 10:22 | As per the reports submitted, the triggering incident was Y-phase CT failure in 220kV Nagarjunasagar_AP SWS Rentachintala line at Nagarjunasagar_AP SWS end causing a Y-N fault in 220kV Bus-1.At Nagarjunasagar_AP SWS, 220kV Bus-1 BBP operated and all elements connected to the 220kV Bus-1 got tripped. | APTRANSCO to report the equipment failure to CEA. | APTRANSCO | eesp:APTRANSCO: 01/10/2024 14:11:52: Informed to the concerned, report will be submitted within 7 days. dee2sp:APTRANSCO: 03/10/2024 17:13:13: Report submitted to CEA on 03-10-2024. | Complied | Complied
122/II/4 | Tripping of 220kV Bus-1 of 220kV VSS SWS | 01-08-2024 02:21 | During DEF operation of 220kV VSS Gajuwaka Line at VSS, B-pole didn't open and this resulted in the LBB operation of 220kV Bus-1 of 220kV VSS SWS. | APTRANSCO to monitor the healthiness of breakers at VSS substation. | APTRANSCO | eesp:APTRANSCO: 01/10/2024 14:10:38: Healthiness of breakers at VSS Substation will be monitored regularly. | Complied | Complied
122/II/5 | Tripping of Bus-2 of 400kV/220kV Jammalamadugu SS | 01-08-2024 16:36 | The triggering incident was R-N fault in 220kV Bus-2 of 400kV/220kV Jammalamadugu SS. At Jammalamadugu end, immediately, 220kV Bus-2 BBP operated and all lines connected to the 220kV Bus-2 got tripped. | APTRANSCO to review the relay settings at Animela substion. | APTRANSCO | dee2sp:APTRANSCO: 01/10/2024 14:05:42: Relay settings verified and found in order. Relays tested on 24/09/2024 and results found satisfactory. Performance of relays kept in observation. | Complied | Complied
122/II/5 | Tripping of Bus-2 of 400kV/220kV Jammalamadugu SS | 01-08-2024 16:36 | The triggering incident was R-N fault in 220kV Bus-2 of 400kV/220kV Jammalamadugu SS. At Jammalamadugu end, immediately, 220kV Bus-2 BBP operated and all lines connected to the 220kV Bus-2 got tripped. | APTRANSCO to review the Zone-1 settings at Animela end. | APTRANSCO | eesp:APTRANSCO: 01/10/2024 14:10:38: Settings reviewed and are in order. Kept in observation | Complied | Complied
122/II/5 | Tripping of Bus-2 of 400kV/220kV Jammalamadugu SS | 01-08-2024 16:36 | The triggering incident was R-N fault in 220kV Bus-2 of 400kV/220kV Jammalamadugu SS. At Jammalamadugu end, immediately, 220kV Bus-2 BBP operated and all lines connected to the 220kV Bus-2 got tripped. | APTRANSCO to revise the A/R dead time to 1sec at Animela end in 220kV Jammalamadugu Animela Line | APTRANSCO | dee2sp:APTRANSCO: 01/10/2024 14:05:42: A/R Dead time revised to 1 Sec on 220kV Jammalamadugu feeder at Animela end. | Complied | Complied
122/II/7 | Tripping of 220kV Bus of 400kV/220kV VTPS | 06-08-2024 18:25 | As per the reports submitted, Unit-5 was synchronized to the grid after completing overhaul works. Immediately after closing the GT-5 breaker, TC1 and TC2 faulty alarms were triggered, and a turbine trip command was issued, leading to Unit-5 tripping on Low Forward Power (LFP).Due to the existing TC1 and TC2 faults, the GT-5 breaker did not open despite the trip command from the GRP. As the trip command and a current of 200mA persisted for more than 200 milliseconds, the LBB protection was activated, tripping all breakers connected to BUS-1. | APGENCO to rectify the DR time sync issue in GRP DR. | APGENCO | APG_NTTPS2202:APGENCO: 11/10/2025 09:41:09: Meeting index No.122/VI/2 repeated. | Complied | Complied
122/IV/6 | 220KV-ASUPAKA-LOWER_SILERU-1 | 15-08-2024 10:03 | Non-operation of A/R needs to be reviewed | APGENCO to verify to A/R logic issues at Lower Sileru end. | APGENCO | APG_LSPH2:APGENCO: 04/03/2025 09:55:32: After this event, the feeder tripped two to three incidents, the A/R Successfully operated. Hence found to be normal. | Complied | Complied
122/VI/2 | VTPS - 220KV | 06-08-2024 18:25 | DR TIME SYNC | APGENCO to furnish the report on DR time synchronization issue at VTPS end. | APGENCO | APG_NTTPS2202:APGENCO: 11/10/2025 09:36:29: Time sync Equipment procurement is under process. | Pending | Pending
123/II/1 | Tripping of 220kV Bus-1 of 220kV/132kV Srisailam RB of APGENCO | 20-08-2024 05:04 | The triggering incident was R-N fault in 220kV Bus-2 due to jumper cut in 220kV Srisailam RB Nsagar Line-1 at 220kV Srisailam RB. Immediately, BBP operated and all elements connected to the 220kV Bus-2 got tripped at 220kV/132kV Srisailam RB | APGENCO/TGGENCO to maintain RoW on 220kV Srisailam RB N Sagar line | APGENCO | APG_SRBSS2:APGENCO: 08/04/2025 12:05:53: carrying the regular maitenance APG_SRBSS2:APGENCO: 08/04/2025 12:10:30: please drop the event | Complied | Complied
123/II/1 | Tripping of 220kV Bus-1 of 220kV/132kV Srisailam RB of APGENCO | 20-08-2024 05:04 | The triggering incident was R-N fault in 220kV Bus-2 due to jumper cut in 220kV Srisailam RB Nsagar Line-1 at 220kV Srisailam RB. Immediately, BBP operated and all elements connected to the 220kV Bus-2 got tripped at 220kV/132kV Srisailam RB | APGENCO to ensure to carry out regular maintenance | APGENCO | APG_SRBSS2:APGENCO: 08/04/2025 12:05:53: carrying the regular maitenance APG_SRBSS2:APGENCO: 08/04/2025 12:10:30: please drop the event | Complied | Complied
123/II/7 | Tripping of 220kV Bus-2 of Lower Sileru PH of APGENCO. | 11-09-2024 20:17 | As per the reports submitted, at 20:16 hours, an internal Y-Phase fault occurred in Unit-2, leading to operation of GT Buchholtz and GT Differential Protections. These protections triggered the master trip relays, causing the unit to trip and the generator breaker to open. However, the LBB Group-B protection relay operated at Lower Sileru because the CT input for the Unit-2 LBB overcurrent relays was being taken from the generator side CTs. Immediately, all elements connected to 220kV Bus-2. | APGENCO to check the orderliness of the LBB Protection provided at their similarly placed Generating Stations by ensuring correct CT input (from the HV side of the GT) is taken | APGENCO | APG_LSPH2:APGENCO: 05/11/2024 15:20:36: Unit-1 LBB CT also changed from 11KV side to 220KV Side.Now present all the LBB CT sensing taken from HV side(220KV) and same information send to HQ. | Complied | Complied
123/II/8 | Tripping of 220kV Bus-2 of 220kV Lower Sileru PH of APGENCO | 13-09-2024 10:05 | As per the reports submitted, while deparalleling Unit-3, Y-pole failed to open. LBB failed to open and other lines connected to 220kV Bus-2 were Hand tripped. | APGENCO to expedite to replacing static relay with numerical LBB relay. | APGENCO | APG_LSPH2:APGENCO: 28/10/2024 09:30:23: LBB numerical relay will be assigned whenever canal shut down works started. APG_LSPH2:APGENCO: 02/02/2026 16:16:31: Shifted LBB protection from Static relays to Numerical relays in Bus-Bar protection relays (ABB make REB670) | Complied | Complied
123/III/5 | 400KV-VTPS_IV-SURYAPET-2 | 31-08-2024 20:18 | As per the reports submitted, 400kV VTPS-Suryapet line-2 tripped only at VTPS end on spurious tripping due to DC earth leakage as switchyard was filled with water and was touching breaker marshalling boxes due to heavy rain. At Suryapet end the line was in service | APGENCO HQ needs to ensure to furnish the details for the events included in PCSC meeting. | APGENCO | APG_NTTPS4001:APGENCO: 14/02/2025 12:22:32: Dewatering of 400KV Switchyard carried out and breaker marshalling box was cleaned and DC leakage rectified | Complied | Complied
123/IV/10 | 220KV-ASUPAKA-LOWER_SILERU-1 | 18-09-2024 11:26 | APGENCO: 1. Non-operation of A/R. 2. Non-receipt of carrier signal. | APGENCO to furnish the detailed report regarding the non-operation of A/R | APGENCO | APG_LSPH2:APGENCO: 28/10/2024 09:25:29: Carrier end to end test conducted on Dt.08.10.2024 and Carrier signal found healthy | Complied | Complied
123/VI/19 | 220KV-ASUPAKA-LOWER_SILERU-1 | 18-09-2024 11:26 | DR TIME SYNC ISSUE | APGENCO to furnish the report regarding the action taken to rectify the DR time syn issue at Lower Sileru station | APGENCO | APG_LSPH2:APGENCO: 28/10/2024 09:23:27: There is no time sync issue observed in relays. All the relays are connected to the GPS. | Complied | Complied
124/I/14 | Complete Outage of 220kV/132kV Borampalli SS, 220kV/33kV Saipuram, 220kV Theta and 220kV Maddelacheru | 10-10-2024 14:22 | Complete Outage of 220kV/132kV Borampalli SS, 220kV/33kV Saipuram, 220kV Theta and 220kV Maddelacheru: 220kV/33kV Saipuram, 220kV Theta and 220kV Maddelacheru are being radially fed from 220kV/132kV Borampalli SS. As per the reports submitted, the triggering incident was LBB maloperaion in 220kV Borampalli Kalyandurgam Line-2. subseqeuntly, all elements connected to 220kV Bus-1 and Bus-2 tripped due to erratic isolator status in 220kV Borrampalli Ecoron feeder-1 bay. This led to complete outage of 220kV/132kV Borampalli SS which inturn led to complete outage of 220kV/33kV Saipuram, 220kV Theta and 220kV Maddelacheru. | APTRANSCO to follow strict adherence to SoP | APTRANSCO | eesp:APTRANSCO: 06/12/2024 10:26:27: APTRANSCO will follow the SOP. | Complied | Complied
124/II/7 | Tripping of 400kV Bus-2 and 220kV Bus-2 at 400/220kV Podili SS | 02-10-2024 19:11 | In the antecedent conditions, 400/220kV Podili substation had only one DC supply as the other DC source was being replaced. As per the reports submitted, due to the station supply failure and complete discharge of the only available DC source led to the tripping of Bus Reactor and 220kV Podili-Podili (old)-1&2 lines. During the supply restoration process, due to control circuit issue led to the tripping of ICT-1,2 &3, 220kV lines and bus coupler other than 220kV Podili-Atmakur-1. This led to the tripping of 400kV Bus-2 and 220kV Bus-2 at 400/220kV Podili SS. | APTRANSCO to follow the strict adherence to SoP | APTRANSCO | eesp:APTRANSCO: 06/12/2024 10:26:27: APTRANSCO will follow the SOP. | Complied | Complied
124/IV/9 | 400KV-KRISHNAPATNAM-RACHAGUNNERI-1 | 16-10-2024 13:19 | As per the reports submitted, the triggering incident was YN fault in the line. At Rachagunneri end the line tripped on operation of Zone-1 distance protection. A/R operated but again the line tripped due to persistent fault. At Krishnapatnam end the line tripped on operation of Zone-1 distance protection. The line tripped on 3-phase on receipt of carrier from the remote end during the dead time of A/R. | APGENCO to furnish the action plan taken regarding this event | APGENCO | APP_SDSTPS4002:APGENCO: 14/02/2025 16:17:09: DT received from other end in the dead time of A/R. Due to this 3 phase trip operated. | Complied | Complied
124/VI/12 | BORAMPALLI - 220KV | 10-10-2024 14:22 | BORAMPALLI - 220KV | APTRANSCO to confirm the DR time sync at Borampalli substation | APTRANSCO | eesp:APTRANSCO: 06/12/2024 17:45:45: It will be rectified within 15 Days. dee2sp:APTRANSCO: 27/12/2024 13:37:08: On 17/12/2024, rectified by replacing the damaged co-axial cable between antenna and GPS receiver. Now all the relays are synced with GPS at 220kV SS, Bormapalli. | Complied | Complied
125/I/1 | Complete Outage 220kV Chinakampalli (Cuddapah) SS of APTRANSCO | 18-10-2024 01:09 | As per the reports submitted, the triggering incident is the B-ph CT failure of 220kV Cuddpah-RTPP-1 at Cuddapah end. The fault was sensed in Z1 in the line and BBP operated leading to the tripping of all elements connected to Bus-1. Due to fire from the failed CT coming into the vicinity of 220kV Cuddpah-RTPP-2 at Cuddpah end led to the operation of BBP of 220kV Bus-2 and led to the complete outage of 220kV Cuddapah (Chinkampalli) SS | APTRANSCO to verify the healthiness of all CTs in the switchyard. | APTRANSCO | dee2sp:APTRANSCO: 02/01/2025 13:00:10: All the CTs in the switchyard of 220kV CK Palli were tested and results found healthy except R-Ph CT (VE make) of 220kV PGCIL-1 which is having high tan delta value. The same will be replaced with healthy CT with in one month. | Complied | Complied
125/III/4 | 400KV-RAYALSEEMA TPP-KALIKIRI-2 | 19-10-2024 16:33 | As per the reports submitted, during the test operations of Breaker through SAS, when trip command executed, DT was sent to Kalikiri end tripping main and tie breaker. Simultaneously tie breaker also tripped at RTPP end. | APGENCO RTPP to follow SOP during testing activities | APGENCO | MARUTHIPRASAD:APGENCO: 11/01/2025 19:31:53: All testing activities at RTPP 400KV Switchyard will follow SOP and comply with the instructions MARUTHIPRASAD:APGENCO: 11/01/2025 19:32:57: Following the SOP as per recommendations MARUTHIPRASAD:APGENCO: 15/04/2025 17:26:57: Submitted SOP for approval to SRPC.Hence,it is requested to mark this recommendation as complied. | Complied | Complied
126/I/3 | Complete Outage of 220KV SS Porumamilla, 132KV SS Brahmamgarimatam,132KV SS Porumamillla,132KV SS Kalasapadu, 132KV Inox and 220KV Ecoren Stations | 24-11-2024 17:37 | Triggering incident was tripping of 220KV PorumamillaJammalamadugu line 2 (only grid connected line that was in service by that time) due to transient fault. This resulted in the complete outage of 220KV SS Porumamilla, 132KV SS Brahmamgari matam, 132KV SS Porumamillla, 132KV SS Kalasapadu, 132KV Inox and 220KV Ecoren Stations. | APTRANSCO to furnish the anti-Islanding protection Scheme available in the downstream connected RE stations. Cause for the existence of Voltage may be studied and furnish the report in this regard. | APTRANSCO | dee2sp:APTRANSCO: 05/02/2025 10:58:18: Protection at M/s.Ecoren Energy india Pvt Ltd and M/s. Inox energy Pvt ltd pertains to respective entities. Hence, APTRANSCO addressed a Letter addressed to M/s.Ecoren Energy india Pvt Ltd and M/s. Inox energy Pvt ltd to furnish the details of anti-islanding scheme at respective stations. | Complied | Complied
126/II/7 | Tripping of 220kV Bus-1 of 220/132 kV KV_KOTA_OLD SS | 06-12-2024 23:09 | The triggering incident is the Y-ph CT failure of 220kV KV_Kota-KV_Kota_Old-1 at KV_Kota Old station, bus bar protection operated leading to the tripping of all the elements connected to 220kV Bus. This led to the tripping of 220kV Bus-1 of KV Kota Old Station. The 132kV network was intact during the event. | APTRANSCO to enable the dead zone protection and configure DT signals during the action of said protection. | APTRANSCO | dee2sp:APTRANSCO: 05/02/2025 10:53:44: It will be completed by the end of March-2025. dee2sp:APTRANSCO: 21/02/2025 11:28:10: End fault protection (dead zone) was enabled for the 220kV KV Kota (Old)- KV Kota(new) line-1,2 and 3 after completion of all the necessary wiring on 19/02/2025. | Complied | Complied
127/I/1 | Complete Outage of 400kV RYTPP Generating station of APGENCO | 29-12-2024 19:41 | As per the reports submitted, the triggering incident was tripping of 400kV RYTPP Kalikiri Line-1&2 on over voltage at 19:41hrs and 16:30hrs respectively. Tripping of both lines led to complete outage of 400kV RYTPP Generating station. | 1.APGENCO shall adhere to the Regulatory Provisions and the Timelines. 2.APGENCO to take up the overvoltage issue before the Study team and take necessary corrective action. | APGENCO | MARUTHIPRASAD:APGENCO: 28/02/2025 16:44:43: Posting of flash report will be taken up by APSLDC and other reports viz.FIR, DR ,EL, TR will be updated by APGENCO. Regarding the system study this will be taken up with power sytem study wing of APTRANSCO and status will be updated soon. | Complied | Complied
127/I/4 | Complete Outage of 220kV/33kV Rajampet SS. | 12-01-2025 14:16 | As per the reports submitted, the triggering incident was B-N fault in 220kV Rajampet Koduru line At Kuduru end, the fault was sensed in carrier aided zone-2. A/R operated and the line was holding. At Rajampet end, the fault was sensed in zone-1 but R-pole tripped instead of B-pole due to interchange of trip circuit wiring between R-Ph and B-Ph CB. Subsequently, 220kV Rajampet Cuddapah line tripped only at Cuddapah end on zone-2 distance protection. | 1.APTRANSCO to monitor the healthiness of all equipment and wiring logic during annual Internal Audit. 2.APTRANSCO to rectify the non-availability of SCADA SOE at Koduru. | APTRANSCO | eesp:APTRANSCO: 04/03/2025 15:00:36: Healthiness of all equipment and wiring logic will be monitored during the annual internal audit. | Complied | Complied
127/III/5 | 400KV-NARNOOR-GHANI-1 | 28-12-2024 13:18 | As per the reports submitted, 400kV Narnoor Ghani line-1 tripped only at Ghani end on operation of OV Stage-I relay operation due to adoption of wrong OVR stage-1 settings. At Narnoor end the line was in service. Tripping is not in order. | APTRANSCO to verify the OVR settings of other 400kV feeders at Ghani SS. | APTRANSCO | eesp:APTRANSCO: 04/03/2025 15:00:36: Verified and found in order | Complied | Complied
127/VI/12 | 400KV/220KV NELLORE_AP-ICT-1 | 12-01-2025 18:09 | As per the reports submitted, 400/220kV Nellore_AP ICT-1 tripped on operation of differential protection due to HV side B phase LA failure. Tripping is in order. | APTRANSCO to rectify the DR time sync issues at Nellore-AP. | APTRANSCO | eesp:APTRANSCO: 04/03/2025 15:00:36: It will be completed within 15 days. dee2sp:APTRANSCO: 24/03/2025 11:24:20: Completed on 10-03-25. | Complied | Complied
128/I/4 | Complete Outage of 220kV Nagarjuna Sagar AP SWS of APTRANSCO | 31-01-2025 02:13 | As per the reports submitted, the triggering incident is the attempted theft of isolators of 220kV Bus-3 (part of 220kV Bus-1) of 220kV Rentachintala-1 as shown in the figure during which R-N bus fault was created in Bus-1,2,3&4 leading to the operation of BBP in both the buses and led to the tripping of all the elements connected to 220kV Bus-1,2,3&4 at Nagarjunasagar (Tallapalli) and led to the complete outage of Complete Outage of 220kV Nagarjun Sagar AP SWS of APTRANSCO. | 1.APTRANSCO to ensure suitable safety measures to avoid thefts | APTRANSCO | eesp:APTRANSCO: 04/04/2025 15:33:14: Suitable safety measures to avoid thefts in APTRANSCO will be ensured . | Complied | Complied
128/II/1 | Tripping of 220kV Bus-2 of 220kV Lower Sileru PH | 25-01-2025 08:09 | As per the reports submitted, the triggering incident was Unit-1 LBB operation due to B phase CB failure resulting in the deengerization of 220kV Bus-2 of 220kV Lower Sileru PH of APGENCO | 1.APGENCO to review the Backup Impedance settings of the ICT at Lower Sileru to ensure that it does not operate for external faults 2.APGENCO to consult OEM regarding the REF pickup for external faults and furnish a report | APGENCO | APG_LSPH2:APGENCO: 05/04/2025 19:41:20: Verified the Back up Impedance and REF Protections.Modified the following settings in Back up Impedance adopted the Zone-1 setting:80% Transformer inpedance with time delay of 2Sec.Zone-2:120% of T/F impedance with time delay of 3S. In REF, the stabilizing value of resistance measured and values are in order.As per the DR analysis the differential current flow is ref CT's is beyond 30%.So REF operated as per settings. | Complied | Complied
128/II/2 | Tripping of 400kV Bus-2 of 400kV VTPS Generating station of APGENCO | 27-01-2025 12:24 | As per the reports submitted, the triggering incident was LBB maloperation in GT-8 of VTPS Generating station. Immediately, LBB operated and all elements connected to 400kV VTPS Bus-2 tripped. | 1.APGENCO to check the feasibility of providing an auxiliary relay to the Busbar | APGENCO | APG_NTTPS4002:APGENCO: 04/09/2025 10:13:19: Sir, In our detailed discussion with our internal protection team, Incorporating of extra elements like auxiliary relays in an important Protection schemes like LBB, Bus bar will impact the reliability of the protection. So The remedies we have already taken by placing 30 milliseconds delay in LBB initiation by keeping overall time delay of LBB operation as 200 milliseconds are better compared to placing an Auxiliary relay. So please update the status of the incident as complied and drop the point. | Complied | Complied
128/II/3 | Tripping of 220kV Bus-1 of 220kV Gooty SWS of APTRANSCO | 27-01-2025 15:53 | As per the reports submitted, the triggering incident was failure of Y-phase conductor in 220kV Gooty SWS Bus-1 causing a Y-phase fault in Bus-1. Immediately Bus-1 BBP operated and all elements connected to 220kV Gooty Bus-1 tripped. | 1.APTRANSCO to ensure the healthiness of insulators in the switchyard at 220kV Gooty SWS 2.APTRANSCO to rectify the time sync issues at 400kV and 220kV bus at Gooty SS | APTRANSCO | dee2sp:APTRANSCO: 04/04/2025 14:37:07: 1) Insulators replacement will be completed by 30-06-2025 at 220kV SWS, Gooty. 2) The defective GPS master clock was already sent to the concerned OEM for rectification. The GPS time synchronization will be implemented by the end of June 2025 after the rectification. dee2sp:APTRANSCO: 03/07/2025 17:31:25: 1)As soon as the allotment of insulators issued for replacement, it will be completed, expected date of completion is 31-10-25. 2)Defective GPS clock was already sent to concerned OEM for rectification. The GPS time sync will be implemented by the end of August-2025 after the rectification. dee2sp:APTRANSCO: 05/08/2025 12:53:25: Insulators replacement will be completed by 31-10-25 at 220kV SWS, Gooty. However strengthening of conductor was done and damaged insulators were replaced. 2)GPS already sent to OEM for rectification. Quotation received.LPO is being placed.GPS time sync will be completed by 31/08/25. | Complied | Complied
128/II/5 | Tripping of 400kV Bus-1 of 400kV/220kV Chittoor SS of APTRANSCO | 01-02-2025 00:55 | As per the reports submitted, the triggering incident was B-phase CT failure in main bay of 400kV Chittoor Cuddapah line-1 at 400kV/220kV Chittoor SS causing a fault in the 400kV Bus- 1 and 400kV Chittoor Cuddapah line-1. Immediately, 400kV Bus-1 BBP operated and all main breakers connected to 400kV Bus-1 tripped. At the same time, Tie breaker of 400kV Chittoor Cuddapah line-1at Chittoor end also tripped on distance protection as the fault is in the line too. This led to tripping of 400kV Chittoor Cuddapah line-1 | 1.APTRANSCO to check the healthiness of other CTs in the switchyard at Chittoor SS 2.APTRANSCO to furnish the report regarding the equipment failure details to CEA | APTRANSCO | dee2sp:APTRANSCO: 04/04/2025 15:31:00: 1) Values of tan-delta and capacitance of all other CTs are within limits at 400kV SS, Chittoor. 2) Report submitted to CEA by field authorities on 04/04/2025. | Complied | Complied
128/III/11 | 400KV-KRISHNAPATNAM-NELLORE_AP-2 | 03-02-2025 15:58 | As per the reports submitted, 400kV Krishnapatnam Nellore line-2 tripped on maloperation of OV St-1 at Krishnapatnam end and DT was received at Nellore end. At Krishnapatnam end, R-Phase CVT Voltage was showing 5% more than normal value compared to other two phases. While changing Ph-N to PH-PH selection in relay line tripped on overvoltage protection in order to achieve OVR grading with other lines. Tripping needs review. | 1.APGENCO to expedite the CVT replacement works | APGENCO | MARUTHIPRASAD:APGENCO: 05/04/2025 10:17:30: As per recommendations of this forum,on 03.04.25,R-phase CVT has been replaced.Now it is under observation. | Complied | Complied
128/VI/7 | GOOTY - 220KV | 27-01-2025 15:53 | As per the reports submitted, the triggering incident was failure of Y-phase conductor in 220kV Gooty SWS Bus-1 causing a Y-phase fault in Bus-1. Immediately Bus-1 BBP operated and all elements connected to 220kV Gooty Bus-1 tripped. | 1.APTRANSCO to rectify the DR time sync issue at Gooty SS | APTRANSCO | dee2sp:APTRANSCO: 04/04/2025 14:34:52: The defective GPS master clock was already sent to the concerned OEM for rectification. The GPS time synchronization will be implemented by the end of June 2025 after the rectification. dee2sp:APTRANSCO: 03/07/2025 17:31:25: Defective GPS clock was already sent to concerned OEM for rectification. The GPS time sync will be implemented by the end of August-2025 after the rectification. dee2sp:APTRANSCO: 05/08/2025 12:53:25: GPS already sent to OEM for rectification. Quotation received.LPO is being placed.GPS time sync will be completed by 31/08/25. dee2sp:APTRANSCO: 09/12/2025 10:04:36: After rectification GPS kept in service on 16.10.25 | Complied | Complied
129/III/2 | 400KV-KALPAKKA VEMAGIRI_AP-1 | 21-02-2025 16:31 | As per the reports submitted, the 400kV Kalpakka Vemagiri line-1 tripped at Kalpakka end on maloperation of Main-1 relay (Siemens make 7SA52) Zone-1 distance protection. At Vemagiri end, no protection operated and not tripped as there was no fault in the line. Tripping is not in order. | 1.APTRANSCO to furnish the detailed analysis of the event. | APTRANSCO | eesp:APTRANSCO: 07/05/2025 15:45:12: The subject was referred to OEM dee2sp:APTRANSCO: 03/07/2025 17:31:25: Pursuing with the OEM for recommendations. dee2sp:APTRANSCO: 05/08/2025 11:15:24: The DR pertaining to the fault, settings and configuration files pertaining to relay were communicated to M/s Seimens. The relay tested with the same parameters as at the time of the fault (simulating the conditions at the time of fault) and the relay was found to be stable and no mal-operation of relay was observed. The same was communicated to OEM. OEM has instructed to keep the relay under observation and to report if any abnormal tripping occurred. Hence the relay was kept under observation. | Complied | Complied
129/III/12 | 400KV KRISHNAPATNAM RACHAGUNNERI-2 | 17-03-2025 11:24 | As per the report submitted, the triggering incident is the B-N fault and subsequently Y N fault which developed into B-Y fault in 400KV-KRISHNAPATNAM RACHAGUNNERI-2 near to Krishnapatnam end due to broken ground wire and fell on to the line phases. At Krishnapatnam end, the fault was sensed in Z1 during the initial B-N fault, and due to the fault in dead time (Y-N fault) led to 3ph tripping at Krishnapatnam end. At Rachagunneri end, the initial B-N fault was sensed in Z2 and carrier was also received, but trip was not extended (due to suspected PSB block) and later during Y-B fault, the fault was sensed in Z2 and carrier receipt was high (during Y-N fault at remote end) and yet the trip was not extended and eventually tripped on Y-B Z2 time trip. | APGENCO to resolve the issue in Main-1 relay of 400kV-KRISHNAPATNAM-RACHAGUNNERI-2. | APGENCO | APP_SDSTPS4002:APGENCO: 05/05/2025 16:29:44: Relays operation at APGENCO side is fine and there is no issue in both Main-I and Main-II relays and the operation is correct. | Complied | Complied
130/I/4 | Complete Outage of 220/132kV Koduru and Rajampet | 17-03-2025 11:45 | At 11:25 Hrs, the 220 kV Cuddapah-Rajampet line tripped due to a B-N fault. At Cuddapah end, the fault was sensed in Z1, and LBB Retrip operated leading to the 3ph tripping. At Rajampet end, the fault was sensed in Z2, and the carrier-aided protection operated, AR operated and was successful and the line holding at Rajampet. Following the tripping of the 220 kV Cuddapah-Rajampet line, the Koduru and Rajampet section became radially connected to Renigunta. At 11:45 Hrs, the 220 kV Renigunta-Koduru line tripped due to a Y-B fault, with the fault sensed only at Renigunta in Z2 resulting in a 3-phase trip at Renigunta. This caused the complete outage of the 220/132 kV Koduru and Rajampet substations. | APTRANSCO to check the wiring scheme for LBB logic of all feeders at 220kV CK Palli SS. | APTRANSCO | eesp:APTRANSCO: 04/06/2025 16:20:12: At present there is no single phase initiation to LBB protection. It will be provided at 220KV SS CK Palli for all 220KV feeders after upgrading of firmware in relays by M/s GE and the work will be completed within two months. dee2sp:APTRANSCO: 03/07/2025 17:31:25: Correspondence with the company is under progress. dee2sp:APTRANSCO: 06/08/2025 16:04:56: The work of single phase LBB protection function in the Busbar protection relays at 220kV CK Palli is under progress and work will be completed by 04-11-2025. eesp:APTRANSCO: 10/03/2026 15:37:56: Wiring scheme for LBB logic for single phase initiation in Busbar protection is configured for all 220KV feeders at 220KV SS CK Palli by incorporating the new logic relays. Further on 30-01-2026 single phase LBB Protection for all 220KV feeders at 220KV SS CK Palli was commissioned and found healthy. | Pending | Pending
130/IV/18 | 400KVKALPAKKAKHAMMAM_ PG-1 | 12-04-2025 12:16 | As per the reports submitted, the triggering incident is Y-N fault in the line. At Khammam end, the fault was sensed in Z1, AR operated and was successful and due to a subsequent fault in reclaim time (after 50ms) led to 3ph trip. At Kalpakka end, the fault was sensed in Z1 AR did not operate and 3 ph tripped. | APTRANSCO to review Non operation of AR at Kalpakka end | APTRANSCO | dee2sp:APTRANSCO: 03/06/2025 16:58:12: On 30/04/25, Line clear availed and AR operation tested, found in order and kept in observation. On 30/04/25, on the same line AR was operated and tripped due to persistent fault. | Complied | Complied
132/I/1 | Complete outage of 220kV Upper Sileru PH | 19-05-2025 13:52 | During antecedent conditions, 220kV Upper Sileru Balimela was idle charged from Upper Sileru end. As per the reports submitted, the triggering incident was R-N fault in 220kV Donkarai Upper Sileru Line. At Donkarayi end, E/F start was observed in EL and DR and the line tripped but E/F trip was not observed. However, the line was not tripped at Upper Sileru end but the fault was cleared by tripping of 220kV Upper Sileru Pendurthy Line at Pendurthy end on zone-3 protection. At the same time, Lower Sileru Unit-1 and Donkarayi Units tripped. This led to complete outage of 220kV Upper Sileru PH. | APGENCO to ensure availability and maintenance of sufficient relay testing kits at substations to facilitate timely testing and verification | APGENCO | APG_LSPH2:APGENCO: 06/08/2025 15:45:23: Procurement of latest test kit is in Progress. APG_LSPH2:APGENCO: 02/02/2026 15:47:52: Testing kit which is repaired and brought to USPH .so now available to facilitate timely testing at at USPH site | Complied | Pending
132/I/1 | Complete outage of 220kV Upper Sileru PH | 19-05-2025 13:52 | During antecedent conditions, 220kV Upper Sileru Balimela was idle charged from Upper Sileru end. As per the reports submitted, the triggering incident was R-N fault in 220kV Donkarai Upper Sileru Line. At Donkarayi end, E/F start was observed in EL and DR and the line tripped but E/F trip was not observed. However, the line was not tripped at Upper Sileru end but the fault was cleared by tripping of 220kV Upper Sileru Pendurthy Line at Pendurthy end on zone-3 protection. At the same time, Lower Sileru Unit-1 and Donkarayi Units tripped. This led to complete outage of 220kV Upper Sileru PH. | APGENCO to furnish the reasons for Directional Earth Fault (DEF) pickup being observed in only one main relay during the incident at Donkarayi end. | APGENCO | APG_LSPH2:APGENCO: 06/08/2025 15:45:23: Relay testing carried out and found that there is a logic issue in Main-2 (GE make D60) . Hence provided the logic whenever VT fuse fails only the Non-Directional Earth fault protection. | Complied | Pending
132/I/1 | Complete outage of 220kV Upper Sileru PH | 19-05-2025 13:52 | During antecedent conditions, 220kV Upper Sileru Balimela was idle charged from Upper Sileru end. As per the reports submitted, the triggering incident was R-N fault in 220kV Donkarai Upper Sileru Line. At Donkarayi end, E/F start was observed in EL and DR and the line tripped but E/F trip was not observed. However, the line was not tripped at Upper Sileru end but the fault was cleared by tripping of 220kV Upper Sileru Pendurthy Line at Pendurthy end on zone-3 protection. At the same time, Lower Sileru Unit-1 and Donkarayi Units tripped. This led to complete outage of 220kV Upper Sileru PH. | APGENCO to review the relay coordination at Donkarayi, Lower Sileru, and Upper Sileru ends | APGENCO | APG_LSPH2:APGENCO: 06/08/2025 15:45:23: At Lower Sileru end, the Unit's GT Standby Earth Fault settings modified duly coordinated with the line Earth fault settings. At Donkarayi end the negative phase sequence settings modifiedas per the Standards (CBIP). | Complied | Pending
132/I/1 | Complete outage of 220kV Upper Sileru PH | 19-05-2025 13:52 | During antecedent conditions, 220kV Upper Sileru Balimela was idle charged from Upper Sileru end. As per the reports submitted, the triggering incident was R-N fault in 220kV Donkarai Upper Sileru Line. At Donkarayi end, E/F start was observed in EL and DR and the line tripped but E/F trip was not observed. However, the line was not tripped at Upper Sileru end but the fault was cleared by tripping of 220kV Upper Sileru Pendurthy Line at Pendurthy end on zone-3 protection. At the same time, Lower Sileru Unit-1 and Donkarayi Units tripped. This led to complete outage of 220kV Upper Sileru PH. | APTRANSCO to rectify the DR time sync issue at Pendurthy end. | APTRANSCO | dee2sp:APTRANSCO: 07/08/2025 17:04:15: The administrative approval was accorded for providing 1 no. GPS equipment at 220kV Pendurthy SS. The work will be completed within 4 months from the date of allotment of material. | Pending | Pending
132/II/2 | Tripping of 220kV Bus-2 of 220kV/132kV Chillakallu SS of APTRANSCO | 24-05-2025 03:37 | As per the reports submitted, the triggering incident was R-N fault in 220kV Chillakallu VTPS Line-2. At Chillakallu end, the breaker failed to open and LBB operated. All elements connected to 220kV Chillakallu Bus-2 tripped | APTRANSCO to recity the DR time sync issue at Chilakallu SS | APTRANSCO | dee2sp:APTRANSCO: 07/08/2025 18:50:38: Time synchronisation was commissioned for all 220KV Inter-state feeder bays at 220KV Chillakallu SS. Indent has already been raised for remaining 220 KV bays. Time synchronisation will be arranged for the remaining 220KV bays in a few weeks dee2sp:APTRANSCO: 08/12/2025 12:33:20: Completed on 15-11-25. | Complied | Complied
132/II/2 | Tripping of 220kV Bus-2 of 220kV/132kV Chillakallu SS of APTRANSCO | 24-05-2025 03:37 | As per the reports submitted, the triggering incident was R-N fault in 220kV Chillakallu VTPS Line-2. At Chillakallu end, the breaker failed to open and LBB operated. All elements connected to 220kV Chillakallu Bus-2 tripped | APTRANSCO to verify the reason for non-tripping of Kondapalli-2 line at Kondapalli end on receipt of DT | APTRANSCO | dee2sp:APTRANSCO: 07/08/2025 18:50:38: The wiring pertaining to DTT protection of 220KV Chillakallu-Kondapalli-2 feeder at Kondapalli SS was found ok. However, the reason for non-tripping on 'Receiving On' DT at Kondapalli end will be confirmed by availing the LC on or before 20-08-2025. dee2sp:APTRANSCO: 20/08/2025 12:29:48: On 19-08-2025 LC was availed on 220KV Chillakallu -Kondapalli-2 Feeder, Initially Wiring at both ends of the feeder was ensured and found Ok. DTT signals were checked from both the ends, and found that operation of DTT function is healthy and satisfactory | Complied | Complied
132/IV/3 | 220KV-ASUPAKA-LOWER_SILERU-1 | 05-06-2025 12:26 | As per the reports submitted, the triggering incident was the R-G Fault in the line. The fault distance from Lower sileru end was 76.8kms. At Lower sileru end, the line tripped on Z2 distance operation, A/R not operated. At Asupaka end, the falt was sensed in Z1, A/R operated and R- pole opened. Non operation of A/R at Lower Sileru end needs review. | APGENCO to furnish the detailed report for Non-operation of AR. | APGENCO | APG_LSPH2:APGENCO: 06/08/2025 15:56:45: Due to non receipt of carrier signal, AR not operated at LSPH end. The same was informed to APTRANSCO, Telecom department during recent vist to LSPH. At present carrier found to be healthy. During recent tripping incidents, AR operated successfully. | Complied | Complied
133/I/7 | Complete Outage of 220kV Upper Sileru PH of APGENCO | 17-07-2025 15:37 | During antecedent conditions, 220KV Upper Sileru- Donkarayi Feeder was under LC. As per the reports submitted, the triggering incident was B-N fault in 220kV Uppper Sileru Pendurthy line and the line tripped. Tripping of the only connected line led to complete outage of 220kV Upper Sileru PH of APGENCO | APGENCO to review the Distance Coordination of relays at Upper sileru end. | APGENCO | APG_LSPH2:APGENCO: 03/09/2025 20:10:09: The feeder relay settings were implemented as per APTRANSCO communicated settings. | Complied | Pending
133/I/7 | Complete Outage of 220kV Upper Sileru PH of APGENCO | 17-07-2025 15:37 | During antecedent conditions, 220KV Upper Sileru- Donkarayi Feeder was under LC. As per the reports submitted, the triggering incident was B-N fault in 220kV Uppper Sileru Pendurthy line and the line tripped. Tripping of the only connected line led to complete outage of 220kV Upper Sileru PH of APGENCO | APGENCO to update the settings in DNMS portal. | APGENCO | APG_LSPH2:APGENCO: 03/09/2025 20:10:09: We will upload the updated relay settings in the DNMS portal within one week. | Complied | Pending
133/I/7 | Complete Outage of 220kV Upper Sileru PH of APGENCO | 17-07-2025 15:37 | During antecedent conditions, 220KV Upper Sileru- Donkarayi Feeder was under LC. As per the reports submitted, the triggering incident was B-N fault in 220kV Uppper Sileru Pendurthy line and the line tripped. Tripping of the only connected line led to complete outage of 220kV Upper Sileru PH of APGENCO | APTRANSCO to rectify the DR time sync issue at Pendurthy end. | APTRANSCO | eesp:APTRANSCO: 03/09/2025 10:42:48: At present there is no time sync equipment available at Pendurthy SS. Administrative approval for procurement of the same was accorded and it will be provided within 4 months from the date of allotment of material. | Pending | Pending
133/I/7 | Complete Outage of 220kV Upper Sileru PH of APGENCO | 17-07-2025 15:37 | During antecedent conditions, 220KV Upper Sileru- Donkarayi Feeder was under LC. As per the reports submitted, the triggering incident was B-N fault in 220kV Uppper Sileru Pendurthy line and the line tripped. Tripping of the only connected line led to complete outage of 220kV Upper Sileru PH of APGENCO | APTRANSCO to review the Distance Coordination of relays at Pendurthy end . | APTRANSCO | eesp:APTRANSCO: 03/09/2025 10:40:04: Distance relay coordination at Pendurthy end were reviewed recently (November-2024) and the same were adopted at Pendurthy end accordingly. | Complied | Pending
133/IV/5 | 220KV-ASUPAKA-LOWER_SILERU-1 | 15-07-2025 11:20 | As per the reports submitted, the triggering incident was B-G fault in the line. The fault distance from Asupaka end was 42kms and from Lower Sileru end was 76.6kms. At Asupaka end, the fault was sensed in Z1. A/R operated and the line tripped due to subsequent fault during A/R reclaim time. At Lower Sileru end, the fault was sensed in Z1. A/R did not operate and the line tripped. Tripping is not in order. | APGENCO to furnish the detailed report regarding non operation of A/r at Lower Sileru end | APGENCO | APG_LSPH2:APGENCO: 03/09/2025 09:37:32: AR did not operated because of Main-1 relay carrier fail.The carrier fail intimated to the APTRANSCO Telecom. After the carrier local PLCC panel found OK.Present the carrier healthy at Lower Sileru End. | Complied | Complied
134/I/7 | Complete Outage of 220kV Vijayawada SS | 13-08-2025 19:40 | During antecedent conditions, 220kV Vijayawada Gudivada Line-1 and 220kV Vijayawada Bus-2 were under LC. As per the reports submitted, the triggering incident was Y-phase isolator failure in 220kV Vijayawada Bhimadole Line-1 causing a Y-N fault in 220kV Vijayawada Bus-1. Immediately, 220kV Vijayawada Bus-1 BBP operated and all elements connected to 220kV Bus-1 tripped. Since all elements are connected to 220kV Bus-1, Bus-1 outage led to complete outage of 220kV Vijayawada SS. | APTRANSCO to rectify the DR time sync issue at 220kV Nunna SS. | APTRANSCO | dee2sp:APTRANSCO: 03/10/2025 10:43:03: Rectified on 14/08/2025 by replacing the existing failed IRIG-B card in BBP relay ( P741 type) by replacing with healthy one. | Complied | Complied
134/II/1 | Tripping of 220kV Bus-1 of 220kV Pendurthi SS of APTRANSCO | 31-07-2025 08:52 | As per the reports submitted, the triggering incident was B-G fault in 220kV Bus-1 of 220kV Pendurthi SS. Immediately, 220kV Bus-1 BBP operated and all elements connected to 220kV Bus-1 tripped leading to the tripping of 220kV Bus-1 of 220kV Pendurthi SS of APTRANSCO | APTRANSCO to ensure strict adherence to SOP during Maintainance activities | APTRANSCO | eesp:APTRANSCO: 03/10/2025 10:30:25: Strict adherence to SOP during the maintenance activities will be ensured. | Complied | Pending
134/II/1 | Tripping of 220kV Bus-1 of 220kV Pendurthi SS of APTRANSCO | 31-07-2025 08:52 | As per the reports submitted, the triggering incident was B-G fault in 220kV Bus-1 of 220kV Pendurthi SS. Immediately, 220kV Bus-1 BBP operated and all elements connected to 220kV Bus-1 tripped leading to the tripping of 220kV Bus-1 of 220kV Pendurthi SS of APTRANSCO | APTRANSCO to rectify the DR time sync issue at 220kV Pendurthy end | APTRANSCO | eesp:APTRANSCO: 03/10/2025 10:29:19: At present is no time syn equipment available at 220kV Pendurthy SS. Procurement process was started. It will be provided within 4 months from the date of allotment of material. | Pending | Pending
135/I/7 | Complete Outage of 220kV Bobbili SS of APTRANSCO | 09-09-2025 15:39 | As per the reports submitted, the triggering incident was B-Phase jumper failure in 220KV Maradam-Bobbili line-2. At Maradam end, 220kV Maradam Bobbili Line-1 tripped on IN>1 trip due to imbalance neutral current and Subsequently, 220kV Garividi Bobbili Line-1 tripped on Negative Sequence protectionI2>1 trip) at Bobbili end. Cpnsequentlly, 132KV Bobbili- Bobbili line-1&2 and 220kV/132kV Bobbili PTRs tripped on E/F protection. At 15:39.41hrs, 220kV Maradam Bobbili Line-2 tripped at Maradam end on IN>1 trip. Tripping of all the lines connected to 220kV Bobbili SS led to complete outage of the substation. | 1.APTRANSCO to review the protection settings of PTR at 220kV Bobbili. 2.APTRANSCO to ensure that all protection settings are reviewed during internal audit. | APTRANSCO | eesp:APTRANSCO: 04/11/2025 11:52:10: 1) PTR settings at 220kV Bobbili SS were reviewed and are found in order. 2) APTRANSCO will ensure that, all protection settings will be reviewed during internal audit. | Complied | Complied
135/III/20 | 400KV-SIMHADRI-KALPAKKA-3 | 18-09-2025 18:51 | As per the reports submitted the triggering incident was B-phase fault in the vicinity where in at Simhadri end Z3 was sensed and B phase isolator for 400kV Simhadri-Kalpakka-3 opened at Simhadri end opened and hence B phase current became zero and reflected in neutral leading to DEF operation. At Kalpakka end, 400KV Kalapaka-Simhadri-3 line got tripped at Kalpakka end on DT receive signal. | APTRANSCO to check the healthiness of all the jumpers in Kalpakka SS. | APTRANSCO | eesp:APTRANSCO: 04/11/2025 10:15:09: All the jumpers were checked and tightened the nut & bolts and are in healthy condition. | Complied | Complied
135/III/22 | 220KV-ASUPAKA-LOWER_SILERU-1 | 19-09-2025 12:09 | As per the reports submitted, the triggering incident was R-N fault. The fault distance from Asupaka end was 16.1kms and from Lower Sileru end it was 91.4kms. At Asupaka end, the fault was sensed in Zone-1 and A/R was initiated but A/R did not operate and 3ph tripped, where in continuously Z1 operation was observed to be high and phase select AC was high. At Lower Sileru end, the fault was sensed in Zone-2 and carrier was received and A/R operated but ToR did not operate and fault was sensed in Z2 and Z2 time tripped. | APGENCO to discuss the ToR settings with the APTRANSCO and enable the ToR for the Zone1 and Zone 2 as well | APGENCO | APG_LSPH2:APGENCO: 07/11/2025 15:11:06: In Main-1 Relay , The TOR Setting Enabled for Zone-1 & Zone-2. APG_LSPH2:APGENCO: 05/01/2026 21:49:26: AS per the PCSC meeting Recommendations the TOR setting enabled in Main-1 Relay completed. | Complied | Complied
135/IV/9 | 400KV-KRISHNAPATNAM-RACHAGUNNERI-2 | 19-09-2025 20:25 | As per the reports submitted, the triggering incident was Y-N fault. The fault distance from krishnapatnam was 40.9kms and from Rachagunneri end was 54.2kms. At Krishnapatnam end, the fault was sensed in Zone-1 and Due to CB trouble (Spring charge circuit problem) in Bay Control Unit AR is not operated. At Rachagunneri end, the fault was sensed in Zone-1. Here AR operated and the tripping was in order. | APGENCO to furnish detailed report regarding non operation of A/R | APGENCO | APP_SDSTPS4002:APGENCO: 19/01/2026 16:18:46: 1. New wiring carried for Spring Charge Motor Circuit in place of the failed circuit for 406 (Main CB) Breaker 2.Replacement of Spring Charge Motor completed for 405 Tie Breaker | Complied | Complied
135/VI/22 | 400KV-KRISHNAPATNAM-RACHAGUNNERI-2 | 19-09-2025 20:25 | 400KV-KRISHNAPATNAM-RACHAGUNNERI-2 | APGENCO to rectify the DR time synchronization issue at KRISHNAPATNAM - 400KV | APGENCO | APP_SDSTPS4002:APGENCO: 19/01/2026 11:06:16: DR TIME SYNCHRONIZATION ISSUE AT KRISHNAPATNAM SIDE IS RECTIFIED | Complied | Complied
136/III/1 | 400KVKRISHNAPATNAMNELLORE_ AP-1 | 27-09-2025 14:28 | As per the reports submitted, the triggering incident is the tripping of the 400KVKRISHNAPATNAM- NELLORE_AP-1 at Nellore end only due to operation of Main- 2 86 operation and 3ph tripped. The line was holding from KRISHNAPATNAM end. | APTRANSCO to follow the SOP during the maintenance of the relays. | APTRANSCO | dee2sp:APTRANSCO: 01/12/2025 12:37:39: Vide Lr. No. CE/ Plg, PS/ SE(PS)/ EE(SP&PSCC)/ DEE-II/F.66 (Vol-2) /D. No. 335 /2025,Dt.04-11-2025, the following was informed to the concerned to follow in such cases to avoid unwarranted trippings. 1) Necessary permission maybe obtained from SRLDC through APSLDC (with an intimation to system protection wing, Vidyut soudha) for keeping the Main-2 protection relay in out/test mode such that it will not extend tripping while carrying testing/ taking remedial actions duly ensuring healthiness of all other protection systems. (OR) 2) Necessary testing/remedial action may be carriedout duly availing shutdown. | Complied | Complied
136/IV/1 | 220KV-ASUPAKALOWER_ SILERU-1 | 21-09-2025 14:05 | As per the reports submitted, the triggering incident was B-G fault in the line. The fault distance from Lower Sileru end was 78.14kms in Z1 and AR did not get operated and 3ph tripped. At Asupaka end, the line tripped on Z1 distance protection operation AR operated and was successful and the line was holding. | APGENCO to rectify the non-operation of AR at LOWER SILERU end. | APGENCO | APG_LSPH2:APGENCO: 04/01/2026 19:13:54: the GE support Engineer suggested to change Trip output function 3-pole&1-pole in place of 3-Pole only in the D60 Relay(GE make). Changed and kept under observeation. | Complied | Complied
136/VI/11 | 400KV-RAYALSEEMA TPP-KALIKIRI-2 | 02-10-2025 20:27 | RAYALSEEMA TPP - 400KV | APGENCO to rectify the DR Time Synchronization Issue at RAYALSEEMA TPP - 400KV. | APGENCO | MARUTHIPRASAD:APGENCO: 05/12/2025 10:10:11: GPS clock system has been checked and found normal. | Complied | Complied
136/VI/24 | 220KV-SRISAILAM_RIGHT_BANKNAGARJUNASAGAR_ TS-1 | 08-10-2025 20:44 | SRISAILAM_RIGHT_BANK - 220KV | APGENCO to rectify the DR Time Synchronization Issue at SRISAILAM_RIGHT_BANK - 220KV. | APGENCO |  | Pending | Pending
137/I/9 | Complete Outage 220kV Naidupeta of APTRANSCO | 21-10-2025 02:53 | 220V Naidupeta SS was being radially from 220kV Rachagunneri Naidupeta Line-1&2. As per the reports submitted, the triggering incident was B-N fault in 220kV Rachagunneri Naidupeta Line-2 at 02:46hrs At both ends, the fault was sensed in zone-1. A/R operated and the line tripped on persistent fault. At the same time, the same fault was sensed in Zone-1 and R-pole opened at Naidupeta end in 220kV Rachagunneri Naidupeta Line-1. After around 1.5seconds other two poles opened on suspected PD relay. Tripping of both lines at Naidupeta end led to complete outage of 220kV Naidupeta SS. | APTRANSCO to update the relay settings in DMNS portal at Naiudupeta SS. | APTRANSCO | dee2sp:APTRANSCO: 07/01/2026 09:50:19: Relay settings were uploaded in DMNS portal vide ticket no.5966 | Complied | Complied
137/I/10 | Complete Outage of 220kV Setipali SS of APTRANSCO | 25-10-2025 17:10 | As per the reports submitted, the triggering incident was CT cable issue in 220kV Setipali RTSS Veludurthy feeder causing BBP to maloperate at 220kV Setipali end. Immediately all elements connected to 220kV Bus tripped. Since 220kV Setipali is operating with SIngle bus configuration this led to complete outage of 220kV Setipali SS. | 1.APTRANSCO to rectify the DR time sync issue at Setipally SS. 2.APTRANSCO to update the RTSS Veldurthy feeder details in DMNS portal. | APTRANSCO | dee2sp:APTRANSCO: 07/01/2026 09:50:19: 2.RTSS Veldurthy feeder details were uploaded in DMNS portal with ticket no.5967. eesp:APTRANSCO: 07/01/2026 09:53:55: 1) DR Time sync at Settipally SS will be provided soon. | Pending | Pending
137/I/12 | Complete Outage of 220kV Upper Sileru PH of APGENCO | 05-11-2025 03:33 | As per the reports submitted, 220kV Upper Sileru PH is operating with single bus with transfer bus configuration. The triggering incident was RY fault lin 220kV Upper Sileru Balimela line. At the same time, 220kV BBP maloperated and all elements connected to the 220kV Bus tripped. This led to complete outage of 220kV Upper Sileru PH. There was no generation at 220kV Upper Sileru PH during antecedent conditions. | 1.APGENCO to review the BUSBAR settings at Upper sileru end. 2.APGENCO to configure the DR as per FOLD committee recommendations at Upper sileru end. | APGENCO | APG_USPH1:APGENCO: 06/01/2026 14:03:42: 1.The Bus Bar Protection settings at USPH end is reviewed and configured in line with the methodologies protection schemes practiced by APTRANSCO 2.The DR configuration will be completed with in the next 10 days in line with the FOLD committee recommendations at USPH end | Complied | Complied
137/II/3 | Tripping of 220kv Bus-1 & Bus-2 of 220kV Peddapuram SS of APTRANSCO | 22-10-2025 00:30 | As per the reports submitted, the triggering incident was failure in CT in 220kV Peddapuram Relaince Line-1 at 220kv Peddapuram SS. The scattered parts of CT caused Y-N fault in 220kV Bus-1 and RY-N fault in 220kV Bus-2. Both Bus-1 and Bus-2 BBP operated causing loss of power supply to 20kV Bus of 220kV Peddapuram SS. 132kV bus was intact during the event. | 1.APTRANSCO to report CT equipment failure to CEA. 2.APTRANSCO to enable Auto reclosure in Reliance feeder. | APTRANSCO | eesp:APTRANSCO: 07/01/2026 09:53:55: 1) CT failure report will be send to CEA soon. 2) AR not enabled due to non availability of carrier equipment at reliance end. PCSC recommendation will be communicated to Reliance for necessary action. dee2sp:APTRANSCO: 03/02/2026 12:40:13: 2)AR enabled at APTRANSCO end and informed to the other end to enable AR at their end dee2sp:APTRANSCO: 03/02/2026 17:14:42: CT failure report sent to CEA on 03/02/2026. | Complied | Complied
137/II/4 | Tripping of 400kV Krishnapatnam Bus-1 of APGENCO | 23-10-2025 19:50 | As per the reports submitted, the triggering incident was an RYB fault at the 400 kV Krishnapatnam Bus-1, caused by a broken guard wire falling on Bus-1, resulting in a three-phase fault. Consequently, the 400 kV Bus-1 busbar protection operated, and all elements connected to Bus-1 tripped. Simultaneously, Unit-1 and Unit-2 tripped due to LT supply disturbance caused by a severe dip in the three-phase voltages. This led to the loss of power supply to the 400 kV Krishnapatnam Bus-1. | APGENCO to ensure regular periodic monitoring of switchyard through Thermovision camera / Drone cameras etc. | APGENCO | APP_SDSTPS4002:APGENCO: 19/01/2026 16:14:02: ALL GANTRY TOWER TOP LOCATION S VISUIAL INSPECTION CARRIED OUT AND BASED ON PHOTOS COLLECTED DECISION WAS TAKEN TO REPLACE GUARD WIRE FOR ENTIRE SWITCHYARD APP_SDSTPS4002:APGENCO: 19/01/2026 16:14:38: ALL GANTRY TOWER TOP LOCATION S VISUIAL INSPECTION CARRIED OUT AND BASED ON PHOTOS COLLECTED DECISION WAS TAKEN TO REPLACE GUARD WIRE FOR ENTIRE SWITCHYARD | Complied | Complied
137/II/6 | Tripping of 220kv Bus of 220kV Markapur SS of APTRANSCO | 29-10-2025 00:55 | As per the reports submitted, the triggering incident was B-N fault in 220kV Srisailam RB Markapur Line-1. At Markapur end, breaker failed to open causing LBB to operate. All elements connected to 220kV Markapur Bus tripped. 132kV Bus was intact during the event. | 1.APTRANSCO to rectify the DR time sync issue at Markapur SS. 2.APTRANSCO to configure DR mapping as per FOLD committee recommendations at Markapur SS. | APTRANSCO |  | Pending | Pending
137/II/6 | Tripping of 220kv Bus of 220kV Markapur SS of APTRANSCO | 29-10-2025 00:55 | As per the reports submitted, the triggering incident was B-N fault in 220kV Srisailam RB Markapur Line-1. At Markapur end, breaker failed to open causing LBB to operate. All elements connected to 220kV Markapur Bus tripped. 132kV Bus was intact during the event. | 3.APGENCO to ensure carrier healthiness at Srisailam RB end. | APGENCO |  | Pending | Pending
137/II/7 | Tripping of 220kV Bus-2 of 400kV VTPS Generating Stations | 31-10-2025 10:01 | As per the reports submitted, the triggering incident was RY fault in 220kV VTPS Bus-2 while taking 220kV VTPS Piduguralla Line-2 under shutdown. Immedeately, 220kV VTPS Bus-2 operated and all elements connected to 220kV Bus-2 trippe | APGENCO to ensure healthiness of Mechanical and Electrical Interlocking between Isolator and CB. | APGENCO | APG_NTTPS2202:APGENCO: 02/02/2026 12:41:36: Interlocks have been provided so that isolator will not open if there is no CB open status. | Complied | Complied
137III/7 | 400KV/220KV NELLORE_AP-ICT-2 | 28-10-2025 17:59 | As per the reports submitted, at Nellore end, OSR caused initiation of trip signal due to moisture ingresses into the Y-phase OLTC. Recently numerical relays retrofitted in place of old Electro mechanical relays and external signals to be configured. | APTRANSCO to check the condition of all other OSR terminal box sealing and to avoid water ingress | APTRANSCO | dee2sp:APTRANSCO: 07/01/2026 09:48:05: The terminal boxes of all phases of OSRs of ICT-2 were properly fitted and sealed with silicon sealant & M-Seal mixture to avoid any future ingress of moisture. Further. the OSRs of all other ICTs are being checked and properly fitted during the scheduled shutdowns carried out periodically. | Complied | Complied
137/IV/1 | 400KV-KRISHNAPATNAM-RACHAGUNNERI-1 | 21-10-2025 12:50 | As per the reports submitted, the triggering incident was B-G fault in the line. The fault distance from Krishnapatnam end was 58.25kms and from Rachagunneri end was 29.32kms. At Krishnapatnam end, the fault was sensed in Z1, A/R operated and tripped due to persistent fault. After around 80ms, A/R operated again in R and Y phases and R-N fault was observed in Zone-1 and the line tripped. At Rachagunneri end, the fault was sensed in Z1, A/R operated and CB tripped on SOFT due to persistent fault. Tripping is in order | APGENCO to check A/R issue at Krishnapatnam end | APGENCO |  | Pending | Pending
138/I/3 | Complete Outage of 220kV Naidupeta SS of APTRANSCO | 14-12-2025 07:07 | 220kV Naidupeta SS is being radially fed through 220kV Rachagunneri Naidupeta Line-1&2. As per the reports submitted, the triggering incident was Y-G fault in 220kV Naidupeta Rachagunneri Line-2 where in during AR operation, the fault YB fault in both 220kV Naidupeta Rachagunneri Line-1&2, 220kV Naidupeta Rachagunneri Line-2 tripped on both ends on persistent fault and 220kV Naidupeta Rachagunneri Line-1 tripped on Z1 at only Rachagunneri end leading to Complete Outage of 220kV Naidupeta SS of APTRANSCO | APTRANSCO to appraise the mamngaement on frequent failures of insulators | APTRANSCO | dee2sp:APTRANSCO: 03/02/2026 16:59:22: It is proposed for replacement of existing 220kV,120kN SRC insulators at all cut points from loc no.01 to 69 to avoid frequent breakdowns in 220kV DC lines from 400kV SS Rachagunneri to 220kV SS Naidupeta. Tenders floated and evaluation is under process. The work will be completed within 4 months after awarding the work. dee2sp:APTRANSCO: 04/02/2026 10:09:03: From Loc no. 70-110, at all cut point towers all the 220kV, 120kN SRC insulators were replaced on 16/11/2025. | Complied | Complied
139/VI/16 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1 | 19-01-2026 13:13 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1 | APGENCO to rectify the DR time synchronization issue at SRISAILAM_RIGHT_BANK - 220KV | APGENCO | APG_SRB2:APGENCO: 28/03/2026 09:21:48: Work Completed and Time Sync done in DECEMBER-2025 and same communicated in SRPC meeting. | Pending | Pending
140/III/8 | 400KV/220KV CUDDAPAH-ICT-3 | 30-01-2026 11:44 | As per the reports submitted, the triggering incident is the tripping of 400KV/220KV CUDDAPAH-ICT-3 only at HV side due to the external LBB operation during the testing activities which were being carried out at CUDDAPAH(AP) during the wiring scheme implementation for Single Phase LBB logic (as per information received from APTRANSCO). During pre-configuration works, the tripping was disabled temporarily by disconnecting positive trip links for all 220kV feeders including PGCIL-I, 2&3 at 220kV CUDDAPAH (AP) station. 96 operation of PGCIL-3 at CUDDAPAH (AP) signal was taken for group relay tripping at PGCIL end and due to oversight, the said signal was not disabled at CUDDAPAH (AP) which led to the tripping of the ICT. | APTRANSCO to ensure SOP during testing activities. | APTRANSCO | dee2sp:APTRANSCO: 08/04/2026 12:16:25: It is to submit that, PCSC recommendation was communicated to the concerned and they informed that they will ensure the SOP during testing of all protection activities. | Complied | Complied
140/VI/19 | 220KV-CHITTOOR_AP-THIRUVALAM_TN-1 | 19-02-2026 18:00 | 220KV-CHITTOOR_AP-THIRUVALAM_TN-1 | APTRANSCO to rectify the DR time synchronization issue at CHITTOOR_AP - 220KV | APTRANSCO |  | Pending | Pending
141/VI/10 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1 | 01-03-2026 12:10 | Station at which DR time synchronisation was not observed SRISAILAM_RIGHT_BANK - 220KV | APGENCO to rectify the DR time synchronization issue at SRISAILAM RIGHT BANK - 220KV | APGENCO |  | Pending | Pending
TELANGANA
93/I/4 | . | 20-08-2020 at 22:25 Hr | As reported, fire broke out at 400 kV Srisailam LB station of TSGENCO. All running units at Srisailam LB tripped one after another. All connected lines at Srisailam LB station tripped at remote end on Zone-2, distance protection and DT also received. Oscillations were also observed from 22:24 Hr. to 22:46 Hr. in Southern Region during the event. Oscillations died out after tripping of all the running units at Srisaila LB | TSGENCO to submit a detailed report and suggestions of their technical enquiry committee for information and discussion in the PCSC forum. | TGGENCO |  | Pending | Pending
97/I/7 | . | 24-06-2021, 19:25 hrs. | Triggering incident was fire in HV side B-ph LA stack of 400/220kV ICT-1. Because of this, all the ICTs along with 400kV, 220kV feeders were hand-tripped as per the SLDC instructions. This resulted in complete outage of 400/220 kV Mamidipally SS. | TSTRANSCO to submit a detailed Action Taken Report w.r.t. the Fire Incident at their 400/ 220 kV Mamidipalli SS including the measures proposed at other (old) TSTRANSCO substations facing similar issues. | TGTRANSCO | deprotection1:TGTRANSCO: 03/06/2024 12:01:34: The failed transformer was replaced with the transformer diverted from veltoor and charged on 27-03-2024. | Pending | Pending
101/II/9 | . | 14-02-2022 at 07:35 hrs | As per the report submitted, triggering incident was fault in 220kV Gajwel - Medchal Line-2. At the same time BBP of Buses - 1 & 2 operated at 220 kV Gajwel resulting in the tripping of all elements connected to the buses. | TSTRANSCO to configure sending of DT to remote end in case of LBB protection operation | TGTRANSCO | deprotection1:TGTRANSCO: 03/06/2024 12:01:34: The proposal for configuring the DT for operation of LBB in 220kV substations will be taken up with the board and will be implemented in all the 220kV substations after approval from the board. | Pending | Pending
108/II/30 | . | 07-06-2023 07:18 | . | TSGENCO to take up with OEM for blocking the Distance protection during VT fuse fail condition. | TGGENCO | PROTECTION.HPC:TGGENCO: 27/07/2024 11:11:05: TGGENCO: TGGENCO was consulted with the OEM (GE) for the blocking of the Distance protection during VT fuse fail condition and blocking of the distance protection during VT fuse fail was already adopted in the protection relay and working normal. PROTECTION.HPC:TGGENCO: 08/02/2025 14:10:52: TGGENCO was consulted with the OEM (GE) for the blocking of the Distance protection during VT fuse fail condition and blocking of the distance protection during VT fuse fail was already adopted in the protection relay and working normal. | Complied | Complied
113/II/3 | Tripping of 400kV Bus-2 of 400kV Boopalpally Generating station of TSGENCO | 26-10-2023 05:25 | As per the reports submitted, while synchronizing the GT-2, the triggering incident was an R-phase Breaker flash over in GT-2 of 400kV Boopalpally causing an arc across the R-phase of the breaker which led to a high resistance R-N fault between 400kV Bus-2 and GT-2. 400kV Boopalpally Warangal Line-1&2, 400kV Boopalpally Chandlapur Line-2 and Boopalpally Generator Transformer-1 cleared the fault on operation of DEF protection. Immediately, after the tripping of the Main and Tie breakers of 400kV Boopalpally Chandlapur Line -2, 400kV Boopalpally Chandlapur Line-1 was no longer feeding the fault as the line was on 400kV Bus-1 and the fault was on 400kV Bus-2. Therefore, all the elements connected to 400kV Boopalpally generating station tripped except 400kV Boopalpally Chandlapur Line-1. This resulted in the tripping of 400kV Bus-2 of the 400kV Boopalpally Generating station. At the same oscillations were observed at nearby substations and the plot is attached for reference. | 1.TSGENCO to explore the possibility of breaker flashover protection and submit report in this regard. 2.TSGENCO to ensure the healthiness of Bus bar Protection relay. | TGGENCO | DEEM.KTPPII:TGGENCO: 06/08/2024 17:46:54: 1.Tggenco-Ktpp - we enquired with no. of generating stations regarding the same issue , but We are not found any breaker flash-over protection implemented practically and after this incident we are having regular practice that every time cleaning the Generator Breaker with DM water before sync the Generator . we are still studying the possibility of implementing breaker flash-over protection. 2.Busbar relays tested and found healthy. | Complied | Complied
114/III/2 | 220kV ASUPAKA - LOWER_SILERU-1 | 04-Dec-2023 16:49:00 | As per the reports submitted, the triggering incident was B-N fault in the line at a distance of 33.73km from Asupaka end and 76km from Lower Sileru end. At Asupaka end, the fault was sensed in zone-1, A/R failed to operate due to problem in BCU. At Lower Sileru end, the fault was sensed in carrier aided zone-2, A/R operated but the line tripped due to persistent fault. Non operation of A/R at Asupaka end needs review | TSTRANSCO to expedite the BCU replacement works. | TGTRANSCO | deprotection1:TGTRANSCO: 03/06/2024 12:01:34: At present the BCU software upgradation is going on and the BCUs replacement will be done by the end of June-2024. deprotection1:TGTRANSCO: 21/09/2024 11:27:25: BCU is replaced and A/R operations are successful at Asupaka end. | Complied | Complied
115/II/1 | Tripping of 400kV Bus-2 and 400kV Manuguru Generating sta-tion of TSGENCO | 14-12-2023 06:30 | As the reports submitted, the triggering incident was maloperation of 400kV Bus-2 LBB. Immediately, all the elements connected to the 400kV Bus-2 tripped. Upon inspection, no external flashovers or equipment damage were found. CU-A and its connected PU-As did not detect any issues with the bus bar protection system, while CU-B and its associated PU-Bs did. Detailed operational data from DRs revealed that the fault current spike of 6.7kA in PU-B of Bay 415 triggered the Zone-2 bus bar protection in CU-B, but no faults were detected in Zone-2 of CU-A, suggesting a possible malfunction in PU-B. DRs also showed the activation of internal LBB back trips in PU-Bs and subsequent tie breaker trips. | TSGENCO to expedite the process for replacement of relay and intimate SRPC/SRLDC on re-placement of relay. | TGGENCO | mrt.btps:TGGENCO: 16/05/2024 10:35:01: Relay was tested and found normal. Spare relay procured, However, It will replaced during Bus LC in next opportunity. mrt.btps:TGGENCO: 10/06/2024 10:20:02: At the time of occurrence of fault and subsequent investigation the relay sensed the current.Sensing was non sinusoidal and hence felt relay was faulty. However after restoration detailed study and inspection was carried out on 415 PU-B relay and it was observed that the earthing connection to Neutral wire link was in open condition. Closed the earth link and relay was thoroughly tested and found normal. During the recent actual Busbar operation also the relay acted normally on 21.05.2024.During Bus LC on 22.05.2024 relay tested again and found normal. Hence it can be concluded that replacement of relay is not required and relay is healthy and working satisfactorily and found normal. | Complied | Complied
115/III/6 | 400kV RAMADUGU GAJWEL 2 | 03-01-2024 23:42 | Line tripped only at Gajwel end on operation of Z3 SOTF due to sus-pected issue in 52XC relay | TSTRANCO to disable SOTF operation in Zone-3. | TGTRANSCO | deprotection1:TGTRANSCO: 03/06/2024 12:01:34: SOTF is disabled for Zone-3 operation on 26-02-2024. deprotection1:TGTRANSCO: 21/09/2024 11:27:25: As already informed vid e Email dated 03-06-2024, SOTF for Zone-3 was disabled on 26-02-2024. | Complied | Complied
115/III/6 | 400kV RAMADUGU GAJWEL 2 | 03-01-2024 23:42 | Line tripped only at Gajwel end on operation of Z3 SOTF due to sus-pected issue in 52XC relay | TSTRANSCO to expedite the replacement of the 52XC relay inform the same SRPC/SRLDC. | TGTRANSCO | deprotection1:TGTRANSCO: 03/06/2024 12:01:34: The 52XC relay contactor was replaced on 26-02-2024. deprotection1:TGTRANSCO: 21/09/2024 11:27:25: As already informed vid e Email dated 03-06-2024, 52XC was replaced on 26-02-2024 | Complied | Complied
115/VI/3 | 400/220 kV ICT-2 AT SURYAPET | 08-01-2024 15:05 | DR Time sync issue at SURYAPET | TSTRANSCO to expedite the procurement of GPS. | TGTRANSCO | deprotection1:TGTRANSCO: 03/06/2024 12:01:34: New GPS was procured and all the relays were GPS time synchronized on 06-05-2024. deprotection1:TGTRANSCO: 21/09/2024 11:27:25: As already informed vide Email dated 03-06-2024, GPS is installed and all relays are time synchronized. | Complied | Complied
116/IIII12 | 220KV KTPS-NUNNA | 18-02-2024 15:08 | The triggering incident was RY fault in the line. At Nunna end, the line tripped on the operation of the Zone-2-time trip. Non-operation of carrier-aided zone-2 protection needs review. | 1.TSTRANSCO/TSGENCO to rectify the reason for not transmitting the Carrier signal. 2.End-to-end testing can be carried out by APTRANSCO/TSTRANSCO/TSGENCO | TGGENCO | DEEM.KTPSA:TGGENCO: 06/08/2024 16:58:08: 1.Earlier carrier send signal in PSL was set only for Single line to ground faults in Zone-I, now it is changed to all types of Zone-I faults. 2. End to End testing will be carried out after wiring for DT is finished at our end. DEEM.KTPSA:TGGENCO: 20/02/2025 17:25:00: 1.Earlier carrier send signal in PSL was set only for Single line to ground faults in Zone-I, now it is changed to all types of Zone-I faults. 2. End to End testing completed on 28.05.2024 and found normal. | Complied | Complied
117/II/1 | Tripping of 220kV Bus-2 of 220kV KTPS station of TSGENCO | 27-02-2024 17:32 | As per the reports submitted the triggering incident is the LBB maloperation due to un wanted LBB initiation from 220kV KTPS-Nunna feeder owing to the faulty cable from Nunna feeder pro-tection relay panel to Bus bar protection panel. With the LBB initiation being high and as the current in the feeder (220kV KTPS-Nunna) is above the 20% threshold value (160A) led to the operation of LBB to all the elements connected to Bus-2 of KTPS. This led to the tripping of 220kV Bus-2 of 220kV KTPS station of TSGENCO and all the elements connected to 220kV Bus-2 of 220kV KTPS. | 1.TSGENCO to furnish the detailed report. 2.TSGENCO to provide the LBB retrip feature and DT to be send to remote end during LBB operation. | TGGENCO | DEEM.KTPSA:TGGENCO: 06/08/2024 16:58:08: 1. Detailed was already submitted to SRPC. 2.Retrip feature is enabled and DT work is under progress it will be completed in 02 weeks. DEEM.KTPSA:TGGENCO: 20/02/2025 17:26:45: 1. Detailed was already submitted to SRPC. 2.Both Retrip and DT feature is enabled. | Complied | Complied
118/I/2 | Complete Outage of 220kV Pulichinthala Generating station of TSGENCO | 31-03-2024 16:12 | In the antecedent condition, there is no generation at Pulichintala. As per the reports submitted the triggering incident is the B-N fault in 220kV Seethapuram-Pulichintala due to fire under the transmission tower. At Seethapuram end, the fault was sensed in Z2 and tripped on carrier aided protection and as AR is disabled 3ph tripped. At Chillakallu end, the fault was sensed in Z1 and the breaker failed to open, LBB operated after around 200ms leading to the tripping of the all the elements connected to the bus. And since at Pulichintala is operating in single bus operation, with the tripping of the only bus led to the Complete Outage of 220kV Pulichinthala Generating station of TSGENCO. | TSGENCO to enable DT for all lines at Pulichintala SS. | TGGENCO |  | Pending | Pending
118/I/2 | Complete Outage of 220kV Pulichinthala Generating station of TSGENCO | 31-03-2024 16:12 | In the antecedent condition, there is no generation at Pulichintala. As per the reports submitted the triggering incident is the B-N fault in 220kV Seethapuram-Pulichintala due to fire under the transmission tower. At Seethapuram end, the fault was sensed in Z2 and tripped on carrier aided protection and as AR is disabled 3ph tripped. At Chillakallu end, the fault was sensed in Z1 and the breaker failed to open, LBB operated after around 200ms leading to the tripping of the all the elements connected to the bus. And since at Pulichintala is operating in single bus operation, with the tripping of the only bus led to the Complete Outage of 220kV Pulichinthala Generating station of TSGENCO. | TSGENCO to enable Retrip feature for LBB operation at Pulichintala SS | TGGENCO |  | Pending | Pending
118/I/2 | Complete Outage of 220kV Pulichinthala Generating station of TSGENCO | 31-03-2024 16:12 | In the antecedent condition, there is no generation at Pulichintala. As per the reports submitted the triggering incident is the B-N fault in 220kV Seethapuram-Pulichintala due to fire under the transmission tower. At Seethapuram end, the fault was sensed in Z2 and tripped on carrier aided protection and as AR is disabled 3ph tripped. At Chillakallu end, the fault was sensed in Z1 and the breaker failed to open, LBB operated after around 200ms leading to the tripping of the all the elements connected to the bus. And since at Pulichintala is operating in single bus operation, with the tripping of the only bus led to the Complete Outage of 220kV Pulichinthala Generating station of TSGENCO. | TSGENCO to enable the AR feature. | TGGENCO |  | Pending | Pending
118/III/12 | 400/132 kV ICT-1 AT RSTPS | 20-04-2024 13:53 | 400/132 kV ICT-1 AT RSTPS tripped on only LV side at Malyalapalli end. | TSTRANSCO to follow SoP. | TGTRANSCO | deprotection1:TGTRANSCO: 03/06/2024 12:11:03: Intimated the field to follow the SOP and further it is to inform that standard SOP will be followed by TGTRANSCO. deprotection1:TGTRANSCO: 21/09/2024 11:27:25: Informed the field staff to follow SOP scrupulously. | Complied | Complied
118/VI/2 | 220kV SITAPURAM PULICHINTALA | 31-03-2024 16:12 | - | TSTRANSCO to rectify the time sync issues at Sitapuram. | TSTRANSCO | deprotection1:TGTRANSCO: 03/06/2024 12:11:03: There is no GPS at Sitapuram. Proposal for implementation of GPS will be taken up. | Pending | Pending
118/I/2 | Complete Outage of 220kV Pulichinthala Generating station of TSGENCO | 31-03-2024 16:12 | In the antecedent condition, there is no generation at Pulichintala. As per the reports submitted the triggering incident is the B-N fault in 220kV Seethapuram-Pulichintala due to fire under the transmission tower. At Seethapuram end, the fault was sensed in Z2 and tripped on carrier aided protection and as AR is disabled 3ph tripped. At Chillakallu end, the fault was sensed in Z1 and the breaker failed to open, LBB operated after around 200ms leading to the tripping of the all the elements connected to the bus. And since at Pulichintala is operating in single bus operation, with the tripping of the only bus led to the Complete Outage of 220kV Pulichinthala Generating station of TSGENCO. | 1.TSGENCO to enable DT for all lines at Pulichintala SS. 2.TSGENCO to enable Retrip feature for LBB operation at Pulichintala SS 3.TSGENCO to enable the AR feature. | TGGENCO |  | Pending | Pending
119/II/1 | Tripping of 400kV Bus-1 of Singareni Generating of TGTRANSCO | 02-05-2024 14:33 | In the antecedent condition 400 kV Singareni-Ramadugu-2 was under emergency outage for replacement of jumper at loc.19 by TSGENCO from 02-05-2024 05:40 Hrs. The jumper issue was attended and the line was charged. The triggering incident is the failure of 86BX relay in 400kV Singareni-Ramadugu-2 relay in relay panel which has extended the initiation for LBB relay. With failure of 86BX which has provided the initiation for LBB Bus-1 and due to the charging of the line 400kV Singareni-Ramadugu-2 and currents above the threshold led to the LBB operation and tripping of all the main breakers connected to 400kV Bus-1 at Singareni. The LBB operation led to the tripping of 400kV Bus-1 at Singareni. The main breaker connected to Singareni U1 tripped on LBB operation, however during the instance tie breaker also tripped on maloperation leading to the tripping of the Unit-1 at Singareni and leading to a generation loss of 416 MW which needs review | TGTRANSCO to take up the matter with Singareni GS through letter regarding non-compliance of IEGC Regulations | TGTRANSCO | deprotection1:TGTRANSCO: 02/07/2024 16:46:06: Report is furnished by M/s Singareni to SRPC after addressing a mail from TGTRANSCO. | Complied | Complied
119/II/1 | Tripping of 400kV Bus-1 of Singareni Generating of TGTRANSCO | 02-05-2024 14:33 | In the antecedent condition 400 kV Singareni-Ramadugu-2 was under emergency outage for replacement of jumper at loc.19 by TSGENCO from 02-05-2024 05:40 Hrs. The jumper issue was attended and the line was charged. The triggering incident is the failure of 86BX relay in 400kV Singareni-Ramadugu-2 relay in relay panel which has extended the initiation for LBB relay. With failure of 86BX which has provided the initiation for LBB Bus-1 and due to the charging of the line 400kV Singareni-Ramadugu-2 and currents above the threshold led to the LBB operation and tripping of all the main breakers connected to 400kV Bus-1 at Singareni. The LBB operation led to the tripping of 400kV Bus-1 at Singareni. The main breaker connected to Singareni U1 tripped on LBB operation, however during the instance tie breaker also tripped on maloperation leading to the tripping of the Unit-1 at Singareni and leading to a generation loss of 416 MW which needs review | Tripping of Unit-1 at Singareni needs review due to the tripping of tie breaker to be explained by M/s Singareni | TGTRANSCO | srpcadmin:SRPC: 04/07/2024 21:47:59: Detailed Report was furnished by M/s Singereni | Complied | Complied
119/VI/1 | 400kV KTPS-6 Khammam | 01-05-2024 14:35 | The relay is not synching with station GPS due to an issue with the communication port (rear port). The same was communicated to M/s TSTRANSCO for rectification. | TGTRANSCO to furnish the remedial action taken. | TGTRANSCO |  | Pending | Pending
119/V/1 | 400 kV Ghanapur - Mamidipally | 03-05-2024 13:06 | Spurious DT receipt at Mamidipally end | TGTRANSCO to furnish the reason for spurious DT send issue from Ghanapur SS. | TGTRANSCO | deprotection1:TGTRANSCO: 02/07/2024 16:23:59: DT was sent from Ghanapur end due to DC earth leakage at their end and DT increment is observed at Ghanapur end. | Complied | Complied
120/II/3 | Tripping of 400kV Bus-1 of 400kV Manuguru generating station of TSGENCO | 21-05-2024 17:20 | As per the reports submitted the triggering incident was R-N fault in the line due to rain and heavy gale wind. At Julurpadu end the fault was sensed in Zone-1 at a distance of 85.73km. A/R operated and the line was holding. At Manuguru end the fault was sensed in Zone-1 with a fault current of 7.764kA and at a distance of 27.87km. During the fault, due to B-ph cable issue R-B fault was sensed in 404 PU-B leading to the LBB operation of Bus-1 at Bhadradri TPS and tripping all the elements connected to Bus-1 at Bhadradri TPS. A/R did not get operated due to LBB operation during the reclaim time. However, Tie CB 405-52 tripped on Pole Discrepancy as Tie CB AR blocked due to tripping of main breaker 404-52. This led to the Tripping of 400kV Bus-1 at Manuguru. | TGGENCO to present the event during next PCSC meeting and furnish the detailed report as per the prescribed format. | TGGENCO | EME3GEN.VS:TGGENCO: 02/11/2024 16:18:43: The event was discussed in the 121 Pcsc meeting and the detailed presentation was submitted. Hence, it is requseted to drop the point. | Complied | Complied
120/III/2 | 400kV Julurpadu - Manuguru CKT-2 | 30-05-2024 10:51 | The tripping of the line on the operation of Dead Zone protection on Julurupadu Line-2 Tie breaker at Manuguru end by mistake during the testing of PU-B relay BB protection. DT was received at Julurupadu. | TGGENCO to present the event during next PCSC meeting and furnish the detailed report. | TGGENCO | EME3GEN.VS:TGGENCO: 02/11/2024 16:18:43: The event was discussed in the 121 Pcsc meeting and the detailed presentation was submitted. Hence, it is requseted to drop the point. | Complied | Complied
121/III/5 | Tripping at 400KV/220KV MALKARAM-ICT-2 | 10-07-2024 11:40 | 400KV/220KV MALKARAM-ICT-2 (315MVA ICT-2) tripped on operation of WTI protection. | TGTRANSCO to ensure regular periodic station maintenance. | TGTRANSCO | deprotection1:TGTRANSCO: 04/09/2024 13:14:30: Periodical maintenance is carried out from TGTRANSCO end. | Complied | Complied
122/III/2 | 220KV-ASUPAKA-LOWER_SILERU-1 | 29-07-2024 16:43 | 220KV-ASUPAKA-LOWER_SILERU-1 Line tripped spuriously without indications at Asupaka end only, while M/s GE service engineer working on SAS | TGTRANSCO to follow the SOP during testing activities | TGTRANSCO | deprotection1:TGTRANSCO: 21/09/2024 11:17:40: SOP are being followed and also informed the field officials to follow SOP scrupulously. | Complied | Complied
122/III/6 | 400KV/220KV JULURUPADU-ICT-2 | 09-08-2024 08:51 | 315MVA ICT-2 tripped on PRV-I indications due to damage of leads in the cable. | TGTRANSCO to include the relevant events in SCADA SOE | TGTRANSCO | deprotection1:TGTRANSCO: 21/09/2024 11:39:06: Relevant SCADA SOE will be included in due course of time deprotection1:TGTRANSCO: 03/01/2025 16:58:23: SCADA SOE will be implemented by taking OCC approval on 10-02-2025 deprotection1:TGTRANSCO: 03/01/2025 16:58:47: SCADA SOE will be implemented by taking OCC approval on 10-02-2025 deprotection1:TGTRANSCO: 29/01/2025 13:14:06: Applied for LC for including the events in SCADA SOE, but LC was not approved by SRLDC. Again applied LC in OCC for the month of May-2025. deprotection1:TGTRANSCO: 03/06/2025 15:06:48: Issue of SCADA SOE is rectified on 22-05-2025 and is confirmed with SLDC. | Complied | Complied
122/III/14 | 400KV-SRISAILAM_LEFT_BANK-SATTENPALLY-1 | 22-08-2024 03:30 | 400KV Srisailam- Satenapally line 1 got tripped on line to ground fault on Zone 1 R ph and carrier was sent to other end | TGGENCO to review the settings and furnish a report in this regard. | TGGENCO | PROTECTION.HPC:TGGENCO: 01/10/2024 12:35:33: A letter was addressed to TGTRANSCO to review the Relay Settings of 400KV Srisailam Sattenapally Line 1 feeder at SLBHES. After receipt of revised settings TGGENCO will implement the same and also communicate to SRPC. | Complied | Complied
123/III/13 | 400KV/220KV MAMIDAPALLI-ICT-2 | 13-09-2024 18:46 | As per the reports submitted, 315MVA 400kV/220kV Mamidapalli ICT-2 LV breaker tripped while MRT officials were checking the CB trouble alarms in Marshelling box. | TGTRANSCO to ensure to follow proper SOP | TGTRANSCO | deprotection1:TGTRANSCO: 23/11/2024 14:10:32: SOPs are followed and also Informed the field officials to follow the SOPs scrupulously. deprotection1:TGTRANSCO: 03/01/2025 16:58:23: As informed on 23-11-2024, SOPs are being followed. deprotection1:TGTRANSCO: 03/01/2025 16:58:47: As informed on 23-11-2024, SOPs are being followed. | Complied | Complied
124/II/2 | Tripping of 220kV Bus-2 of 220kV NSagar PH | 20-09-2024 20:30 | As per the reports submitted, the triggering incident was B-N fault in 220kV Nagarjunasagar-Srisailam RB feeder at 17:00hrs. While charging the line at 20:30hrs, the line tripped again due to permanent fault. At the same time, other 220kV Nasagar PH lines connected to 220kV Bus-2 tripped due to LBB maloperation in 220kV Nagarjun Sagar Chalakurthy line. This led to outage of 220kV Bus-2 of 220kV/132kV Nsagar PH Generating station. | TGGENCO to explore the feasibility to provide earthing at one end for the short cables instead of both ends | TGGENCO | MRT.NSHES:TGGENCO: 06/12/2024 17:13:22: Earth mat integrity between 220kV Receiving Station and NSagar Main Power House was completed by 23.11.2024. Most of the control cables used for existing Bus Bar protection are of unarmoured type. However, the armoured cables used for the same have been ensured that they were earthed at one end only. | Complied | Pending
124/II/2 | Tripping of 220kV Bus-2 of 220kV NSagar PH | 20-09-2024 20:30 | As per the reports submitted, the triggering incident was B-N fault in 220kV Nagarjunasagar-Srisailam RB feeder at 17:00hrs. While charging the line at 20:30hrs, the line tripped again due to permanent fault. At the same time, other 220kV Nasagar PH lines connected to 220kV Bus-2 tripped due to LBB maloperation in 220kV Nagarjun Sagar Chalakurthy line. This led to outage of 220kV Bus-2 of 220kV/132kV Nsagar PH Generating station. | TGGENCO to explore to replace the old LBB relay with numerical type which has retrip feature | TGGENCO | MRT.NSHES:TGGENCO: 06/12/2024 17:16:15: Termination of external wiring to the new bus bar protection schemes (i.e. Main-1 and Main-2) will be completed by 09.12.2024. In parallel to this, we have requested M/s. GE T&D India Ltd. to depute service engineer for testing and commissioning of the same and also requested TGTRANSCO for providing necessary settings to the Main-1 and Main-2 schemes. Probably, by the end of December-2024, Main-1 scheme will be commissioned. | Pending | Pending
125/III/8 | 400KV-SINGARENI-SUNDILA-2 | 03-11-2024 11:34 | As per the reports submitted, the triggering incident was fuse fail at Singareni end. Immediately, OV stage-1 operated (only in Main-2 relay of ABB REL 670) and DT was sent to remote end though the bus voltages at Singareni were within the range. The line tripped at both ends. Tripping is not in order. | M/s SCCL to furnish the root cause and action taken report for the event. TGTRANSCO may kindly take up with M/s SCCL | TGTRANSCO | deprotection1:TGTRANSCO: 29/01/2025 13:14:06: The same was discussed in the 125th PCSC meeting in which SCCL officials have attended. Updated may be obtained from M/s SCCL. | Complied | Complied
125/VI/1 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1 | 22-10-2024 10:49 | DR Time Synchronization Issues Related Events at NAGARJUNASAGAR_TS - 220KV | TGGENCO to furnish the action report in this regard. | TGGENCO | PROTECTION.HPC:TGGENCO: 06/01/2025 10:47:42: During the incident, DR was properly time Synchronized with GPS. Present also there is no GPS time Synchronization issue. | Complied | Complied
126/II/1 | Tripping of 220kV Bus-2 of 400kV/220kV Ghanapur SS of TGTRANSCO. | 16-11-2024 09:29 | As per the reports submitted, the triggering incident was R-N fault in 220kV Ghanapur - Hayathnagar Line-2. At Ghanapur end, the fault was sensed in zone-1 and the line tripped. However, after around 200ms, 220kV Bus-2 BBP mal-operated at 400kV/220kV Ghanapur SS. | 1.TGTRANSCO to consult with OEM and furnish the detailed report of the event along with the OEM findings and remedial action taken. 2.Since the forum noted that no saturation had been seen, TGTRANSCO to examine the waveform for saturation and furnish a report. | TGTRANSCO | deprotection1:TGTRANSCO: 29/01/2025 13:14:06: As discussed in the 126th PCSC meeting, the Knee point voltages of Bus Bar core of the CTs are incorporated in all the PUs connected to Bus Bar. Presently it is under observation. deprotection1:TGTRANSCO: 03/06/2025 15:06:48: Contacted OEM and response is awaited. deprotection1:TGTRANSCO: 03/11/2025 12:19:53: Point may be dropped as the response from OEM is still awaited. It is under observation. deprotection1:TGTRANSCO: 04/04/2026 14:44:33: As informed earlier the point may be dropped. | Pending | Pending
126/II/3 | Tripping of 220kV Bus-2 at 220kV/132kV Malyalalapalli SS | 25-11-2024 06:20 | Triggering incident was fault in 220kV RSS (Malyalapally)-Durshed feeder-1. At the same time, 220kV Bus-2 BBP mal-operated resulting in the tripping of all the connected elements at 220kV Bus-2 of 220kV/132kV Malyalapalli SS. | 1.TGTRANSCO to consult the event with OEM and furnish the detailed report along with the remedial action taken. 2.TGTRANSCO to rectify DR time sync issue at Malyalapalli - 220KV SS. | TGTRANSCO | deprotection1:TGTRANSCO: 29/01/2025 13:14:06: 2. DR time sync issue will be rectified within 10 days deprotection1:TGTRANSCO: 12/02/2025 15:43:52: Rectified the time sync issue on 04-02-2025 | Complied | Complied
126/IV/1 | 220KV-VIJAYAWADA-KOTHAGUDEM_TPS-1 | 26-11-2024 00:24 | As per the reports submitted, the triggering incident was BN fault in the line. At Vijayawada end the line tripped on operation of Zone-2, carrier aided distance protection. A/R operated successfully and the line was holding. At Kothagudem end the line tripped on operation of Zone-1 distance protection and the line tripped on 3-phase. A/R did not get operated | TGGENCO to furnish the reason for 3-phase trip of Main-2 relay (D-60). | TGGENCO | DEEM.KTPSA:TGGENCO: 03/02/2025 11:48:14: On 26.11.2024 , 00:24 hrs Fault triggered for 220kv KTS - Nunna line in BN phase at location 2.158km from KTS end.Main - 1(P442) relay observed fault and sent carrier to far end. concurrently ,Main -2 (D60) relay gave 3 - phase trip to circuit breaker at KTS end.It has been observed that consistently D60 relay is initiating lock-out relay for near-end faults.The same issue was mailed to OEM. | Complied | Complied
126/VI/4 | MALYALAPALLI - 220KV | 25-11-2024 06:20 | Triggering incident was fault in 220kV RSS(Malyalapally)-Durshed feeder-1. At the same time, 220kV Bus-2 BBP malperated resulting in the tripping of all the connected elements at 220kV Bus-2 of 220kV/132kV Malyalapalli SS | TGTRANSCO to rectify the DR time sync issues at 220kV Malayalapalli SS. | TGTRANSCO | deprotection1:TGTRANSCO: 29/01/2025 13:14:06: DR time sync issue will be rectified within 10 days deprotection1:TGTRANSCO: 12/02/2025 15:44:41: Rectified the time sync issue on 04-02-2025 | Complied | Complied
126/VI/5 | 220KV-VIJAYAWADA-KOTHAGUDEM_TPS-1 | 26-11-2024 00:24 | As per the reports submitted, the triggering incident was BN fault in the line. At Vijayawada end the line tripped on operation of Zone-2, carrier aided distance protection. A/R operated successfully and the line was holding. At Kothagudem end the line tripped on operation of Zone-1 distance protection and the line tripped on 3-phase. A/R did not get operated. | TGGENCO to furnish the detailed report in this regard. | TGGENCO | DEEM.KTPSA:TGGENCO: 03/02/2025 11:44:25: On 26.11.2024 , 00:24 hrs Fault triggered for 220kv KTS - Nunna line in BN phase at location 2.158km from KTS end.Main - 1(P442) relay observed fault and sent carrier to far end. concurrently ,Main -2 (D60) relay gave 3 - phase trip to circuit breaker at KTS end.It has been observed that consistently D60 relay is initiating lock-out relay for near-end faults.The same issue was mailed to OEM. DEEM.KTPSA:TGGENCO: 03/02/2025 11:50:19: Detailed Report will be sent. DEEM.KTPSA:TGGENCO: 20/02/2025 17:19:26: On 26.11.2024 , 00:24 hrs Fault triggered for 220kv KTS - Nunna line in BN phase at location 2.158km from KTS end.Main - 1(P442) relay observed fault and sent carrier to far end. concurrently ,Main -2 (D60) relay gave 3 - phase trip to circuit breaker at KTS end.It has been observed that consistently D60 relay is initiating lock-out relay for near-end faults.The same issue was mailed to OEM. | Complied | Complied
127/IV/3 | 220KV-VIJAYAWADA-KOTHAGUDEM_TPS-1 | 19-01-2025 01:48 | As per the reports submitted, the triggering incident was BN fault in the line. At Vijayawada end the line tripped on operation of Zone-1 distance protection. A/R operated but again the line tripped due to persistent fault. At Kothagudem end the line tripped on operation of Zone-1 distance protection and the line tripped on 3-phase. A/R did not get operated. Tripping needs review. | TGGENCO to check the Main-II relay and report. | TGGENCO | DEEM.KTPSA:TGGENCO: 03/03/2025 12:16:17: On 19.01.2025 , 01:48 hrs Fault triggered for 220kv KTS - Nunna line in CN phase at location 20.17km with fault current of 7.2KA from KTS end.Main - 1(P442) relay observed fault and sent carrier to far end.concurrently ,Main -2 (D60) relay gave 3 - phase trip to circuit breaker at KTS end.It has been observed that consistently D60 relay is initiating lock-out relay for near-end and high fault current faults.The same issue was mailed to OEM. | Complied | Complied
127/VI/5 | 400KV/220KV NARSAPUR-ICT-3 | 26-12-2024 06:50 | As per the reports, 400/220kV Narsapur ICT-3 tripped on operation of OLTC OSR R&B-Phase relay indications. As per the information furnished by TGTRANSCO, it was observed that monkeys on the transformer made OSR relay to operated. | TGTRANSCO to rectify the DR time sync issues at Naraspur. | TGTRANSCO | deprotection1:TGTRANSCO: 03/06/2025 15:06:48: Time sync issue is due to the relay. Spare relay is available and will be replaced by availing the LC. deprotection1:TGTRANSCO: 04/07/2025 14:41:47: Line Clearance is approved in OCC for 12th and 13th of August, 2025. Spare relay will be commissioned and DR time sync will be done. deprotection1:TGTRANSCO: 23/08/2025 12:02:29: Relay was replaced and DR time sync is done on 07-08-2025. The point may be closed deprotection1:TGTRANSCO: 15/09/2025 11:53:04: Replaced the issue and DR time sync is rectified on 07-08-2025. deprotection1:TGTRANSCO: 15/09/2025 11:53:59: Replaced the relay and DR time sync issue is rectified on 07-08-2025. Hence point may be dropped | Complied | Complied
127/VI/11 | 220KV-VIJAYAWADA-KOTHAGUDEM_TPS-1 | 10-01-2025 22:40 | As per the reports submitted, the triggering incident was RN fault in the line. At both ends the line tripped on operation of Zone-1 distance protection. A/R operated but again the line tripped due to persistent fault. Tripping is in order. | TGGENCO to rectify the DR time sync issues at KTPS. | TGGENCO | deprotection1:TGTRANSCO: 12/06/2025 11:11:41: Not related to TGTRANSCO deprotection1:TGTRANSCO: 23/08/2025 12:02:29: As already the substation is not related to TGTRANSCO. It is requested to change the entity or close the point. deprotection1:TGTRANSCO: 23/08/2025 12:04:09: As already informed that substation is not related to TGTRANSCO. Hence the entity name may be changed or close the point. deprotection1:TGTRANSCO: 15/09/2025 11:53:04: As informed already Substation doesnt belong to TGTRANSCO. Point may be dropped | Pending | Pending
127/VI/13 | 220KV-VIJAYAWADA-KOTHAGUDEM_TPS-1 | 16-01-2025 21:58 | As per the reports submitted, the triggering incident was YN fault in the line. At both ends the line tripped on operation of Zone-1 distance protection. A/R operated but again the line tripped due to persistent fault. Tripping is in order. | TGGENCO to rectify the DR time sync issues at KTPS. | TGGENCO | DEEM.KTPSA:TGGENCO: 03/03/2025 12:08:12: DR time synchronization failed due to internal issues in GPS panel(Sands make), and it is in regular pursual with OEM service engineer. this will be resolved after service engineer on-site inspection . DEEM.KTPSA:TGGENCO: 03/04/2025 10:08:58: DR time synchronization failed due to internal issues in GPS panel(Sands make), and it is in regular pursual with OEM service engineer. this will be resolved after service engineer on-site inspection . | Complied | Complied
127/VI/14 | 220KV-VIJAYAWADA-KOTHAGUDEM_TPS-1 | 19-01-2025 01:48 | As per the reports submitted, the triggering incident was BN fault in the line. At Vijayawada end the line tripped on operation of Zone-1 distance protection. A/R operated but again the line tripped due to persistent fault. At Kothagudem end the line tripped on operation of Zone-1 distance protection and the line tripped on 3-phase. A/R did not get operated. Tripping needs review. | TGGENCO to rectify the DR time sync issues at KTPS. | TGGENCO | DEEM.KTPSA:TGGENCO: 03/03/2025 12:08:12: DR time synchronization failed due to internal issues in GPS panel(Sands make), and it is in regular pursual with OEM service engineer. this will be resolved after service engineer on-site inspection . DEEM.KTPSA:TGGENCO: 03/04/2025 10:08:58: DR time synchronization failed due to internal issues in GPS panel(Sands make), and it is in regular pursual with OEM service engineer. this will be resolved after service engineer on-site inspection . | Complied | Complied
128/II/6 | Tripping of 220kV Bus-2 of 220 kV Upper Jurala of TGGENCO | 13-02-2025 12:05 | In the antecedent conditions, 220kV Jurala-Upper-Jurala-1&2 was under idle charged condition. The triggering incident is the B-N fault in Bus-2 caused by a manual error in closing an earthed section to a live section at 220kV Upper Jurala and immediately BBP protection operated leading to the tripping of all elements connected to Bus-2 of Upper Jurala. | 1.TGGENCO to follow SOP and furnish the revised SOP 2.TGGENCO to resolve the DR time sync Issue at Upper Jurala SS 3.TGGENCO/TGSLDC to adhere to the IEGC Regulatory Provisions and the timelines | TGTRANSCO | PROTECTION.HPC:TGGENCO: 03/06/2025 11:47:44: TGGENCO: 1. TGGENCO will follow SOP and will furnish the SOP through e-mail. 2. DR Time sync has been synced with GPS at Upper Jurala SS. 3. TGGENCO will follow the IEGC Regulatory Provisions and the timeline | Complied | Complied
128/III/10 | 400KV-YADADRI TPP-DINDI-2 | 02-02-2025 20:26 | As per the reports submitted, the line tripped on the operation of OV St-1 protection at YTPP end and DT was received at Dindi end. From DR at YTPP end, there was a difference in Y-ph CVT voltage compared to R and B phase voltages. From DR of YTPP end, the voltages observed were: Vr-244kV, Vy-251kV and Vb-244kV. Tripping needs review | 1.TGGENCO to check for CVT drift and report to SRPC and SRLDC | TGGENCO | DEEM.YTPS:TGGENCO: 07/04/2025 15:52:03: LC TAKEN ON 04.03.2025 ON DINDI-2 FEEDER AND TESTED ,FOUND OK THE RATIO ERROR IS 2.8% WHICH IS LESS THAN +- 3% AS PER IEC 61869-5 . | Complied | Complied
128/III/16 | 400KV-YADADRI TPP-DINDI-2 | 20-02-2025 20:26 | As per the reports submitted, the line tripped on the operation of OV St-1 protection at YTPP end and DT was received at Dindi end. From DR at YTPP end, there was a difference in Y-ph CVT voltage compared to R and B phase voltages. From DR of YTPP end, the voltages Observed were: Vr-244kV, Vy-251kV and Vb-244kV. Tripping needs review | 1.TGGENCO, YTPS to check for CVT drift and report to SRPC and SRLDC | TGGENCO | DEEM.YTPS:TGGENCO: 07/04/2025 16:04:50: LC TAKEN ON 04.03.2025 ON DINDI-2 FEEDER AND TESTED CVT Y-PHASE, FOUND OK . THE RATIO ERROR IS 2.8% WHICH IS LESS THAN +-3% AS PER IEC61869-5 | Complied | Complied
128/IV/1 | 220KV-VIJAYAWADA-KOTHAGUDEM_TPS-1 | 22-01-2025 03:40 | As per the reports submitted, the triggering incident was BN fault in the line. At Vijawada end the line tripped on operation of Zone-1 distance protection. A/R operated and the line was holding. At Kothagudem end the line tripped on operation of Zone-1 distance protection. A/R did not get operated and the line tripped on 3-phase. Tripping needs review. | 1.TGGENCO to furnish the detailed analysis of the event. | TGGENCO | DEEM.KTPSA:TGGENCO: 03/04/2025 10:08:58: On 22.01.2025 , 03:40 hrs Fault triggered for 220kv KTS - Nunna line in BN phase at location 18.1 km from KTS end.Main - 1(P442) relay observed fault and sent carrier to far end.concurrently ,Main -2 (D60) relay gave phase - phase trip to circuit breaker at KTS end.It has been observed that consistently D60 relay is initiating lock-out relay for near-end faults with high fault current(7.59KA).The same issue was mailed to OEM. | Complied | Complied
128/IV/9 | 220KV-VIJAYAWADA-KOTHAGUDEM_TPS-1 | 13-02-2025 20:30 | As per the reports submitted, the triggering incident was YN fault in the line. At Vijaywada end the line tripped on operation of Zone-1 distance protection. A/R operated successfully and the line was holding. At Kothagudem end, the line tripped on operation of Zone-1 distance protection. A/R did not get operated and the line tripped on 3-phase. Tripping needs review. | 1.TGGENCO to furnish a detailed analysis of the event | TGGENCO | DEEM.KTPSA:TGGENCO: 03/04/2025 10:16:42: On 13.02.2025 , 20:30 hrs Fault triggered for 220kv KTS - Nunna line in BN phase at location 21.57 km from KTS end.Main - 1(P442) relay observed fault and sent carrier to far end.concurrently ,Main -2 (D60) relay gave phase - phase trip to circuit breaker at KTS end.It has been observed that consistently D60 relay is initiating lock-out relay for near-end faults with high fault current(6.732KA).The same issue was mailed to OEM. | Complied | Complied
128/V/6 | 220KV-VIJAYAWADA-KOTHAGUDEM_TPS-1 | 12-02-2025 04:46 | As per the reports submitted, the triggering incident was BN fault in the line. At Vijaywada end the line tripped on operation of Zone-2, carrier-aided, distance protection. A/R operated and the line was holding. At Kothagudem end the line tripped on operation of Zone-1 distance protection. A/R did not get operated and the line tripped on 3-phase. Tripping needs to be reviewed. | 1.TGGENCO to furnish a detailed analysis of the event | TGGENCO | DEEM.KTPSA:TGGENCO: 03/04/2025 10:16:42: On 12.02.2025 , 20:30 hrs Fault triggered for 220kv KTS - Nunna line in CN phase at location 2.2 km from KTS end.Main - 1(P442) relay observed fault and sent carrier to far end.concurrently ,Main -2 (D60) relay gave phase - phase trip to circuit breaker at KTS end.It has been observed that consistently D60 relay is initiating lock-out relay for near-end faults with high fault current(22.94KA).The same issue was mailed to OEM. | Complied | Complied
128/VI/3 | 220KV-VIJAYAWADA-KOTHAGUDEM_TPS-1 | 22-01-2025 03:40 | As per the reports submitted, the triggering incident was BN fault in the line. At Vijawada end the line tripped on operation of Zone-1 distance protection. A/R operated and the line was holding. At Kothagudem end the line tripped on operation of Zone-1 distance protection. A/R did not get operated and the line tripped on 3-phase. Tripping needs review. | 1.TGGENCO to furnish the detailed analysis of the event. | TGGENCO | DEEM.KTPSA:TGGENCO: 03/04/2025 10:08:58: On 22.01.2025 , 03:40 hrs Fault triggered for 220kv KTS - Nunna line in BN phase at location 18.1 km from KTS end.Main - 1(P442) relay observed fault and sent carrier to far end.concurrently ,Main -2 (D60) relay gave phase - phase trip to circuit breaker at KTS end.It has been observed that consistently D60 relay is initiating lock-out relay for near-end faults with high fault current(7.59KA).The same issue was mailed to OEM. | Complied | Complied
128/VI/12 | 220KV-VIJAYAWADA-KOTHAGUDEM_TPS-1 | 13-02-2025 20:30 | As per the reports submitted, hte triggering incident was YN fault in the line. At Vijaywada end the line tripped on operation of Zone-1 distance protection. A/R oeprated successfully and the line was holding. At Kothagudem end, the line tripped on operation of Zone-1 distance protection. A/R did not get operated and the line tripped on 3-phase. Tripping needs review. | TGGENCO to furnish a detailed analysis of the event. | TGGENCO | DEEM.KTPSA:TGGENCO: 03/04/2025 10:16:42: On 13.02.2025 , 20:30 hrs Fault triggered for 220kv KTS - Nunna line in BN phase at location 21.57 km from KTS end.Main - 1(P442) relay observed fault and sent carrier to far end.concurrently ,Main -2 (D60) relay gave phase - phase trip to circuit breaker at KTS end.It has been observed that consistently D60 relay is initiating lock-out relay for near-end faults with high fault current(6.732KA).The same issue was mailed to OEM. | Complied | Complied
129/I/12 | Complete Outage of 400kV/11kV Medaram LIS | 10-03-2025 16:02 | During antecedent condition, 400kV Ramadugu Medaram line-2 was under outage due to relay testing works. Triggering incident was tripping of 400kV Ramadugu Medaram line-1 only at Medaram end due to suspected maloperation. Tripping of the only connected line resulted in the complete outage of 400kV/11kV Medaram LIS. During this event there was no pump load. | 1. TGTRANSCO to follow SOP while carrying out Testing Activities. 2.TGTRANSCO to verify time synch issue and confirm. 3.TGTRANSCO to look into not updating of SCADA data and SOE at 400kV Medaram end. | TGTRANSCO | deprotection1:TGTRANSCO: 03/06/2025 15:06:48: 1. SOPs are followed. 2. GPS time is synchronized with the relays. 3. Updation of SCADA SOE will be checked. | Complied | Complied
129/II/1 | Tripping of 220kV Bus-1 and Bus-2 of 220kV/132kV Erragadda SS of TGTRANSCO | 25-02-2025 13:06 | During antecedent conditions, 220kV Erragadda ShapurNagar line was under Planned outage. 220kV/132kV Erragadda SS was being radially fed through 220kV Rayadurg Erragadda line and 132kV Bus of 220kV/132kV Erragadda SS is operating with bus split condition. The triggering incident was Y-B fault in 220kV Rayadurg Erragadda line and the line tripped. Tripping of the only connected line led to tripping of 220kV buses of 220kV/132kV Erragadda SS. 132kV Bus 2 was in service. | 1.TGTRANSCO to ensure proper ROW manitenace for 220kV Raidurg-Erragadda feeder. 2.TGTRANSCO to analyze the cause of the event and furnish the report. | TGTRANSCO | deprotection1:TGTRANSCO: 03/06/2025 15:06:48: As informed in the 130th PCSC meeting, the fault occurred due to cable falling on the line and was cleared. Hence the point may be dropped | Complied | Complied
129/III/4 | 400KV-YADADRI TPP DINDI-2 | 26-02-2025 20:40 | As per the reports submitted, the line tripped on the operation of OV St-1 protection at YTPP end and DT was received at Dindi end. From DR at YTPP end, there was a difference in Y ph. CVT voltage compared to R and B phase voltages. From DR of YTPP end, the voltages observed were: Vr-244kV, Vy-251kV and Vb 245kV. Tripping needs review. | TGGENCO to expedite the commissioning of bus reactor. | TGGENCO | DEEM.YTPS:TGGENCO: 29/05/2025 16:19:04: Erection of Bus Reactor in Stage-2 of YTPS is completed. Testing and Commissioning are in full swing. | Complied | Complied
129/III/6 | 400KV MEHBOOBNAGAR-RTPS 1 | 07-03-2025 03:55 | As per the reports submission, the triggering incident is the maloperation of stub protection during a through fault due to issue with contacts of line Points for Review TGTRANSCO : 1. isolator status at Mehboobnagar and tripped at Mehboobnagar end. The line was holding at RTPS end. | TGTRANSCO to address the issue completely and furnish the revised report. | TGTRANSCO | deprotection1:TGTRANSCO: 03/06/2025 15:06:48: As already informed the issue was rectified by changing the wiring to spare contacts and Stub protection is in place. | Complied | Complied
129/VI/16 | 400KV-YADADRI TPP-DINDI-2 | 09-03-2025 18:02 | As per the reports submitted, the line tripped on the operation of OV St-1 protection at YTPP end and DT was received at Dindi end. From DR at YTPP end, there was a difference in Y-ph CVT voltage compared to R and B phase voltages. From DR of YTPP end, the voltages observed were: Vr-245kV, Vy-252kV and Vb-244kV. Tripping needs review. | TGGENCO to rectify the DR time sync issues at Yadadri TPP SS. | TGGENCO | DEEM.YTPS:TGGENCO: 29/05/2025 16:15:20: The issue has been discussed in 129th PCSC meeting. There was no issue found in Time Synch.And same has been confirmed in the meeting. | Complied | Complied
129/VI/25 | 400KV-DICHPALLY-RAMAGUNDAM-1 | 12-03-2025 18:25 | As per reports submitted, the triggering incident is the R-N fault in line. At Dichipally end, the fault was sensed in Z2 carr aided trip, AR operated and tripped due to persistent fault. At Ramagundam end, the fault was sensed in Z1, AR operated and tripped due to persistent fault. | TGTRANSCO to expedite replacement of server. | TGTRANSCO | deprotection1:TGTRANSCO: 03/06/2025 15:06:48: Replacement of the server will be taken up shortly. deprotection1:TGTRANSCO: 23/08/2025 12:02:29: GPS server was replaced on 15-08-2025. The point may be closed. deprotection1:TGTRANSCO: 23/08/2025 12:26:42: Please ignore the previous status of GPS replacement at Dichpally SS. Actually purchase order has been placed and will be replaced shortly. deprotection1:TGTRANSCO: 03/11/2025 12:26:39: Tendering under progress. May be completed by end of December 2025. deprotection1:TGTRANSCO: 01/01/2026 14:37:22: Will be completed by the end of January 2026. deprotection1:TGTRANSCO: 02/03/2026 12:37:38: Purchased order has been placed. will be commissioned after receiving at site. deprotection1:TGTRANSCO: 04/04/2026 14:44:33: GPS server is drawn from stores on 04-04-2026. The same will be commissioned within 15days. | Pending | Pending
130/III/22 | 400KV/220KV MAMIDAPALLIICT- 3 | 15-04-2025 10:51 | As per the reports submitted, the triggering incident is LV WTI protection relay maloperation due to tilted cubical box due to a loose nut bolt (as per FIR) leading to the tripping of 400KV/220KV MAMIDAPALLI- ICT-3 | TGTRANSCO to verify the alignment of the WTI meters and other protective devices across all ICTs. | TGTRANSCO | deprotection1:TGTRANSCO: 03/06/2025 15:06:48: Fixed the WTI meter and charged the ICT. | Complied | Complied
130/III/24 | Multiple trippings at Bhadradri TPS | 16-04-2025 06:03 | As per the reports submitted, the triggering incident is the tripping of 400KV/6.9KV Bhadradri TPS-ST-1 due to PRV Maloperation. During which Bhadradri TPS - UNIT 2 tripped after around 3 minutes and later Bhadradri TPS - UNIT 1 and Bhadradri TPS - UNIT 4 tripped at around 06:30 Hrs leading to a total generation loss of 750 MW. | TGGENCO to review the auxiliary system design and submit a detailed report to SRPC | TGGENCO | DEEM.KTPSA:TGGENCO: 03/06/2025 11:31:04: The Detailed report on Auxiliary system design and proposed modification of cooling water circuit to IACs of Bhadradri TPS(4X270MW) is submitted through mail on 03.06.2025. Hence it is requested to drop the point. | Complied | Complied
130/IV/11 | 400KVMALKARAMSURYAPET- 2 | 05-04-2025 11:00 | As per the reports submitted, the triggering incident is the B-N fault in the line. At Malkaram end, the fault was sensed in Z1 and AR operated and AR was successful and line was holding. At Suryapet end, the fault was sensed in Z1 and AR did not operate and 3ph tripped. | TGTRANSCO to review the Non operation of AR at Suryapet end | TGTRANSCO | deprotection1:TGTRANSCO: 03/06/2025 15:06:48: Issue was with the BCU. Now the A/R operation is in service after rebooting of the BCU on 06-04-2025 | Complied | Complied
131/I/3 | Complete Outage of 220kV Chalakurthy SwS, 220kV Puliyanthanda LIS and 220kV Puttamgandi LIS of TGTRANSCO | 21-04-2025 01:32 | During antecedent conditions, 20kV Puliyanthanda LIS and 220kV Puttamgandi LIS were being radially fed from 20kV Chalakurthy SwS. 220kV Chalakurthy is operating with single bus. As per the reports submitted, the triggering incident was R-phase CT failure of 220kV Chalakurthy Puttamgandi line. BBP of 220kV Chalakurthy bus operated and all line sconnected to 220kV Chlakaurthy bus tripped. Tripping of all lines led to complete outage of 220kV Chalakurthy SwS which inturn led to complete outage of 220kV Puliyanthanda LIS and 220kV Puttamgandi LIS. | TGTRANSCO to check the healthiness of the Y & B phase CTs also. | TGTRANSCO | deprotection1:TGTRANSCO: 02/07/2025 13:35:58: Checked the healthiness of Y & B Phase CTs and found to be OK | Complied | Complied
131/I/3 | Complete Outage of 220kV Chalakurthy SwS, 220kV Puliyanthanda LIS and 220kV Puttamgandi LIS of TGTRANSCO | 21-04-2025 01:32 | During antecedent conditions, 20kV Puliyanthanda LIS and 220kV Puttamgandi LIS were being radially fed from 20kV Chalakurthy SwS. 220kV Chalakurthy is operating with single bus. As per the reports submitted, the triggering incident was R-phase CT failure of 220kV Chalakurthy Puttamgandi line. BBP of 220kV Chalakurthy bus operated and all line sconnected to 220kV Chlakaurthy bus tripped. Tripping of all lines led to complete outage of 220kV Chalakurthy SwS which inturn led to complete outage of 220kV Puliyanthanda LIS and 220kV Puttamgandi LIS. | TGTRANSCO to rectify the DR Time sync issue at Chalakurthy SS | TGTRANSCO | deprotection1:TGTRANSCO: 03/11/2025 12:19:53: DR time sync will be completed by the end of December 2025. deprotection1:TGTRANSCO: 01/01/2026 14:37:22: Time synchronization is completed on 31-12-2025. Point may be dropped | Complied | Complied
131/I/3 | Complete Outage of 220kV Chalakurthy SwS, 220kV Puliyanthanda LIS and 220kV Puttamgandi LIS of TGTRANSCO | 21-04-2025 01:32 | During antecedent conditions, 20kV Puliyanthanda LIS and 220kV Puttamgandi LIS were being radially fed from 20kV Chalakurthy SwS. 220kV Chalakurthy is operating with single bus. As per the reports submitted, the triggering incident was R-phase CT failure of 220kV Chalakurthy Puttamgandi line. BBP of 220kV Chalakurthy bus operated and all line sconnected to 220kV Chlakaurthy bus tripped. Tripping of all lines led to complete outage of 220kV Chalakurthy SwS which inturn led to complete outage of 220kV Puliyanthanda LIS and 220kV Puttamgandi LIS. | TGTRANSCO to send the equipment failure report to CEA | TGTRANSCO | deprotection1:TGTRANSCO: 02/12/2025 12:00:33: Equipment failure report is furnished to CEA deprotection1:TGTRANSCO: 01/01/2026 14:37:22: As already informed the report is furnished to CEA. The point may be dropped | Complied | Complied
132/IV/5 | 220KV-VIJAYAWADA-KOTHAGUDEM_TPS-1 | 10-06-2025 06:29 | As per the reports furnished, the triggering incident was Y-G fault in the line. The fault distance from Vijawada end was 93.97kms and from Kothagudem end was 19.24kms. At KTPS end, line tripped on operation of Zone-1 distance protection, A/R not operated. At Vijayawada end, fault was sensed in Zone 1, A/R operated and tripped due to persistent fault. Non-operation of A/R at KTPS end needs review. | TGGENCO to furnish the reasons for non-operation of Auto reclosure. | TGGENCO | DEEM.KTPSA:TGGENCO: 20/08/2025 10:38:15: On 10.06.2025, 06:29 hrs Fault triggered for 220kv KTS - Nunna line in YN (in RYB) phase at location 19.25km from KTS end.Main - 1(P442) relay observed fault and sent carrier to far end.concurrently ,Main -2 (D60) relay gave phase - phase trip to circuit breaker at KTS end.It has been observed that consistently D60 relay is initiating lock-out relay for near-end faults with high fault current.The same issue was mailed to OEM. | Pending | Pending
133/II/3 | Tripping of 220kV Bus-1 and Bus-2 of Nirmal SS of TGTRANSCO | 26-06-2025 06:45 | The triggering incident is the failure of B-phase insulator string of the 220kV jumper from the Jack bus to the ICT-2 LV breaker creating Bus-1 fault. However during the event, all elements connected to Bus-1 and Bus-2 tripped due to BBP operation due to the isolator status issue led to the tripping of 220kV Bus-1 and 2 at Nirmal. 400kV Buses at Nirmal was intact during the event. | TGTRANSCO to rectify the DR time sync issue at Nirmal. | TGTRANSCO | deprotection1:TGTRANSCO: 15/09/2025 11:53:04: DR time sync issue rectified on 15-08-2025. Point may be dropped | Complied | Complied
133/II/3 | Tripping of 220kV Bus-1 and Bus-2 of Nirmal SS of TGTRANSCO | 26-06-2025 06:45 | The triggering incident is the failure of B-phase insulator string of the 220kV jumper from the Jack bus to the ICT-2 LV breaker creating Bus-1 fault. However during the event, all elements connected to Bus-1 and Bus-2 tripped due to BBP operation due to the isolator status issue led to the tripping of 220kV Bus-1 and 2 at Nirmal. 400kV Buses at Nirmal was intact during the event. | TGTRANSCO to rectify the issue of non availability of busbar DR during fault. | TGTRANSCO | deprotection1:TGTRANSCO: 03/11/2025 12:19:53: Awaited for LC. Will be tested during LC. deprotection1:TGTRANSCO: 02/12/2025 12:00:33: LC will be availed by the end of December, 2025 and rectify the issue. deprotection1:TGTRANSCO: 01/01/2026 14:37:22: Bus bar testing completed on 31-12-2025. At present the Bus bar is in service and DR are being recorded. The point may be dropped. | Complied | Complied
133/II/4 | Tripping of 220kV Bus-1 of 400kV/220kV Shankarapally SS of TGTRANSCO | 03-07-2025 16:50 | As per the reports submitted, the 220kV ShankarpallyGachibowli Feeder2 was charged at 400/220kV Shankarpally Substation following successful testing of the A/R scheme by the MRT wing. At the same time, The BBP if Bus-1 maloperated, which in turn resulted in the tripping of the 220kV Shankarpally Bus-1 and all its connected elements. | TGTRANSCO to ensure strict adherence to SOP during Testing and maintainence activities. | TGTRANSCO | deprotection1:TGTRANSCO: 15/09/2025 11:53:04: Instructed to follow SOPs and is being followed. Point may be dropped | Complied | Complied
133/III/4 | 400KV-RAMADUGU-GAJWEL-2 | 25-06-2025 21:12 | As per the reports submitted, the triggering incident was Overvoltage tripping. At Gajwel end, line tripped on Stage-1 Overvoltage operated and DT was sent to Ramadugu end. From the EL data, V>3 was observed. However voltages were in order and over voltage should not have operated for the event. | TGTRANSCO to configure the DR as per FOLD recommendations. | TGTRANSCO | deprotection1:TGTRANSCO: 03/11/2025 12:19:53: DRs configured as per FOLD recommendations. Point may be dropped. deprotection1:TGTRANSCO: 02/12/2025 12:00:33: Already informed that DRs configured. please mention the reasons for pending status. | Complied | Complied
133/IV/8 | 400KV-BHOOPALAPALLY-WARANGAL-2 | 20-07-2025 01:21 | As per the reports submitted, the triggering incident was B-G fault in the line. The Fault distance from Bhoopalapally end was 14.5kms. At Bhoopalapally end, the fault was sensed in Z1, A/R not operated due to PD relay operation. At Warangal end, the fault was sensed in Z1, A/R operated and line was holding at Warangal end. Non-operation of A/R at Bhoopalapally end needs review. Tripping is not in order. | TGGENCO to furnish the detailed report regarding non operation of A/r at BHOOPALAPALLY end. | TGGENCO | DEEM.KTPPII:TGGENCO: 01/09/2025 12:12:20: Warangal-2 feeder tripped B-N fault at 01:21hrs at 20.07.2025 ( Fault current 10.1kA). Warangal feeder 407 CB tripped on Pole discrepancy relay operation within 70 msec as it was not hold for 2 sec ( PD setting is 2 sec). PD relay operation is given to A/R inhibit logic in REL670 relay. At the same time, Warangal Tie breaker is not in service, due to this AR was unsuccessful from KTPP end. Remedial Actions Taken: LC was taken on Warangal-2 line on 11.08.2025 for checking of CB pole discrepancy circuit and CB AR operation. Pole Discrepancy timer was replaced in Circuit Breaker Control cubicle. CB PD operation , CB AR operation were checked and found normal. The detailed tripping report sent through mail on 01/09/2025 | Complied | Complied
134/III/10 | 400KV/220KV KTPS_VI-PST-1 | 18-08-2025 15:04 | As per the reports submitted the triggering incident was the tripping of the PST due to suspected cable issue of the cable with respect to OLTC Buchholz or OLTC Oil Surge which was activated high. | Detailed review of all PST PSL logic settings and control wiring at KTPP SS to be done by TGGENCO and submit a report to SRPC after verification. | TGGENCO | DEEM.KTPSVI:TGGENCO: 29/09/2025 10:42:14: The basic protection settings and scheme were checked. The detailed report will be submitted once the all the PSL LOGICS, binary input mapping and other interlocks checking is done in the upcomming annual overhaul which is scheduled in nov-2025 | Pending | Pending
135/II/1 | Tripping of 220kV Bus-1 of Malyalapalli SS of TGTRANSCO | 25-08-2025 11:15 | The triggering incident was B-G fault in 220kV Malyalapalli Bus-1. Immediately, 220kV Bus-1 BBP operated and all elements connected to the bus tripped. This led to tripping of 220kV Malyalapalli Bus-1 | TGTRANSCO to ensure the healthiness of all the jumpers at 220kV Malyalapalli SS. | TGTRANSCO | deprotection1:TGTRANSCO: 03/11/2025 12:19:53: Healthiness ensured. Point may be dropped deprotection1:TGTRANSCO: 02/12/2025 12:00:33: Already informed healthiness ensured. Please drop the point or mention the reasons for pending status. | Complied | Complied
135/II/4 | Tripping of 220kV Bus-3 and Bus-4 of 220kV KTPS Generating station of TGGENCO | 05-09-2025 13:19 | As per the reports submitted, the triggering incident was B-N fault in 220kV Vijayawada KTPS Line-1 and the line tripped. However, the breaker failed to open at KTPS end LBB of 220kV Bus-3 and Bus-4 operated tripping all elements connected to 220kV Bus-3 and Bus-4 of 220kV KTPS Generating station | 1.TGGENCO to check the healthiness of trip coils of all breakers at 220kv KTPS. 2.TGGENCO to check the LBB scheme and LBB operating time should be with in 200ms. 3.TGGENCO to rectify the DR Time synch issue at KPTS SS. | TGGENCO | DEEM.KTPSA:TGGENCO: 06/11/2025 16:06:43: I)The healthiness of the trip coils of all Breakers has been thoroughly checked and all trip coils of all breakers were found to be normal. II)The LBB scheme was checked and verified. All LBB operating timings were found to be within 200 msec. III)DR time synchronization has failed due to internal issues in the GPS panel (Sands make). The matter is under regular follow-up with the OEM service engineer. As per their update, the existing GPS panel model is obsolete, and spare parts are difficult to arrange. The issue will be resolved once the required spares are available. | Complied | Complied
135/V/1 | 400KV-GAJWEL-CHANDALAPUR-1 | 31-08-2025 01:31 | As per the reports submitted, while arresting DC earth leakage at Gajwel end, DT was sent to Chandalapur end and the line tripped only at Chandalapur end. | TGTRANSCO to furnish detailed report regarding maloperation of PLCC | TGTRANSCO | deprotection1:TGTRANSCO: 03/11/2025 12:19:53: As already informed in 135th PCSC meeting, DC earth leakage is rectified. Point may be dropped. deprotection1:TGTRANSCO: 02/12/2025 12:00:33: Already informed DC earth leakage rectified. PLCC is in order now. please drop the point. | Complied | Complied
135/VI/6 | 400KV/220KV SURYAPET -ICT-2 | 04-09-2025 06:01 | Suspected Buchholz relay faulty with trip contacts and will be replaced shortly. Meanwhile alarm is configured for tripping in case of any internal problem in ICT. | TGTRANSCO to rectify the DR time synchronization issue at SURYAPET - 400KV | TGTRANSCO | deprotection1:TGTRANSCO: 03/11/2025 12:19:53: Buchholz relay is replaced on 18-10-2025. DR time sync is done. Point may be dropped deprotection1:TGTRANSCO: 02/12/2025 12:00:33: Already informed time sync is done. Please mention the reasons for pending status. | Complied | Complied
135/VI/8 | 220KV-VIJAYAWADA-KOTHAGUDEM_TPS-1 | 08-09-2025 14:10 | 220KV-VIJAYAWADA-KOTHAGUDEM_TPS-1 | TGGENCO to rectify the DR time synchronization issue at KOTHAGUDEM_TPS - 220KV | TGGENCO | DEEM.KTPSA:TGGENCO: 06/11/2025 16:06:43: DR time synchronization has failed due to internal issues in the GPS panel (Sands make). The matter is under regular follow-up with the OEM service engineer. As per their update, the existing GPS panel model is obsolete, and spare parts are difficult to arrange. The issue will be resolved once the required spares are available. | Pending | Pending
136/II/1 | Tripping of 220kV Manuguru Bus-2 | 29-09-2025 12:36 | As per the reports submitted, the triggering incident was maloperation of 220kV Manuguru Bus-2 BBP due to human error during an external fault. Immediately, all elements connected to 220kV Manuguru Bus-2 tripped | TGGENCO to review the wiring diagram of BBP, CU, PU & BCU at KTPS SS. | TGGENCO | DEEM.BTPS:TGGENCO: 02/12/2025 10:35:42: Thoroughly physical verification of CT wiring carried out throught CT path and correctness ensured. | Complied | Complied
136/II/2 | Tripping of 220kV Bus-2 of 220kV Khammam_TS SS of TGTRANSCO | 06-10-2025 19:25 | As per the reports submitted, the triggering incident was R-N fault in 220kV Khammam KTPS V Line-2. At both ends, the fault was sensed in zone-1. At Khammam end, the R-pole limb of the breaker failed to open causing LBB to operate. Immediately, all elements connected to 220kV Bus-2 tripped on LBB operation causing loss of power supply to 220kV Khammam Bus-2. | 1.TGTRANSCO to rectify the DR Time sync at Khammam TS. 2.TGTRANSCO to review the Zone-1 overreach at Suryapet SS during the event. 3.TGTRANSCO to implement DT for LBB operation. | TGTRANSCO | deprotection1:TGTRANSCO: 02/12/2025 12:00:33: 1. DR time sync done. 2. As already discussed in the PCSC meeting, the zone-1 settings are in order. The over reach was only due to sudden change in the parallel impedance due to tripping of all feeders. The point may be dropped. 3. DT for LBB operation is under process and will be implemented. deprotection1:TGTRANSCO: 04/04/2026 14:44:33: point 1 & 2 may be dropped as informed earlier. Point 3 will be attended as it takes time to implement it throughout TGTRANSCO network. | Pending | Pending
136/III/3 | Tripping of 400KV/220KV MANUGURU-ICT-1 | 30-09-2025 16:42 | As per the reports submitted, the triggering incident occurred when the HV side of the 400 kV/220 kV Manuguru ICT-1 tripped on 86A/B operation due to a trip command that was inadvertently issued during testing of the 220 kV bus bar protection scheme. | 1.TGGENCO to follow the SOP while carrying any testing on protection equipment. 2.TGGENCO to rectify the 315 MVA LV ICT Bay BCU at the earliest | TGGENCO | DEEM.BTPS:TGGENCO: 02/12/2025 10:35:42: 1. It will be ensured SOP in all future protection Relays testing. 2. PO Placed on M/s GE Veronava and will be completed in a Month. | Pending | Pending
137/III/5 | 400KV/220KV BHOOPALAPALLY-ICT-2 | 25-10-2025 12:50 | As per the reports submitted, 500MVA ICT-1 LV breaker was tripped due to suspected low SF6 pressure in CT. Unwanted operation needs review at Bhoopalapally end. | TGGENCO to submit the detailed report on the incident. | TGGENCO | deprotection1:TGTRANSCO: 02/03/2026 11:54:25: The issue was with the loose wiring near the Breaker panel. Rectified the loose wiring and provided insulation on 12-12-2025. The point may be dropped. deprotection1:TGTRANSCO: 04/04/2026 14:44:33: Please furnish the remarks for pending as it is already informed that remedial measures were taken. | Pending | Pending
137/III/11 | 400KV/220KV SURYAPET-ICT-2 | 05-11-2025 00:22 | As per the reports submitted, the triggering incident was Relay Maloperation in 315MVA ICT-2 at Suryapet due to OLTC OSR R-phase protection due to ingress of moisture into the relay. As per TGTRANSCO, the moisture ingress was cleaned and ICT was charged. | TGTRANSCO to rectify the DR time synchronization issue at 400kV Suryapet SS | TGTRANSCO | deprotection1:TGTRANSCO: 01/01/2026 14:44:32: There is no time sync issue on ICT-2 at Suryapet SS. The point may be dropped. | Complied | Complied
137/IV/7 | 20KV-VIJAYAWADA-KOTHAGUDEM_TPS-1 | 29-10-2025 13:02 | As per the reports submitted, the triggering incident was Y-N fault in the line. The fault distance from Kothagudem end was 24.8kms and from Vijayawada end it was 90.65kms. At Kothagudem end, the fault was sensed in Zone-1 and here AR lockout operated. At Vijayawada end, the fault was sensed in Zone-1. Here AR operated and the line was holding | TGGENCO to rectify the A/R issue at KTPS end. | TGGENCO |  | Pending | Pending
138/I/4 | Tripping of 220kV Bus-1 & Bus-2 of 400kv/220kv Nirmal SS and Complete Outage 220kV Utnoor SS of TGTRANSCO | 15-12-2025 13:45 | As per the reports submitted, the triggering incident was Y-G fault in 220kV Nirmal Bus-2. Immediately, 220kV Bus-1 and Bus-2 BBP operated tripping all elements connected to the buses which led to loss of power supply to 220kV Bus-1& Bus-2. Since 220kV Utnoor is being radially fed through 220kV Nirmal Utnoor Line-1&2, tripping of both lines led to complete outage of 220kV Utnoor SS. | TGTRANSCO to follow SOPs during the LC works TGTRANSCO to take up the issue of BUS2 operation for BUS1 fault with OEM | TGTRANSCO | deprotection1:TGTRANSCO: 03/02/2026 11:28:14: SOPs are followed. Issue of Bus2 operation for fault Bus-1 is rectified. Presently Bus Bar protection is in order. The point may be dropped. | Complied | Complied
138/III/6 | Multiple trippings at Srisailam | 29-11-2025 15:37 | As per the reports submitted, the triggering incident was a PLCC Maloperation at the Srisailam end, wherein direct trips (DTs) were sent to the remote ends of 400 kV Srisailam Left Bank Sattenpally1 2, 400 kV Narnoor Srisailam Left Bank1, and 400 kV Srisailam Left Bank Dindi 2. Subsequently, overvoltage protection operated at the remote ends of 400 kV Srisailam Left Bank Sattenpally1 2 and 400 kV Srisailam Left BankDindi 2, and DTs were sent to the Srisailam end, resulting in tripping of these lines at the Srisailam end. However, in the 400 kV Narnoor Srisailam Left Bank1 line, the line remained in service at the Srisailam end. | TGTRANSCO and TGGENCO to carry out the joint end to end test to identify the root cause of the PLCC maloperation at SLBHES and rectification of the same. | TGGENCO | MRT.SLBHES:TGGENCO: 03/02/2026 15:52:03: A comprehensive joint inspection was conducted in coordination with TG TRANSCO officials to examine the PLCC system, protection relays, and associated 48V and 110V DC battery systems and equipment. All components were found to be operating normally and in accordance with the configured settings. End-to-end PLCC DT send/receive and carrier send/receive signal simulations were carried out on the 400kV Narnoor feeder and found to be satisfactory. PLCC event data was downloaded and verified against the corresponding protection relay data. The observed PLCC time synchronization issue was rectified. Subsequent to the tripping incident and up to the present date, no further maloperations or abnormalities have been observed, and all systems continue to function satisfactorily. | Complied | Complied
138/III/6 | Multiple trippings at Srisailam | 29-11-2025 15:37 | As per the reports submitted, the triggering incident was a PLCC Maloperation at the Srisailam end, wherein direct trips (DTs) were sent to the remote ends of 400 kV Srisailam Left Bank Sattenpally1 2, 400 kV Narnoor Srisailam Left Bank1, and 400 kV Srisailam Left Bank Dindi 2. Subsequently, overvoltage protection operated at the remote ends of 400 kV Srisailam Left Bank Sattenpally1 2 and 400 kV Srisailam Left BankDindi 2, and DTs were sent to the Srisailam end, resulting in tripping of these lines at the Srisailam end. However, in the 400 kV Narnoor Srisailam Left Bank1 line, the line remained in service at the Srisailam end. | TGTRANSCO and TGGENCO to carry out the joint end to end test to identify the root cause of the PLCC maloperation at SLBHES and rectification of the same. | TGTRANSCO | deprotection1:TGTRANSCO: 03/02/2026 11:28:14: Informed the telecom officials to carry out end to end testing on all the feeders at 400kV Srisailam. | Complied | Complied
138/III/12 | 400KV/220KV BHOOPALAPALLY-ICT-1 | 10-12-2025 17:05 | The 500 MVA ICT1 LV breaker tripped due to suspected low SF6 pressure in Bus Coupler-1 CT Upon inspection of the CT and its associated wiring, loose cable terminations were identified between the 207 Bus Coupler CT and the LV breaker The issue was rectified by properly securing the connections and providing adequate insulation | TGTRANSCO to check the wiring integrity at BHOOPALAPALLY SS. | TGTRANSCO | deprotection1:TGTRANSCO: 03/02/2026 11:28:14: Checked all the wiring and removed all loose wiring. Presently it is in order. Point may be dropped. | Complied | Complied
139/I/3 | Tripping of 400kV Bus-2 of Shankarpally of TGTRANSCO | 11-01-2026 06:48 | The triggering incident was failure of R-ph breaker at Shankarapally end connected to 400kV Bus-2, while hand tripping 125MVAR bus reactor creating a bus fault and bus bar protection operated tripping all the breakers (main) connected to 400kV Bus-2 tripped. This led to the tripping of 400kV Bus-2 at Shankarapally | TGTRANSCO to send equipment failure report to CEA. | TGTRANSCO | deprotection1:TGTRANSCO: 02/03/2026 12:34:34: Informed the transmission wing to send the equipment failure report to CEA | Pending | Pending
139/III/3 | 400KV/220KV SURYAPET-ICT-1 | 30-12-2025 08:34 | As per the reports submitted, at Suryapet end the 315 MVA ICT-1 tripped on operation of Buchholz protection. Observed monkeys on the transformer causing Buchcholz relay operation. | TGTRANSCO advised to take corrective actions to avoid the recurrence of the incident | TGTRANSCO | deprotection1:TGTRANSCO: 02/03/2026 11:54:25: Additional support for the pipe conencting the main tank to conservator was provided on 19-01-2026. The point may be dropped. | Complied | Complied
139/III/7 | 400KV/220KV SURYAPET-ICT-2 | As per the reports submitted, the 315MVA ICT-2 tripped on maloperation of Buchholz relay protection due to monkey movement near the transformer. | 14-01-2026 06:06 | TGTRANSCO advised to take corrective actions to avoid the recurrence of the incident | TGTRANSCO | deprotection1:TGTRANSCO: 02/03/2026 11:54:25: Additional support for the pipe conencting the main tank to conservator was provided on 22-01-2026. The point may be dropped. | Complied | Complied
139/III/9 | 400KV/220KV NARSAPUR-ICT-3 | 18-01-2026 19:26 | As per the reports submitted, the 315MVA ICT-3 tripped on maloperation of Buchholz relay protection due to suspected monkey movement near the transformer. | TGTRANSCO advised to take corrective actions to avoid the recurrence of the incident | TGTRANSCO | deprotection1:TGTRANSCO: 02/03/2026 11:54:25: Additional support for the pipe conencting the main tank to conservator was provided on 11-02-2026. The point may be dropped. | Complied | Complied
139/III/10 | 400KV/220KV SURYAPET-ICT-1 | 19-01-2026 06:41 | As per the report submitted , the 315MVA ICT-1 tripped on operation of Buchholz relay protection due to suspected monkey movement near the transformer (as per FIR) | TGTRANSCO advised to take corrective actions to avoid the recurrence of the incident | TGTRANSCO | deprotection1:TGTRANSCO: 02/03/2026 11:54:25: Additional support for the pipe conencting the main tank to conservator was provided on 19-01-2026. The point may be dropped. | Complied | Complied
140/III/11 | 400KV-BHOOPALAPALLY-WARANGAL-2 | 10-02-2026 18:34 | As per the reports submitted, the triggering incident was Pole discrepancy relay maloperation and gave trip at Bhoopalapally end in the line. The line was holding at Warangal end. | TGGENCO to rectify the Pole discrepancy issue at 400kV Bhoopalapally. | TGGENCO |  | Pending | Pending
140/IV/1 | 220KV-VIJAYAWADA-KOTHAGUDEM_TPS-1 | 25-01-2026 00:49 | As per the reports submitted, the triggering incident was B-G fault in the line. The fault distance from Vijayawada end was 115.2 kms and from Kothagudem end was 2.28 kms. At Vijayawada end, the fault was sensed in Z1, A/R did not operate. At KTPS end, the ABC trip operated and the line was tripped. | TGGENCO to review the A/R operation at KOTHAGUDEM_TPS | TGGENCO |  | Pending | Pending
140/VI/2 | 220KV-VIJAYAWADA-KOTHAGUDEM_TPS-1 | 25-01-2026 00:49 | 220KV-VIJAYAWADA-KOTHAGUDEM_TPS-1 | TGGENCO to rectify the DR time synchronization issue at 220kV KTPS | TGGENCO |  | Pending | Pending
141/III/9 | 400KV/11.5KV YADADRI TPP-ST-2 | 09-03-2026 00:09 | As per the reports submitted, the triggering incident in the downstream 11kV fault. During the event, LV REF Protection operated and 3ph trip | TGGENCO to submit a detailed report on the incident. | TGGENCO |  | Pending | Pending
141/VI/9 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1 | 01-03-2026 12:10 | Station at which DR time synchronisation was not observed NAGARJUNASAGAR_TS - 220KV | TGGENCO to rectify the DR time synchronization issue at NAGARJUNASAGAR TS 220KV | TGGENCO |  | Pending | Pending
KARNATAKA
109/II/13 | Tripping of 400/220kV ICT-2 at GUTTUR | 23-07-2023 12:20:00 | ICT tripped due to problem with local remote switch in breaker cubicle. Findings and remedial actions taken shall be furnished. | KPTCL to carry out a physical inspection of Guttur Substation & ICTs and furnish the findings to SRPC & SRLDC. | KPTCL | Puspha:KPTCL: 04/02/2024 22:26:59: CEE,RT&R&D visited the Guttur Sub station. During his visit control cables having severe damages which requires replacement were identified. . WIth respect to the subject tripping it is to update that the control cable issues in ICT-2 bay has been attended and complied to SRPC Puspha:KPTCL: 17/02/2025 17:24:03: Attended. Physical inspection of the site has been done by CEE RT and details updated to SRPC in this regard. | Complied | Complied
110/I/1 | Complete Outage of 220kV/110kV Ambewadi SS of KPTCL | 27-07-2023 09:41 | As per the reports submitted, the triggering incident was B-N fault in 220kV Nagjheri Ambewadi line-2 and the line tripped. Because of this, 220kV Ambewadi Nagjheri line-1 got overloaded and caused the B-phase bus jumper connected to the line to fail. This resulted in a B-phase bus fault causing BBP to operate and all the elements connected to the 220kV Bus tripped. This led to a complete outage of 220kV/110kV Ambewadi SS. | 1.KPTCL to rectify the Issue with Main 2 relay of 220 kV Ambewadi Nagjhari line 2. | KPTCL | Puspha:KPTCL: 17/02/2025 22:54:52: Attended, settings are verified, relay tested and found to be normal | Complied | Complied
110/I/1 | Complete Outage of 220kV/110kV Ambewadi SS of KPTCL | 27-07-2023 09:41 | As per the reports submitted, the triggering incident was B-N fault in 220kV Nagjheri Ambewadi line-2 and the line tripped. Because of this, 220kV Ambewadi Nagjheri line-1 got overloaded and caused the B-phase bus jumper connected to the line to fail. This resulted in a B-phase bus fault causing BBP to operate and all the elements connected to the 220kV Bus tripped. This led to a complete outage of 220kV/110kV Ambewadi SS. | 2.KPTCL to rectify the Time synchronization issues. | KPTCL | Puspha:KPTCL: 02/08/2024 22:23:27: Attended. GPS time sync device is put back to service after repairs | Complied | Complied
110/I/1 | Complete Outage of 220kV/110kV Ambewadi SS of KPTCL | 27-07-2023 09:41 | As per the reports submitted, the triggering incident was B-N fault in 220kV Nagjheri Ambewadi line-2 and the line tripped. Because of this, 220kV Ambewadi Nagjheri line-1 got overloaded and caused the B-phase bus jumper connected to the line to fail. This resulted in a B-phase bus fault causing BBP to operate and all the elements connected to the 220kV Bus tripped. This led to a complete outage of 220kV/110kV Ambewadi SS. | 3.KPTCL to complete the pending works (replacement of Tubular structures) at 220 kV Ambewadi substation switchyard at the earliest and needs to restore Double Bus Operation and Enable Auto reclosure to all lines. | KPTCL | Puspha:KPTCL: 09/05/2024 15:29:56: Structure replacement work taken up at Ambewadi is almost completed. Dismantling of old structures under process. Puspha:KPTCL: 17/02/2025 22:47:03: Structure replacement work is completed, Bus-2 strengthening is required to restore double bus operation at Ambewadi. | Complied | Complied
110/I/1 | Complete Outage of 220kV/110kV Ambewadi SS of KPTCL | 27-07-2023 09:41 | As per the reports submitted, the triggering incident was B-N fault in 220kV Nagjheri Ambewadi line-2 and the line tripped. Because of this, 220kV Ambewadi Nagjheri line-1 got overloaded and caused the B-phase bus jumper connected to the line to fail. This resulted in a B-phase bus fault causing BBP to operate and all the elements connected to the 220kV Bus tripped. This led to a complete outage of 220kV/110kV Ambewadi SS. | 4.KPCL to furnish their end details records for the incident to identify the root cause nature of the fault and to analyze the incident further. | KPCL | EE (E )/CEED:KPCL: 03/10/2023 15:50:02: The events details of NA line- 1 & 2 was sent vide email dated:31.08.2023. EE (E )/CEED:KPCL: 03/10/2023 15:54:58: The events details of NA lines 1 and 2 was sent vide email dated 31st August 2023 EE (E )/CEED:KPCL: 03/10/2023 15:55:45: The events details of NA lines 1 and 2 was sent vide email dated 31st August 2023 EE (E )/CEED:KPCL: 03/11/2023 10:56:59: The event details of Nagjhari - Ambewadi lines 1 & 2 sent vide mail dated 31st August 2023. EE (E )/CEED:KPCL: 04/12/2023 12:51:01: The event details of Nagjhari - Ambewadi lines 1 & 2 sent vide mail dated 31st August 2023. Reply awaited EE (E )/CEED:KPCL: 02/04/2024 14:24:01: The event details of Nagjhari - Ambewadi lines 1 & 2 sent vide mail dated 31st August 2023. Reply awaited EE (E )/CEED:KPCL: 03/06/2024 15:08:13: The event details of Nagjhari - Ambewadi lines 1 & 2 sent vide mail dated 31st August 2023. Reply awaited EE (E )/CEED:KPCL: 04/07/2024 14:33:51: The event details of Nagjhari - Ambewadi lines 1 & 2 sent vide mail dated 31st August 2023. Reply awaited EE (E )/CEED:KPCL: 06/08/2024 16:55:57: The events details of NA line- 1 & 2 was sent vide email dated:31.08.2023. Request to close the point. | Complied | Complied
110/I/2 | Complete Outage of 220kV Varahi PH of KPCL | 09-08-2023 13:36 | As per the reports submitted, the triggering incident was R-N fault in 220kV Varahi Shimoga line-3. At the same time, other lines connected to the bus tripped on zone-2 operation from remote ends and were holding at Varahi end. Tripping of all the connected lines resulted in complete outage of 220kV Varahi PH. Further details are awaited. | KPCL/KPTCL to analyze the reason for the Zone-1 operation for the 220kV Varahi-Shimoga-3 and rectify the issues ,if any, observed. | KPCL | EE (E )/CEED:KPCL: 03/10/2023 17:01:10: The issue is discussed with OEM & the report will be furnished. EE (E )/CEED:KPCL: 03/11/2023 10:56:59: The issue is discussed with OEM & the report will be furnished. EE (E )/CEED:KPCL: 04/12/2023 12:52:33: The DR & EL details vide email dated:16.11.2023 have been furnished to OEM. Reply is waited from OEM EE (E )/CEED:KPCL: 04/03/2024 15:36:43: The DR & EL details vide email dated:16.11.2023 have been furnished to OEM. Reply is waited from OEM EE (E )/CEED:KPCL: 02/04/2024 14:24:01: The DR & EL details vide email dated:16.11.2023 have been furnished to OEM. Reply is waited from OEM EE (E )/CEED:KPCL: 03/06/2024 15:08:13: The DR & EL details vide email dated:16.11.2023 have been furnished to OEM. Reply is waited from OEM EE (E )/CEED:KPCL: 04/07/2024 14:33:51: The DR & EL details vide email dated:16.11.2023 have been furnished to OEM. Reply is waited from OEM EE (E )/CEED:KPCL: 06/08/2024 16:55:57: The issue is discussed with OEM & Reply from OEM is still awaited. EE (E )/CEED:KPCL: 01/10/2024 17:09:24: Cause of the fault is analyzed and was due to trancient fault towards live bus resulted in tripping of reemote end breakers of four live lines under Z2 at remote ends, where as vartahi end breakers sensed Z4 having Z4 time dalay of 1Sec hence not tripped at Varahi End. The outage was not due to Bus bsr protection trip. it was due to tripping of all lines. The Z4 time settings are revised to 0.5 secs. Requested to close the point. | Complied | Pending
110/I/2 | Complete Outage of 220kV Varahi PH of KPCL | 09-08-2023 13:36 | As per the reports submitted, the triggering incident was R-N fault in 220kV Varahi Shimoga line-3. At the same time, other lines connected to the bus tripped on zone-2 operation from remote ends and were holding at Varahi end. Tripping of all the connected lines resulted in complete outage of 220kV Varahi PH. Further details are awaited. | KPCL/KPTCL to analyze the reason for the Zone-1 operation for the 220kV Varahi-Shimoga-3 and rectify the issues ,if any, observed. | KPTCL |  | Pending | Pending
110/I/3 | Complete Outage of 220kV Kodasalli PH, 220kV Kadra PH of KPCL and 220kV/110kV Karwar SS of KPTCL | 12-08-2023 11:38 | During antecedent conditions, 220kV Kaiga Kadra and 220kV Kaiga Kodasalli were under outage. 220kV Kodasalli PH, 220kV Kadra PH and 220kV/110kV Karwar SS were being radially fed from 220kV Nagjheri PH. As per the reports submitted, the triggering incident was the tripping of 220kV Nagjheeri Kodsalli Line-1 and 220kV Nagjheri Kodsalli Line-2 on earth fault protection at Nagjheri end and further details are awaited. Tripping of both lines led to complete outage of 220kV Nagjheri PH, 220kV Kodasalli PH, 220kV Kadra PH and 220kV/110kV Karwar SS . | KPCL/KPTCL to check the resistive reach at Kodasalli end for the 220 kV Nagjheri-Kodasalli Line | KPCL | EE (E )/CEED:KPCL: 03/10/2023 17:01:51: KPTCL was requested to review the settings & the same will be checked in consultation with KPTCL. EE (E )/CEED:KPCL: 03/11/2023 10:41:52: KPTCL was requested to review the settings and the same will be checked in consultation with KPTCL. EE (E )/CEED:KPCL: 04/12/2023 13:00:58: KPTCL was requested to review the settings and the same will be checked in consultation with KPTCL. EE (E )/CEED:KPCL: 02/04/2024 14:24:01: KPTCL was requested to review the settings and the same will be checked in consultation with KPTCL. EE (E )/CEED:KPCL: 03/06/2024 15:08:13: KPTCL was requested to review the settings and the same will be checked in consultation with KPTCL. EE (E )/CEED:KPCL: 04/07/2024 14:33:51: KPTCL was requested to review the settings and the same will be checked in consultation with KPTCL. EE (E )/CEED:KPCL: 06/08/2024 16:55:57: KPTCL was requested to review the settings & the same will be checked in consultation with KPTCL. EE (E )/CEED:KPCL: 02/09/2024 10:51:01: KPTCL was requested to review the settings & the same will be checked in consultation with KPTCL. EE (E )/CEED:KPCL: 01/10/2024 15:32:19: KPTCL was requested to review the settings & the same will be checked in consultation with KPTCL. EE (E )/CEED:KPCL: 06/11/2024 12:26:37: KPTCL was requested to review the settings & the same will be checked in consultation with KPTCL. EE (E )/CEED:KPCL: 02/12/2024 14:42:59: KPTCL was requested to review the settings & the same will be checked in consultation with KPTCL. EE (E )/CEED:KPCL: 02/01/2025 12:15:19: KPTCL was requested to review the settings & the same will be checked in consultation with KPTCL. EE (E )/CEED:KPCL: 05/02/2025 15:29:00: KPTCL was requested to review the settings & the same will be checked in consultation with KPTCL. EE (E )/CEED:KPCL: 01/03/2025 14:23:15: KPTCL confirmed that the resistive reach settings at Kodasalli end for the 220 kV Nagjhari lines are reveiwed and is corrcet. As the same settings are adopted, It is requested to close the piont. | Complied | Complied
110/I/3 | Complete Outage of 220kV Kodasalli PH, 220kV Kadra PH of KPCL and 220kV/110kV Karwar SS of KPTCL | 12-08-2023 11:38 | During antecedent conditions, 220kV Kaiga Kadra and 220kV Kaiga Kodasalli were under outage. 220kV Kodasalli PH, 220kV Kadra PH and 220kV/110kV Karwar SS were being radially fed from 220kV Nagjheri PH. As per the reports submitted, the triggering incident was the tripping of 220kV Nagjheeri Kodsalli Line-1 and 220kV Nagjheri Kodsalli Line-2 on earth fault protection at Nagjheri end and further details are awaited. Tripping of both lines led to complete outage of 220kV Nagjheri PH, 220kV Kodasalli PH, 220kV Kadra PH and 220kV/110kV Karwar SS . | KPCL/KPTCL to check the resistive reach at Kodasalli end for the 220 kV Nagjheri-Kodasalli Line | KPTCL | EE (E )/CEED:KPCL: 01/10/2024 16:45:48: KPTCL was requested to review the settings & the same will be checked in consultation with KPTCL. Puspha:KPTCL: 17/02/2025 16:44:28: Settings issued to KPCL for Kodasalli-Nagzari lines at Kodasalli end (for REL670) relay is verified and it is in order as per theprotection philosophy followed in KPTCL. KPCL may verify the adopted reaches . Puspha:KPTCL: 02/03/2025 23:54:12: Settings given by KPTCL are in order , adopted settings to be veriffied by KPCL , | Complied | Complied
110/I/3 | Complete Outage of 220kV Kodasalli PH, 220kV Kadra PH of KPCL and 220kV/110kV Karwar SS of KPTCL | 12-08-2023 11:38 | During antecedent conditions, 220kV Kaiga Kadra and 220kV Kaiga Kodasalli were under outage. 220kV Kodasalli PH, 220kV Kadra PH and 220kV/110kV Karwar SS were being radially fed from 220kV Nagjheri PH. As per the reports submitted, the triggering incident was the tripping of 220kV Nagjheeri Kodsalli Line-1 and 220kV Nagjheri Kodsalli Line-2 on earth fault protection at Nagjheri end and further details are awaited. Tripping of both lines led to complete outage of 220kV Nagjheri PH, 220kV Kodasalli PH, 220kV Kadra PH and 220kV/110kV Karwar SS . | KPCL/KPTCL to provide the detailed analysis of the event. | KPCL | EE (E )/CEED:KPCL: 03/10/2023 17:02:55: The detailed report is already furnished before 110th PCSC meeting & will be reviewed again & report will furnished. EE (E )/CEED:KPCL: 03/11/2023 10:41:52: The detailed report is already furnished before 110th PCSC meeting & will be reviewed again & report will be furnsihed. EE (E )/CEED:KPCL: 04/12/2023 13:00:58: The detailed report is already furnished before 110th PCSC meeting & will be reviewed again & report will be furnished after consultation with KPTCL EE (E )/CEED:KPCL: 04/03/2024 15:21:58: The detailed report already submitted. Request to close the point. EE (E )/CEED:KPCL: 02/04/2024 14:24:01: The detailed report already submitted. Request to close the point. EE (E )/CEED:KPCL: 03/06/2024 15:08:13: The detailed report already submitted. Request to close the point. EE (E )/CEED:KPCL: 04/07/2024 14:33:51: The detailed report already submitted. Request to close the point. EE (E )/CEED:KPCL: 06/08/2024 16:55:57: The detailed report is already furnished before 110th PCSC meeting. Request to close the point EE (E )/CEED:KPCL: 02/09/2024 10:51:01: The detailed report is already furnished before 110th PCSC meeting. Request to close the point | Complied | Complied
110/I/3 | Complete Outage of 220kV Kodasalli PH, 220kV Kadra PH of KPCL and 220kV/110kV Karwar SS of KPTCL | 12-08-2023 11:38 | During antecedent conditions, 220kV Kaiga Kadra and 220kV Kaiga Kodasalli were under outage. 220kV Kodasalli PH, 220kV Kadra PH and 220kV/110kV Karwar SS were being radially fed from 220kV Nagjheri PH. As per the reports submitted, the triggering incident was the tripping of 220kV Nagjheeri Kodsalli Line-1 and 220kV Nagjheri Kodsalli Line-2 on earth fault protection at Nagjheri end and further details are awaited. Tripping of both lines led to complete outage of 220kV Nagjheri PH, 220kV Kodasalli PH, 220kV Kadra PH and 220kV/110kV Karwar SS . | KPCL/KPTCL to provide the detailed analysis of the event. | KPTCL | EE (E )/CEED:KPCL: 01/10/2024 16:45:48: Reports uploaded in SRLDC Portal. Requested to close the point. | Complied | Complied
110/II/3 | Tripping of 400 kV KAIGA - GUTTUR 2 | 04-Aug-2023 19:42 | Line tripped only at Guttur end. Tripping needs review. Findings and remedial actions shall be furnished. | KPTCL to furnish the detailed analysis report after visiting the Guttur Station. | KPTCL | Puspha:KPTCL: 17/02/2025 17:26:58: Attended, Physical inspection of the site is done and updated to SRPC forum. SRPC is requested to close the recommendation. | Complied | Complied
110/II/5 | Tripping of 220kV Bus-1 of 220kV Alamatti Generating station of KPCL | 09-Aug-2023 06:02 | During antecedent conditions, 220kV Alamatti Generating station was operating with split bus condition at 220kV level. 220kV Alamatti Bagewadi Line-1, 220kV Alamatti Bagalkot Line-1 and Unit-4,5 and 6 are connected to 220kV Bus-1. As per the reports submitted, the triggering incident was R-N fault in 220kV Alamatti Bagewadi Line-1. At the same time, 220kV Alamatti Bagalkot Line-1 tripped at Bagalkot end on zone-2. Tripping of both lines led to loss of evacuation path for the Unit-4,5&6 and they tripped on over frequency protection. This led to de-energisation of 220kV Bus-1 at Alamatti Generating station. Subsequently, Unit-1,2&3 connected to 220kV Bus-2 tripped and further details are awaited. | KPCL to revise the settings of Over current protection of generating units | KPCL | EE (E )/CEED:KPCL: 03/10/2023 17:04:41: The OCR settings will be increased after consultation with KPTCL. EE (E )/CEED:KPCL: 03/11/2023 10:41:52: The OCR settings will be increased after consultation with KPTCL EE (E )/CEED:KPCL: 04/12/2023 13:02:23: The OCR settings will be increased after consultation with KPTCL EE (E )/CEED:KPCL: 02/04/2024 14:24:01: OCR increased to 1.1 & time is 0.3sec EE (E )/CEED:KPCL: 03/06/2024 15:08:13: Complied. EE (E )/CEED:KPCL: 04/07/2024 14:33:51: Complied EE (E )/CEED:KPCL: 06/08/2024 16:55:57: Work completed. | Complied | Complied
111/I/1 | Complete Outage of 220kV/110kV Ranebennur SS, 220kV/33kV Sarjan_Suzlon Wind_Guttur, 220kV/66kV Davanagere SS, 220kV/33kV Suzlon_Wind_Honnali, and 220kV/66kV Benkikere SS of KPTCL | 23-08-2023 15:50 | As per the information received, the triggering incident was failure of R-phase CT of 220kV Guttur Ranebennur line at Guttur end. This resulted in the operation of 220kV Bus-2 BBP at 400kV/220kV Guttur SS and all the elements connected to 220kV Bus-2 got tripped. This in turn resulted in the complete loss of supply to 220kV Sarjan_Suzlon Wind_Guttur and 220kV/110kV Ranebennur SS since both SS were only connected to 220kV Bus-2 at 400kV/220kV Guttur SS. After the tripping of 220kV Guttur Davanagere line-1 and 2 on 220kV Bus-2 BBP operation, 220kV Guttur Davanagere line-3 which was connected to 220kV Bus-1 also got tripped on operation of overcurrent protection. This resulted in complete outage of 220kV/66kV Davanagere SS which in turn led to the de-energization of 220kV Bus-2 at 220kV/66kV Honnali SS. Due to this, there was complete loss of supply at 220kV/66kV Benkikere SS, and 220kV/33kV Suzlon_Wind_Honnali. | KPTCL to conduct the trans play of Main-1 and Main-2 for 220 kV Guttur- Davangere Line-1, checking PT ratio and DR time synchronization needs to be addressed. | KPTCL | Puspha:KPTCL: 17/02/2025 17:25:43: Relay Settings checked,logic issue rectified at both ends, DR time sync issue also resolved at Guttur. Once logic issues are resolved further no such trippings occurred .In view of this SRPC is requested to close this recommendations. | Complied | Complied
108/I/16 | Complete Outage of 220kV Varahi PH of KPCL | 11-05-2023 18:34 | . | KPCL may implement the time-differentiated single-ph, single-shot A/R scheme for evacuation lines. | KPCL | srpcadmin:SRPC: 26/10/2023 17:25:35: KPCL Mail dated 03-08-2023_AND_30-08-2023_and_04-10-2023 Obtainiing of approval is under progress for floaitng tender for implementation of time differentiated AR is in progress. EE (E )/CEED:KPCL: 03/11/2023 10:27:23: Tender floated & obtaining from approval is sought from competitive authority. EE (E )/CEED:KPCL: 04/12/2023 13:02:23: Approval is awaited to place work order EE (E )/CEED:KPCL: 27/12/2023 12:48:48: Work order is placed & will be completed by Mar-2023. EE (E )/CEED:KPCL: 27/12/2023 12:50:25: Work order is placed & will be completed by Mar-2024 EE (E )/CEED:KPCL: 04/03/2024 15:12:57: SLDC was requested for line LC along with tentative schedule. SLDC has informed that LC will be permitted only after Mar 15th. EE (E )/CEED:KPCL: 02/04/2024 14:24:01: SLDC was requested for line LC along with tentative schedule. SLDC has informed that LC will be permitted only after Mar 15th. EE (E )/CEED:KPCL: 04/07/2024 14:37:07: SLDC was requested for line LC along with tentative schedule. SLDC has informed that LC will be permitted only after Mar 15th. EE (E )/CEED:KPCL: 06/08/2024 16:55:57: Work completed & AR will be enabled in consultation with KPTCL. | Complied | Complied
46/II/21 | . | 07-06-2015 at 01:35 hrs | . | KPCL to use both the 220 kV buses as main buses under normal operation, and should go for single bus operation only during emergencies | KPCL | EE (E )/CEED:KPCL: 03/11/2023 10:35:18: 1) & 2) Completed. 3) The feasibilty for the Two Bus operation with the Bus coupler for 220kV switchyard will be appraised and will be made operational. EE (E )/CEED:KPCL: 04/12/2023 13:04:27: The feasibilty for the Two Bus operation with the Bus coupler for 220kV switchyard will be appraised and will be made operational. EE (E )/CEED:KPCL: 04/03/2024 15:32:32: The feasibility for the Two Bus operation with the Bus coupler for 220kV switchyard will be appraised and will be made operational. EE (E )/CEED:KPCL: 02/04/2024 14:24:01: The feasibility for the Two Bus operation with the Bus coupler for 220kV switchyard will be appraised and will be made operational. EE (E )/CEED:KPCL: 03/06/2024 15:08:13: The feasibility for the Two Bus operation with the Bus coupler for 220kV switchyard will be appraised and will be made operational. EE (E )/CEED:KPCL: 04/07/2024 14:33:51: The feasibility for the Two Bus operation with the Bus coupler for 220kV switchyard will be appraised and will be made operational. EE (E )/CEED:KPCL: 06/08/2024 16:55:57: The feasibility for the Two Bus operation with the Bus coupler for 220kV switchyard will be appraised and will be made operational. EE (E )/CEED:KPCL: 02/09/2024 10:51:01: The feasibility for the Two Bus operation with the Bus coupler for 220kV switchyard will be appraised and will be made operational. EE (E )/CEED:KPCL: 06/11/2024 12:26:37: The feasibility for the Two Bus operation with the Bus coupler for 220kV switchyard will be appraised and will be made operational EE (E )/CEED:KPCL: 02/12/2024 14:42:59: The feasibility for the Two Bus operation with the Bus coupler for 220kV switchyard will be appraised and will be made operational EE (E )/CEED:KPCL: 02/01/2025 12:15:19: The feasibilty for the Two Bus operation with the Bus coupler for 220kV switchyard will be appraised and will be made operational. EE (E )/CEED:KPCL: 06/02/2025 14:52:22: Retrofitting of ABB make REL511 relays with GE make D60 numerical relays as Main-I distance protection is completed for all the lines except RTPS-Mallat line and will be completed by March-2025. Two Bus will be made operational after completion of above works. EE (E )/CEED:KPCL: 01/03/2025 14:29:11: Retrofitting of ABB make REL511 relays with GE make D60 numerical relays as Main-I distance protection is completed for all the lines except RTPS-Mallat line and will be completed by March-2025. EE (E )/CEED:KPCL: 02/07/2025 10:38:15: Retrofitting of Bus bar protection relays is completed and double bus operation will be made operational after third party verification of busbar settings and commissioning. | Complied | Complied
54/II/13 | Tripping of Units at 220 kV Raichur TPS | 15-04-2016 at 15:36 hrs | During testing of retrofitted distance protection in 400kV Raichur-2 feeder, LBB protection trip DC got extended to Bus trip. This resulted in tripping of 220kV bus at RTPS and all connected 220 kV elements. Unit-4 which is connected to 400 kV Bus got tripped due to tripping of Station Utility Transformer that is connected 220 kV bus | In view of the availability of two buses along with healthy bus-coupler at 220 kV RTPS, KPCL is recommended to put in service the double-bus operation at 220 kV RTPS by suitably distributing loads within 15 days. | KPCL | EE (E )/CEED:KPCL: 03/11/2023 10:56:59: The feasibilty for the Two Bus operation with the Bus coupler for 220kV switchyard will be appraised and will be made operational. EE (E )/CEED:KPCL: 04/12/2023 13:04:27: The feasibility for the Two Bus operation with the Bus coupler for 220kV switchyard will be appraised and will be made operational. EE (E )/CEED:KPCL: 04/03/2024 15:32:32: The feasibility for the Two Bus operation with the Bus coupler for 220kV switchyard will be appraised and will be made operational. EE (E )/CEED:KPCL: 02/04/2024 14:26:49: The feasibility for the Two Bus operation with the Bus coupler for 220kV switchyard will be appraised and will be made operational. EE (E )/CEED:KPCL: 03/06/2024 15:08:13: The feasibility for the Two Bus operation with the Bus coupler for 220kV switchyard will be appraised and will be made operational. EE (E )/CEED:KPCL: 04/07/2024 14:33:51: The feasibility for the Two Bus operation with the Bus coupler for 220kV switchyard will be appraised and will be made operational. EE (E )/CEED:KPCL: 06/08/2024 16:55:57: The feasibility for the Two Bus operation with the Bus coupler for 220kV switchyard will be appraised and will be made operational. EE (E )/CEED:KPCL: 02/09/2024 10:51:01: The feasibility for the Two Bus operation with the Bus coupler for 220kV switchyard will be appraised and will be made operational. EE (E )/CEED:KPCL: 01/10/2024 16:53:38: The feasibility for the Two Bus operation with the Bus coupler for 220kV switchyard will be appraised and will be made operational. | Complied | Complied
73/I/5 | Complete outage of 220kV Varahi power station | 15-03-2018 at 22:36 hrs | There was Y-phase to ground fault on 220 kV Varahi Shimoga line-2. Consequent to persisting fault in Y phase, the breaker failure protection operated resulting in operation of 220KV bus bar protection at Varahi, tripping all the connected lines and Varahi running units. | KPCL to take steps to put double-bus operation into service at their 220 kV Varahi PH. | KPCL | EE (E )/CEED:KPCL: 03/11/2023 10:56:59: Double bus operation will be carried out after obtaining & discussion & confirmation with site. the same will be intimated at the earliest. EE (E )/CEED:KPCL: 04/12/2023 13:06:48: Consent has been given to site for combination of units and lines. The same will be implemented at the earliest. EE (E )/CEED:KPCL: 04/03/2024 15:27:19: Consent has been given to site for combination of units and lines. It will be put into operation after obtaining confirmation from OEM in respect of logics implemented in bus bar protection relay for double bus operation. . EE (E )/CEED:KPCL: 02/04/2024 14:26:49: Consent has been given to site for combination of units and lines. It will be put into operation after obtaining confirmation from OEM in respect of logics implemented in bus bar protection relay for double bus operation. EE (E )/CEED:KPCL: 03/06/2024 15:08:13: Consent has been given to site for combination of units and lines. It will be put into operation after obtaining confirmation from OEM in respect of logics implemented in bus bar protection relay for double bus operation. EE (E )/CEED:KPCL: 04/07/2024 14:33:51: 03/06/2024 15:08:13: Consent has been given to site for combination of units and lines. It will be put into operation after obtaining confirmation from OEM in respect of logics implemented in bus bar protection relay for double bus operation. EE (E )/CEED:KPCL: 02/04/2024 14:26:49: Consent has been given to site for combination of units and lines. It will be put into operation after obtaining confirmation from OEM in respect of logics implemented in bus bar protection relay for double bus operation. EE (E )/CEED:KPCL: 06/08/2024 16:55:57: Double bus operation will be carried out after obtaining & discussion & confirmation with site. the same will be intimated at the earliest. EE (E )/CEED:KPCL: 02/09/2024 10:51:01: Double bus operation will be carried out after Zone selectivity tests in consultation with OEM. EE (E )/CEED:KPCL: 01/10/2024 16:53:38: Double bus operation will be carried out after Zone selectivity tests in consultation with OEM. EE (E )/CEED:KPCL: 06/11/2024 12:25:31: Double bus operation will be carried out after Zone selectivity tests in consultation with OEM. EE (E )/CEED:KPCL: 02/12/2024 14:42:59: Double bus operation will be carried out after Zone selectivity tests in consultation with OEM. EE (E )/CEED:KPCL: 02/01/2025 12:26:20: Replacement of Bus bar protection panel is planned for next financial year. Double bus operation will be made operational after completion of said works. EE (E )/CEED:KPCL: 06/02/2025 14:50:00: Double Bus Bar Operation will be implemented after complete testing of Busbar protection. (Planned to complete by December-2025) EE (E )/CEED:KPCL: 01/03/2025 14:29:11: Double Bus Bar Operation will be implemented after complete testing of Busbar protection. (Planned to complete by December-2025) EE (E )/CEED:KPCL: 02/07/2025 10:47:08: Double Bus Bar Operation will be implemented after complete testing of Busbar protection. (Planned to complete by December-2025) EE (E )/CEED:KPCL: 04/08/2025 10:31:39: Work order has been issued for OEM to carryout the zone selectivity tests and will be completed by NOV 2025. Double bus operation will be made operational DEC 2025. EE (E )/CEED:KPCL: 30/08/2025 14:55:02: Work order has been issued for OEM to carryout the zone selectivity tests and will be completed by NOV 2025. Double bus operation will be made operational DEC 2025. EE (E )/CEED:KPCL: 04/10/2025 11:41:34: Work order has been issued for OEM to carryout the zone selectivity tests and will be completed by NOV 2025. Double bus operation will be made operational by DEC 2025. EE (E )/CEED:KPCL: 04/11/2025 10:04:03: Work order has been issued for OEM to carryout the zone selectivity tests and will be completed by NOV 2025. Double bus operation will be made operational by DEC 2025. EE (E )/CEED:KPCL: 04/12/2025 16:42:28: Works completed and Double bus operation is in Service on trial basis. Will be contined in Double bus operation. Requested to drop the point. | Complied | Complied
78/I/1 | Complete Outage of 220 kV Varahi UGPH. | 24-08-2018 at 11:00 hrs | Due to suspected mal-operation of 220KV bus bar protection at Varahi, all the connected lines and Varahi running Units got tripped. (6 nos 220kV lines and 4 nos Varahi generating station running Units). This resulted in complete outage of 220kV Varahi UGPH | 1. KPCL to take steps to put double-bus operation into service at their 220 kV Varahi UGPH by December, 2018. 2. KPCL to employ correct operational practices like keeping DC fuses of B/C CB intact during bus changeover works, disabling back-up protections of B/C CB during bus changeover works & enabling them with proper settings only when it is used as Main-CB of the grid elements. | KPCL | EE (E )/CEED:KPCL: 03/11/2023 10:46:30: Double bus operation will be carried out after obtaining & discussion & confirmation with site. the same will be intimated at the earliest. EE (E )/CEED:KPCL: 04/12/2023 13:06:48: Consent has been given to site for combination of units and lines. The same will be implemented at the earliest. EE (E )/CEED:KPCL: 04/03/2024 15:32:32: Consent has been given to site for combination of units and lines. It will be put into operation after obtaining confirmation from OEM in respect of logics implemented in bus bar protection relay for double bus operation. EE (E )/CEED:KPCL: 02/04/2024 14:26:49: Consent has been given to site for combination of units and lines. It will be put into operation after obtaining confirmation from OEM in respect of logics implemented in bus bar protection relay for double bus operation. EE (E )/CEED:KPCL: 03/06/2024 15:08:13: Consent has been given to site for combination of units and lines. It will be put into operation after obtaining confirmation from OEM in respect of logics implemented in bus bar protection relay for double bus operation. EE (E )/CEED:KPCL: 04/07/2024 14:33:51: 03/06/2024 15:08:13: Consent has been given to site for combination of units and lines. It will be put into operation after obtaining confirmation from OEM in respect of logics implemented in bus bar protection relay for double bus operation. EE (E )/CEED:KPCL: 02/04/2024 14:26:49: Consent has been given to site for combination of units and lines. It will be put into operation after obtaining confirmation from OEM in respect of logics implemented in bus bar protection relay for double bus operation. EE (E )/CEED:KPCL: 06/08/2024 16:55:57: Double bus operation will be carried out after obtaining & discussion & confirmation with site. the same will be intimated at the earliest. EE (E )/CEED:KPCL: 02/09/2024 10:56:47: Double bus operation will be carried out after Zone selectivity tests in consultation with OEM. EE (E )/CEED:KPCL: 01/10/2024 16:53:38: Double bus operation will be carried out after Zone selectivity tests in consultation with OEM. EE (E )/CEED:KPCL: 06/11/2024 12:25:31: Double bus operation will be carried out after Zone selectivity tests in consultation with OEM. EE (E )/CEED:KPCL: 02/12/2024 14:42:59: Double bus operation will be carried out after Zone selectivity tests in consultation with OEM. EE (E )/CEED:KPCL: 02/01/2025 12:26:20: Replacement of Bus bar protection panel is planned for next financial year. Double bus operation will be made operational after completion of said works. EE (E )/CEED:KPCL: 05/02/2025 15:29:00: Double Bus Bar Operation will be implemented after complete testing of Busbar protection, Selectivity tests with OEM. (Planned to take up in FY-2025-26 and complete by December-2025) EE (E )/CEED:KPCL: 01/03/2025 14:29:11: Double Bus Bar Operation will be implemented after complete testing of Busbar protection. (Planned to complete by December-2025) EE (E )/CEED:KPCL: 02/07/2025 10:47:08: Double Bus Bar Operation will be implemented after complete testing of Busbar protection. (Planned to complete by December-2025) E EE (E )/CEED:KPCL: 04/08/2025 10:31:39: Work order has been issued for OEM to carryout the zone selectivity tests and will be completed by NOV 2025. Double bus operation will be made operational DEC 2025. EE (E )/CEED:KPCL: 30/08/2025 14:55:02: Work order has been issued for OEM to carryout the zone selectivity tests and will be completed by NOV 2025. Double bus operation will be made operational DEC 2025 EE (E )/CEED:KPCL: 04/10/2025 11:42:17: Work order has been issued for OEM to carryout the zone selectivity tests and will be completed by NOV 2025. Double bus operation will be made operational DEC 2025. EE (E )/CEED:KPCL: 04/11/2025 10:04:03: Work order has been issued for OEM to carryout the zone selectivity tests and will be completed by JAN 2026 EE (E )/CEED:KPCL: 04/12/2025 16:42:28: Works completed and Double bus operation is in Service on trial basis. Will be contined in Double bus operation. Requested to drop the point. | Complied | Complied
87/I/3 | Complete Outage of 220kV Kemar, MSEZ, Puttur&Kavoor stations of KPTCL | 29-09-2019 at 11:31 hrs | 1.Single line to ground fault occurred in 220kV Kemar Varahi line-2 due to R-phase insulator flashover and the line tripped on Zone-1 distance protection. Simultaneously, 220kV Kemar Varahi line-1 tripped at Kemar end only. 2. 220kV Kemar Varahi line-3 tripped due to overloading. This resulted in complete loss of supply at 220kV Kemar since all the three source feeders tripped. 3. In addition there was complete loss of supply at 220kV MSEZ, 220kV Kavoor and 220kV Puttur stations since these stations were radially fed from 220kV Kemar station. | KPCL to check A/R functionality for all lines emanating from 220 kV Varahi GS and submit a report regarding the same. | KPCL | EE (E )/CEED:KPCL: 03/11/2023 10:56:59: Tender floated & obtaining from approval is sought from competitive authority. EE (E )/CEED:KPCL: 04/12/2023 13:02:23: Approval is awaited to place work order EE (E )/CEED:KPCL: 27/12/2023 12:48:48: Work order is placed & will be completed by Mar-2023. EE (E )/CEED:KPCL: 27/12/2023 12:50:25: Work order is placed & will be completed by Mar-2024. EE (E )/CEED:KPCL: 04/03/2024 15:29:57: SLDC was requested for line LC along with tentative schedule. SLDC has informed that LC will be permitted only after Mar 15th. EE (E )/CEED:KPCL: 02/04/2024 14:26:49: SLDC was requested for line LC along with tentative schedule. SLDC has informed that LC will be permitted only after Mar 15th. EE (E )/CEED:KPCL: 03/06/2024 15:08:13: Work is under progress & will be completed by June-2024. The AR will be enabled in coordination with KPTCL. EE (E )/CEED:KPCL: 04/07/2024 14:33:51: EE (E )/CEED:KPCL: 04/07/2024 14:47:48: In VS-1,VS-2,VS-3,VM1,VM2 lines & BC auto reclosure logics modified and tested, VH line AR logics to be modified and tested. Work under progress and will be completed by July-2024. EE (E )/CEED:KPCL: 06/08/2024 16:55:57: Work completed & AR will be enabled in consultation with KPTCL. EE (E )/CEED:KPCL: 02/09/2024 10:56:47: Work completed & AR will be enabled in consultation with KPTCL. | Complied | Complied
42/I/2 | Complete outage of 220 kV Ambewadi substation of KPTCL | 12-03-2015 at 7:51 hrs | Fault in 220kV Ambewadi-Nagjheri line-2 | 1. KPTCL shall provide A/R feature on Ambewadi Ponda 220 kV D/C inter-state line. 2. Till the completion of R&M works for bus bar and LBB protection, KPTCL shall explore the possibility of having split bus operation at Ambewadi and submit the details of the same to PCSC forum. | KPTCL | Puspha:KPTCL: 06/03/2024 22:48:58: At Ambewadi, AR enabled forNagzari 1 &2 lines on 06.03.2024 Puspha:KPTCL: 17/02/2025 22:32:24: Ambewadi-Xeldom and Ambewadi-Ponda being two inter state inter regional lines which are operated radially, AR is not enabled as per the practice followed in KPTCL for singke circuit radial lines AR is not enabled. | Complied | Complied
48/I/3 | Outage of 220kV Ambewadi station in Karnataka | 30-09-2015 at 10:41 hrs | 220kV Ambewadi-Nagjheri line-2 tripped on B-phase to earth fault. This resulted in loss of supply to 220kV Ambewadi bus. 220kV Ambewadi-Ponda line-1&2 were hand tripped after deenergization of bus at Ambewadi. | KPTCL to fast-track providing A/R on all 220 kV lines emanating from Ambewadi SS to prevent Station shut-down on temporary faults. | KPTCL | Puspha:KPTCL: 05/03/2024 10:43:55: The GPS device is sent to OEM M/s SANDS factory at Chennai, expected to receive the device in second week of March 2024. Once the GPS device is received and put back to service the time sync issue will be resolved. Puspha:KPTCL: 06/03/2024 22:47:06: Auto Reclosure enabled for Nagzari 1 &2 lines at Ambewadi on 06.03.2024 Puspha:KPTCL: 09/05/2024 15:18:47: At Ambewadi Auto reclosure is enabled for Nagzari lines. Narendra lines to be enabled after structure replacement work. Lines connecting to Goa are radial lines for which AR is not enabled. | Pending | Pending
62/II/5 | Tripping of 220 kV South Bus and connected elements (220kV HSR, 220kV Nagnathpura, 220 kV Harohalli, 220 kV Subramanyapura, 220 kV Tataguni, 220 kV Mallur and 400/220kV ICT-2 and 3) at 400/220kV Somanhalli substation of KPTCL (Load loss: 850 MW) | 20-01-2017 at 14:34 hrs | Triggering incident was fault in 66 kV Somanahalli - Bannerghatta line and fault was cleared by operation of Back-up OCR at Somanahalli end. | KPTCL to provide numerical Busbar Protection at their 220 kV Somanahalli SS at the earliest. | KPTCL | Puspha:KPTCL: 06/12/2023 16:55:10: Work is pending due to poor response from the turn key agency executing the R&M works. Puspha:KPTCL: 17/02/2025 17:27:51: Testing and commissioning works of Bus Bar Protection is under progress at Somanahally. Puspha:KPTCL: 03/02/2026 15:02:51: Attended.Busbar protection is commissioned for 220kV buses at SOmanahally | Complied | Complied
112/I/4 | Complete Outage of 220kV/66kV Koramangala SS and 220kV/66kV Nimhans SS of KPTCL | 06-10-2023 12:09 | The triggering incident was a Y-N fault in the 220kV Koramangala Nimhans line and the line tripped. At the same time, 220kV HSR Koramangala line tripped at HSR end. This resulted in a complete outage of 220kV/66kV Koramangala SS and 220kV/66kV Nimhans SS. | KPTCL to rectify the OF communication problem. | KPTCL |  | Pending | Pending
112/I/5 | Complete Outage of 220kV/66kV A Station, 220kV/66kV Subramanyapura SS, 220kV/66kV Peenya SS, 220kV/66kV Brindavan SS, 220kV/66kV/11kV NRS station and 220kV/66kV Khodays SS of KPTCL | 09-10-2023 09:32 | During antecedent conditions, 220kV/66kV A Station, 220kV/66kV Subramanyapura SS, 220kV/66kV Peenya SS, 220kV/66kV Brindavan SS, 220kV/66kV/11kV NRS station and 220kV/66kV Khodays SS were being radially fed through 220kv Nelamangala Peenya Line-2,3 and 220kV Nelamangala Brindavan line. The triggering incident was 220kV Nelamangala Peenya Line-2. Subsequently, 220kV Nelamangala Peenya Line-3 and 220kV Nelamangala Brindavan lines tripped on overloading at Nelamangala end. Tripping of all these lines resulted in complete outage of the radially connected stations too. | 1.KPTCL to review/finalize SPS in consultation with SRLDC 2.SOP to be followed by SLDC in real time operation. | KPTCL | Puspha:KPTCL: 17/02/2025 17:29:13: SPS implemented for Tied operation of sources in Bangalore is submitted to SRPC/SRLDC and the same has been approved in the OCC forum. SRPC is requested to close the recommendations in this regard | Complied | Complied
112/I/7 | Complete Outage of 220kV Nandhihal, 220kV/11kV Bijapur SS, 220kV/110kV Indi SS and 220kV/110kV Aheri SS of KPTCL and 220kV/33kV Vaishali | 10-10-2023 12:35 | The triggering incident was R-N fault in 220kV Kudgi_NTPC Nandhihal line-4. Breaker at Nandhihal end failed to open causing LBB to operate. Immediately all the elements connected to the 220kV Bus-1 tripped resulting in complete outage of 220kV Nandhihal SS. Since, 220kV/11kV Bijapur SS, 220kV/110kV Indi SS, 220kV/110kV Aheri SS and 220kV/33kV Vaishali were being radially connected to 220kV Nandhihal, outage of Nandhihal resulted in complete outage of these stations. | KPTCL to open both the bus isolators during outage period and include the same in the SOP accordingly | KPTCL | Puspha:KPTCL: 04/02/2024 22:34:41: Puspha:KPTCL: 01/12/2024 23:48:00: Directions have been given to follow the same as part of SOP Puspha:KPTCL: 17/02/2025 17:05:10: Attended, directions have been given to follow the same as part of SOP | Complied | Complied
109/II/13 | Tripping of 400/220kV ICT-2 at GUTTUR | 23-07-2023 12.20 | ICT tripped due to problem with local remote switch in breaker cubicle. Findings and remedial actions taken shall be furnished. | KPTCL to carry out a physical inspection of Guttur Substation & ICTs and furnish the findings to SRPC & SRLDC. | KPTCL | Puspha:KPTCL: 06/12/2023 16:59:28: The physical inspection of Guttur sub station was conducted by CEE,RT and R&D along with CEE,Transmission ZOne,Tumkur on 20.10.2023 and conducted site meeting. Actionable points to mitigate spurious trippings due to control cable issues were discussed during the site meeting. Procurement of new control cables required is under progress in CEE,TZ, Tumkur office. | Complied | Complied
107/I/6 | Complete Outage of 220kV Suzlon_Honnahalli_wind of Suzlon_KA and multiple trippings at 220kV/66kV Honnali SS, 220kV/110kV KB Cross SS and 220kV/110kV MRS Shimoga SS of KPTCL | 03-03-2023 12:50 | . | KPTCL to take necessary precautions during the retrofitting works. Also recommdedned that Re-trip feature can be enabled in the relays. | KPTCL | Puspha:KPTCL: 01/12/2024 23:48:00: Suitable instructions have been given to the concerned officers Puspha:KPTCL: 17/02/2025 17:06:34: Suitable instructions have been given to the concerned officers | Complied | Complied
102/I/9 | Complete Outage of 220/ 110kV Ranebennur SS, 220/ 66kV Davanagere SS, 220/ 66kV Honnali SS and 220/ 66kV Benkikere SS and Multiple trippings in 400/ 220kV Guttur SS of KPTCL | 16-04-2022 01:43 | During the antecedent conditions, 220/ 110kV Ranebennur SS, 220/ 66kV Davanagere SS, 220/ 66kV Benkikere and 220kV Honnali SS were radially fed from 400/ 220kv Guttur SS. As per the reports submitted, the triggering incident was B-phase isolator failure in 220kV Guttur Haveri Line-1 at Guttur end resulting in Bus-1 fault. BBP initiated but did not operate due to DC supply failure. All 220kV lines connected to 220kV Guttur Bus-1 and Bus-2 got tripped on operation of Zone-4 protection. 400/ 220kV Guttur ICT-1 & 2 tripped on Back-up over current protection. This resulted in complete outage of 220/ 110kV Ranebennur SS, 220/ 66kV Davanagere SS, 220/ 66kV Honnali SS and 220/ 66kV Benkikere SS. | 1. KPTCL was recommended to configure DT sending to remote end during LBB operation. | KPTCL | srpcadmin:SRPC: 28/11/2023 16:49:11: 1). Yet to be confirmed by Guttur Sub station Puspha:KPTCL: 04/02/2024 22:28:20: SRPC recommendation regarding providing Alarm for Bus Bar DC fail is implemented | Pending | Pending
102/I/9 | Complete Outage of 220/ 110kV Ranebennur SS, 220/ 66kV Davanagere SS, 220/ 66kV Honnali SS and 220/ 66kV Benkikere SS and Multiple trippings in 400/ 220kV Guttur SS of KPTCL | 16-04-2022 01:43 | During the antecedent conditions, 220/ 110kV Ranebennur SS, 220/ 66kV Davanagere SS, 220/ 66kV Benkikere and 220kV Honnali SS were radially fed from 400/ 220kv Guttur SS. As per the reports submitted, the triggering incident was B-phase isolator failure in 220kV Guttur Haveri Line-1 at Guttur end resulting in Bus-1 fault. BBP initiated but did not operate due to DC supply failure. All 220kV lines connected to 220kV Guttur Bus-1 and Bus-2 got tripped on operation of Zone-4 protection. 400/ 220kV Guttur ICT-1 & 2 tripped on Back-up over current protection. This resulted in complete outage of 220/ 110kV Ranebennur SS, 220/ 66kV Davanagere SS, 220/ 66kV Honnali SS and 220/ 66kV Benkikere SS. | 2. KPTCL was also recommended to provide an Alarm in case of DC supply failure to BBP tripping circuit. | KPTCL | srpcadmin:SRPC: 28/11/2023 16:49:11: KPTCL Mail dated 03-08-2023 2). Alarm is provided for Bus Bar trip DC failure | Complied | Pending
107/I/1 | Multiple Trippings at 220V/66kV Malur SS and Complete Outage of 220kV/66kV Vikas Tech park, 220kV/66kV Sarjapur SS, and 220kV/66kV Exora SS of KPTCL | 04-02-2023 13:40 | . | To expedite the connectivity to Somanahally Station from Malur and reconductoring of 220kV lines in order to address the issue of split bus operation at Malur station. | KPTCL | Puspha:KPTCL: 17/02/2025 22:36:54: Malur Connectivity to Somanahally is not possible. However, commissioning of Hoody-Hagadur-Exora link which will be main source for EXORA and VTP is in commissioning stage. Once this 220kV link is established drawl from Hoody through Malur bus will come down. | Complied | Complied
107/I/5 | Complete Outage of 400kV/220kV Mylasandra SS, 220kV/66kV HSR SS, 220kV/66kV Koramangala SS, 220kV/66kV Nagnathpura SS, 220kV/66kV Nimhans SS, 220kV/66kV Jigani SS and 220kV/66kV Yerandahally SS of KPTCL | 25-02-2023 14:48 | . | KPTCL to ensure redundant supply availability to the loads when other source is taken under outage. | KPTCL | Puspha:KPTCL: 17/02/2025 22:38:45: Attended, after tieing of sources in and around Bangalore redundancy is available, In view of this SRPC is requested to close the recommendation. | Complied | Complied
95/II/9 | 220 kV Bus-1 outage at 400/220 kV Hoody SS of KPTCL | 25-01-21 00:42 | Triggering incident was R phase PT failure of Bus-1 at 220kV Hoody SS. All the elements connected to Bus-1 got tripped at 220kV Hoody Bus-1. 400kV Hoody-Devanahalli line-1 also got tripped during this event | KPTCL to expedite commissioning of BBP for 220kV bus at their 220/ 110/ 66kV Hoody substation. | KPTCL | Puspha:KPTCL: 17/02/2025 17:31:21: At 220kV Hoody Substation new Bus bar Protection is commissioned on 21.01.2025 | Complied | Complied
95/I/11 | Complete outage of 220kV Nagjheri PH , 110kV Supa PH of KPCL and 220kV Ambewadi SS of KPTCL | 25-02-21 13:16 | Triggering incident was B E fault in 220kV Naghjeri Hubli line-2. (220kV Naghjeri Hubli line 3 went out around 11:30 hrs.) 220kV Naghjeri Bidnal lines also got tripped on B E fault. Then, 220kV Naghjeri Hubli line 1 got tripped on operation of over-current protection. Due to tripping of evacuating lines, running units 2, 5 and 6 at Naghjeri got tripped on operation of over frequency protection. This resulted in complete loss of supply at 220kV Nagjheri PH, 110kV Supa PH and 220kV Ambewadi SS.During antecedent conditions, 220kV Ambewadi SS was radially fed from 220kV Naghjeri PH due to outage of 220kV Ambewadi Narendra lines. | KPCL to take steps to enable A/R on all 220 kV lines emanating from 220 kV Nagjheri GS. | KPCL | srpcadmin:SRPC: 28/11/2023 16:54:39: KPCL Mail dated 05-06-2023_(Discussed in Bilateral meeting held on 12.05.2023):_AND_03-08-2023_and_30-08-2023_&_04-10-23 Approval from PSDF was received on 31.03.2021. Detailed order is placed on M/s GE T&D Ltd. Contract agreement is executed with contractor & drawing approval is completed. Supply portion is completed. EE (E )/CEED:KPCL: 04/03/2024 15:36:43: Work completed at NPH end & enabled for Hubli lines. Awaited reply from KPTCL for enabling AR in remaining lines. Request to close the point from KPCL end EE (E )/CEED:KPCL: 02/04/2024 14:26:49: Work completed at NPH end & enabled for Hubli lines. Awaited reply from KPTCL for enabling AR in remaining lines. Request to close the point from KPCL end EE (E )/CEED:KPCL: 03/06/2024 15:08:13: Work completed at NPH end & enabled for Hubli lines. Awaited reply from KPTCL for enabling AR in remaining lines. Request to close the point from KPCL end EE (E )/CEED:KPCL: 04/07/2024 14:33:51: Work completed at NPH end & enabled for all lines except Bidnal line. Awaited reply from KPTCL for enabling AR in Bidnal line. Request to close the point from KPCL end EE (E )/CEED:KPCL: 06/08/2024 16:55:57: AR is enabled except Bidnal line EE (E )/CEED:KPCL: 02/09/2024 10:56:47: AR is enabled except Bidnal line EE (E )/CEED:KPCL: 01/10/2024 16:53:38: AR is enabled except Bidnal line and AR in Bidnal line will be enables in co ordination with KPTCL EE (E )/CEED:KPCL: 06/11/2024 12:25:31: AR is enabled except Bidnal line and AR in Bidnal line will be enables in co ordination with KPTCL EE (E )/CEED:KPCL: 02/12/2024 14:42:59: AR is enabled except Bidnal line and AR in Bidnal line will be enables in co ordination with KPTCL EE (E )/CEED:KPCL: 02/01/2025 12:18:50: AR is enabled except Bidnal line & NA-1 line and AR will be enabled in co ordination with KPTCL EE (E ) EE (E )/CEED:KPCL: 05/02/2025 15:29:00: Auto Reclosure Enabled for All Lines Except Ambewadi Line. Due to some problem, the Auto reclosure was disabled on 220kV Nagjhari- Ambewadi lines As per KPTCL request. KPTCL confirmed that after addressing the technical issue, the Auto reclosure will be enabled on 220kV Nagjheri-Ambewadi lines. EE (E )/CEED:KPCL: 01/03/2025 14:29:11: Auto Reclosure Enabled for All Lines Except Ambewadi Line. Due to some problem, the Auto reclosure was disabled on 220kV Nagjhari- Ambewadi lines As per KPTCL request. KPTCL confirmed that after addressing the technical issue, the Auto reclosure will be enabled on 220kV Nagjheri-Ambewadi lines. EE (E )/CEED:KPCL: 03/05/2025 15:17:36: A/R enabled for all lines at NPH except Ambewadi line as per the request of KPTCL .Hence request to close the point. | Complied | Complied
94/I/3 | Complete outage of 220kV Nandihal SS, Bijapur SS, and Indi SS | 17-Oct-20 22:35 | Triggering incident was failure of Y-ph Metering CT connected to Nandihal - GM Navara line-1. Bus bar protection operated at 220kV Nandihal station and all connected elements tripped. There was supply failure at 220kV Indi and Bijapur stations, since these station are radially fed from 220kV Nandihal station. | i. M/s. Gamesa Ltd./KPTCL to restore Double bus operation at 220kV Nandihal SS after replacing failed bus coupler CT. Ii. M/s. Gamesa Ltd./KPTCL to submit Equipment failure report for failed CT to CEA with a copy to SRPC | KPTCL | srpcadmin:SRPC: 28/11/2023 16:55:59: KPTCL Mail dated 03-06-2023_(Discussed in Bilateral meeting held on 12.05.2023): i. Failed CT is replaced by M/s Siemens Gamesa,double bus operation is yet to be restored at Nandihal Switching Station owned by IPP M/s Siemens Gamesa. ii. So far equipment failure reports of KPTCL sub stations are being sent to CEA by KPTCL. Nandihal Switching station owned and maintained by M/s Siemens Gamesa Pvt Ltd. In future, Equipment Failure report of Nandihal Switching station if any will be furnished to KPTCL by M/s Siemens Gamesa IPP for onward submission to CEA. SRPC is requested to close this observation. Puspha:KPTCL: 06/05/2024 14:42:55: Bus Coupler bay CTs are replaced. Due to problem with Bus Coupler Breaker double bus operation is not yet restored. Matter is being persued with M/s Siemens Gamesa Puspha:KPTCL: 01/12/2024 23:48:00: Attended and complied Puspha:KPTCL: 17/02/2025 17:07:21: Attended and complied by M/s Gamesa. Double bus operation is in place in Nandihal Switching station | Complied | Complied
113/I/3 | Complete Outage of 220kV/66kV Alipura SS of KPTCL | 17-10-2023 12:10 | As per the reports submitted, the triggering incident was a B-N fault in the 220kV Alipur BTPS line. At the BTPS end, the fault was sensed in zone-1 and the line tripped. Alipur end failed to clear the fault, and the fault was cleared by 220kV Alipur Regulpadu line on operation of zone-3 at Regulpadu end with a delay of 750ms. Tripping of both connected lines resulted in a complete outage of 220kV/66kV Alipura SS. | KPTCL to test the configuration of relays at Alipura end and submit a detailed report to SRPC & SRLDC. | KPTCL | Puspha:KPTCL: 02/04/2024 21:19:06: Compliance furnished to SRPC through email dt 22.12.2023 with a request to close the issue. Puspha:KPTCL: 09/05/2024 15:30:54: Attended and complied | Complied | Complied
113/II/2 | Tripping of 220kV Bus-1 of 400kV/220kV Munirabad SS of PGCIL SR-1 | 18-10-2023 15:17 | During antecedent conditions, at 400kV/220kV Munirabad SS, main circuit breaker of 220kV Munirabad Lingapur line-2 was bypassed and the line was charged through Bus Coupler by connecting to 220kV Bus-1. The triggering incident was the tripping of 220kV Munirabad Lingapur line-2 on the R-N fault. Since this is the only line connected to Bus-1 at Munirabad, this resulted in the de-energization of 220kV Bus-1 of 400kV/220kV Munirabad SS | KPTCL to expedite to put line breaker into service for 220kV Munirabad Lingapur line-2. | KPTCL | Puspha:KPTCL: 04/02/2024 22:30:12: Erection ,wiring, testing of the new circuit breaker was completed. Due to Inspectorate approval pending the same was not commissioned. Now approval is received. after their inspection new CB will be put in to service. Puspha:KPTCL: 06/03/2024 22:44:31: Replacement of existing age old Pneumatic type CGL make 220kV breaker by new CGL make spring type breaker at 400/220kV PGCIL, Gudadahalli has been completed successfully and commissioned on 05.03.2024 @ 22:12 Hrs. New breaker details:- Make:-CGL, 245kV, 3150A, 50kA, SF6 CB, Sl.No: 60964C. Puspha:KPTCL: 06/03/2024 22:45:57: Replacement of existing age old Pneumatic type CGL make 220kV breaker by new CGL make spring type breaker at 400/220kV PGCIL, Gudadahalli has been completed successfully and commissioned on 05.03.2024 @ 22:12 Hrs. New breaker details:- Make:-CGL, 245kV, 3150A, 50kA, SF6 CB, Sl.No: 60964C. Puspha:KPTCL: 25/03/2024 10:19:37: New Circuit Breaker commissioned for Lingapur line -2 at Munirabad on 05.03.2024 and complied to SRPC Puspha:KPTCL: 02/04/2024 21:21:38: New CB commissioned on 05.03.2024 and complied in PREC portal. Request SRPC to consider the same . Puspha:KPTCL: 09/05/2024 15:16:24: Attended and complied already Puspha:KPTCL: 09/05/2024 15:16:55: Attended and already coplied Puspha:KPTCL: 02/08/2024 22:42:24: Attended and complied. SRPC i requested to close the recommendation | Complied | Complied
113/III/7 | 400/220 kV ICT-1 AT HOODY and 400/220 kV ICT-3 AT HOODY | 15-11-2023 12:44 | As per the reports submitted, at 12:44hrs, the triggering incident was tripping of 400kV/220kV Hoody ICT-1 on over flux protection. Immediately, SPS operated and 150MVA Hoody Transformer tripped. Subsequently, at 13:02hrs, while checking the operating condition of MV side isolator of 400kV/220kV Hoody ICT-1, LBB maloperated and gave a trip signal to 400kV/220kV Hoody ICT-3. Tripping is not in order. | KPTCL to furnish the stage wise settings for over flux relay and to specify the base for revising the setting from 1.1 to 1.6. | KPTCL |  | Pending | Pending
114/I/4 | Complete Outage of 220kV/66kV Begur SS, 220kV/66kV TK Halli SS, 220kV/66kV Chamrajnagar SS, 220kV/66kV Madhuvanahalli SS and 220kV/66kV Hebbani SS and 220kV Bus-2 of 220kV/66kV Vajamangala SS of KPTCL | 29-11-2023 12:15 | As the reports submitted, the triggering incident was a Y-phase jumper failure in the 220kV My-sore Kadakola line. At both ends, the fault was sensed in zone 1. At the Kadakola end, the fault current was 10kA and this caused I>4 to operate which enabled the A/R block. Immediately, the line tripped. At Mysore end, the fault was sensed in zone-1. A/R operated and the line was hold-ing. At the same time, 220kV Kadakola Adakanahally Line-1&2 tripped on DEF protection at the Adakanahally end. At Vajamangala, the 220kV Vajamangala Hootagally line was on Bus-1 and the 220kV Vajamangala TK Halli line was on Bus-2 and Buscoupler was in closed condition. Af-ter tripping of above lines 220kV Bus coupler Breaker tripped at Vajamangala on over current relay. Subsequently, the Vajamangala bus coupler tripped on over current protection. This result-ed in complete outage of 220kV/66kV Begur SS, 220kV/66kV TK Halli SS, 220kV/66kV Chamrajnagar SS, 220kV/66kV Madhuvanahalli SS and 220kV/66kV Hebbani SS and 220kV Bus-2 of 220kV/66kV Vajamangala SS. | KPTCL to review the BUS COUPLER setting and furnish the report to SRPC and SRLDC | KPTCL | Puspha:KPTCL: 04/02/2024 22:37:38: Action has been taken verify the Bus Coupler settings. After review, compliance report will be submitted to SRPC/SRLDC. Puspha:KPTCL: 17/02/2025 22:39:58: | Complied | Complied
114/I/6 | Complete Outage of 400kV Talaguppa SS, 220kV Shimoga SS, Chikkamangalore SS, Heggunje SS, Kadur SS, Shiralkoppa SS, Sirsi SS, Arasikere SS and 220kV Bus-2 of Honnali SS of KPTCL and 220kV Varahi and Sharavathy SS of KPCL | 08-12-2023 14:37 | The triggering incident was R-N fault in 220kV Sharavathy Shimoga Line-1 at 14:35:24.351. At Shimoga end the fault was sensed in Zone 2 carrier aided protection operated with location of fault was around 89.6kM, Fault current recorded was 1.7kA in R phase. AR operated successfully and line was holding from Shimoga end. At Sharavathy, Shimoga line-1 relays sensed the fault in Zone-1, R phase with a fault current 2kA | KPCL to check the under frequency settings of all the units of Varahi Generating Stations as it operates at 48Hz. The same needs to comply with CEA Regulations | KPCL | EE (E )/CEED:KPCL: 04/03/2024 15:20:17: Settings revised as per CEA guidelines. Request to close the point. EE (E )/CEED:KPCL: 02/04/2024 14:26:49: Settings revised as per CEA guidelines. Request to close the point. EE (E )/CEED:KPCL: 03/06/2024 15:08:13: Complied EE (E )/CEED:KPCL: 04/07/2024 14:19:19: Settings revised as per CEA guidelines. Request to close the point. EE (E )/CEED:KPCL: 06/08/2024 16:55:57: Settings revised as per CEA guidelines. Request to close the point. EE (E )/CEED:KPCL: 02/09/2024 10:56:47: Settings revised as per CEA guidelines. Request to close the point. | Complied | Complied
114/I/6 | Complete Outage of 400kV Talaguppa SS, 220kV Shimoga SS, Chikkamangalore SS, Heggunje SS, Kadur SS, Shiralkoppa SS, Sirsi SS, Arasikere SS and 220kV Bus-2 of Honnali SS of KPTCL and 220kV Varahi and Sharavathy SS of KPCL | 08-12-2023 14:37 | The triggering incident was R-N fault in 220kV Sharavathy Shimoga Line-1 at 14:35:24.351. At Shimoga end the fault was sensed in Zone 2 carrier aided protection operated with location of fault was around 89.6kM, Fault current recorded was 1.7kA in R phase. AR operated successfully and line was holding from Shimoga end. At Sharavathy, Shimoga line-1 relays sensed the fault in Zone-1, R phase with a fault current 2kA | KPCL to disable the OVR settings in all 220 kV lines of Sharavathy | KPCL | EE (E )/CEED:KPCL: 04/03/2024 15:20:17: OVR settings is disabled. Request to close the point.. EE (E )/CEED:KPCL: 02/04/2024 14:26:49: OVR settings is disabled. Request to close the point.. EE (E )/CEED:KPCL: 03/06/2024 15:08:13: Complied. EE (E )/CEED:KPCL: 04/07/2024 14:19:19: OVR settings is disabled. Request to close the point. EE (E )/CEED:KPCL: 06/08/2024 16:55:57: OVR settings is disabled. Request to close the point. EE (E )/CEED:KPCL: 02/09/2024 10:56:47: OVR settings is disabled. Request to close the point. | Complied | Complied
114/I/6 | Complete Outage of 400kV Talaguppa SS, 220kV Shimoga SS, Chikkamangalore SS, Heggunje SS, Kadur SS, Shiralkoppa SS, Sirsi SS, Arasikere SS and 220kV Bus-2 of Honnali SS of KPTCL and 220kV Varahi and Sharavathy SS of KPCL | 08-12-2023 14:37 | The triggering incident was R-N fault in 220kV Sharavathy Shimoga Line-1 at 14:35:24.351. At Shimoga end the fault was sensed in Zone 2 carrier aided protection operated with location of fault was around 89.6kM, Fault current recorded was 1.7kA in R phase. AR operated successfully and line was holding from Shimoga end. At Sharavathy, Shimoga line-1 relays sensed the fault in Zone-1, R phase with a fault current 2kA | KPCL to enable the A/R on all 220 kV lines at Sharavathy Station | KPCL | EE (E )/CEED:KPCL: 04/03/2024 15:20:17: LC is awaited from SLDC. The same will be completed after obtaining LC. EE (E )/CEED:KPCL: 02/04/2024 14:26:49: LC is awaited from SLDC. The same will be completed after obtaining LC. EE (E )/CEED:KPCL: 03/06/2024 15:08:13: LC is awaited from SLDC. The same will be completed after obtaining LC. EE (E )/CEED:KPCL: 04/07/2024 14:19:19: LC is awaited from SLDC. The same will be completed after obtaining LC. EE (E )/CEED:KPCL: 06/08/2024 16:55:57: LC is awaited from SLDC. The same will be completed after obtaining LC. EE (E )/CEED:KPCL: 02/09/2024 10:56:47: LC is awaited from SLDC. The same will be completed after obtaining LC EE (E )/CEED:KPCL: 01/10/2024 15:32:19: Works completed AR will be enabled in coordination with KPTCL. | Complied | Complied
114/V/6 | 220kv Ambewadi-Xeldem | 16-12-2023 05:02 | As per the reports submitted, the triggering incident was R-N fault in the line. At Ambewadi end, zone-2 protection operated and the line tripped. Fault current was 2.36kA. Fault distance was 83.43kM from Ambewadi end. A/R is not in service since the line is radially connected. Tripping is in order. DR time sync issue needs review. Non-operation of carrier-aided zone-2 protection also needs review. | KPTCL to provide GPS equipment at Ambewadi station | KPTCL | Puspha:KPTCL: 04/02/2024 22:34:41: The faulty GPS time synchronizing equipment is released and sent to OEM SANDs factory at Chennai. After repairs time synchronization of relays will be restored. Puspha:KPTCL: 02/08/2024 22:41:34: Attended. GPS is put back to service on 29.05.2024 after repairs | Complied | Complied
115/I/2 | Complete Outage of 220kV Shimoga SS, Ka-dur SS, Heggunje SS and 220kV Bus-1 of Honnali SS, 220kV Bus-2 of Kemar SS, 220kV Bus-1 of KB Cross SS of KPTCL and 220kV Varahi of KPCL | 30-12-2023 20:18 | During antecedent conditions, 220kV MRS Shimoga was operating with single bus. The triggering incident was B-N fault in 220kV Shimoga Varahi Line-3. A/R is disabled at both ends. At Varahi, zone-2 protection operated and the line tripped with a delay of 360ms. At Shimoga end, the fault was sensed in zone-1 but B pole failed to open causing LBB to operate. This resulted in complete outage of 220kV Shimoga SS and the radial connected stations. At the same time Varahi Unit-3 tripped on under frequency resulting in complete of 220kV Varahi SS. Since the source feeders of 220kV Heggunje SS, 220kV Kadur SS, 220kV Bus-1 of Honnali SS, 220kV Bus-1 of KB Cross SS and 220kV Bus-2 of Kemar SS were from 220kV Shimoga and 220kV Varahi SS, complete outage of Shomoga and Varahi resulted in loss of power supply to these stations and buses. | KPCL to check and rectify the time sync issue. | KPCL | EE (E )/CEED:KPCL: 04/03/2024 15:36:43: Checked & found ok. Request to close the point. | Complied | Complied
115/I/2 | Complete Outage of 220kV Shimoga SS, Ka-dur SS, Heggunje SS and 220kV Bus-1 of Honnali SS, 220kV Bus-2 of Kemar SS, 220kV Bus-1 of KB Cross SS of KPTCL and 220kV Varahi of KPCL | 30-12-2023 20:18 | During antecedent conditions, 220kV MRS Shimoga was operating with single bus. The triggering incident was B-N fault in 220kV Shimoga Varahi Line-3. A/R is disabled at both ends. At Varahi, zone-2 protection operated and the line tripped with a delay of 360ms. At Shimoga end, the fault was sensed in zone-1 but B pole failed to open causing LBB to operate. This resulted in complete outage of 220kV Shimoga SS and the radial connected stations. At the same time Varahi Unit-3 tripped on under frequency resulting in complete of 220kV Varahi SS. Since the source feeders of 220kV Heggunje SS, 220kV Kadur SS, 220kV Bus-1 of Honnali SS, 220kV Bus-1 of KB Cross SS and 220kV Bus-2 of Kemar SS were from 220kV Shimoga and 220kV Varahi SS, complete outage of Shomoga and Varahi resulted in loss of power supply to these stations and buses. | KPCL to check the under frequency settings of all the units of Varahi Generating Stations as they are set at 48Hz. As per the CEA Technical Standards for Grid Connectivity, generating units shall be capable of operating in the frequency range of 47.5 Hz to 52 Hz. | KPCL | EE (E )/CEED:KPCL: 04/03/2024 15:36:43: Settings is revised as per CEA guidelines Request to close the point.. | Complied | Complied
115/I/2 | Complete Outage of 220kV Shimoga SS, Ka-dur SS, Heggunje SS and 220kV Bus-1 of Honnali SS, 220kV Bus-2 of Kemar SS, 220kV Bus-1 of KB Cross SS of KPTCL and 220kV Varahi of KPCL | 30-12-2023 20:18 | During antecedent conditions, 220kV MRS Shimoga was operating with single bus. The triggering incident was B-N fault in 220kV Shimoga Varahi Line-3. A/R is disabled at both ends. At Varahi, zone-2 protection operated and the line tripped with a delay of 360ms. At Shimoga end, the fault was sensed in zone-1 but B pole failed to open causing LBB to operate. This resulted in complete outage of 220kV Shimoga SS and the radial connected stations. At the same time Varahi Unit-3 tripped on under frequency resulting in complete of 220kV Varahi SS. Since the source feeders of 220kV Heggunje SS, 220kV Kadur SS, 220kV Bus-1 of Honnali SS, 220kV Bus-1 of KB Cross SS and 220kV Bus-2 of Kemar SS were from 220kV Shimoga and 220kV Varahi SS, complete outage of Shomoga and Varahi resulted in loss of power supply to these stations and buses. | KPTCL to expedite the process of breaker replacement and enable the A/R after replacement of the breaker. KPCL to enable A/R at after replacement of Breaker at Shimoga. | KPTCL | Puspha:KPTCL: 05/03/2024 10:18:33: AT Shimoga, replacement of Varahi-3 Circuit Breaker is taken up. New CB ereccted, wiring work under progress. Testing activity scheduled from in presence of OEM. After successful testing and commissioning new CB will be commissioned and AR will be put back to service. Puspha:KPTCL: 02/04/2024 21:45:55: Attended and complied to SRPC Puspha:KPTCL: 02/08/2024 22:40:45: Attended. Breaker replaced, AR is put back to service. Double bus operation is restored at Shimoga. | Complied | Complied
115/VI/1 | 400 kV GUTTUR - HIRIYUR 1 | 01-01-2024 17:35 | DR Time Sync At Guttur | KPTCL to replace the faulty cable. | KPTCL | Puspha:KPTCL: 05/03/2024 10:48:30: Identification and replacement of all suspected cables will be taken up by taking M/s Kalkitech support. The observation is yet to be attended Puspha:KPTCL: 17/02/2025 22:39:58: Attended and complied | Complied | Complied
115/VI/6 | 220KV AMBEWADI-XELDOM | 12-01-2024 15:22 | DR Time sync at AMBEWADI | As recommended in 114th PCSC meeting, KPTCL to provide GPS equipment at Ambewadi sta-tion. | KPTCL | Puspha:KPTCL: 09/05/2024 15:15:37: The GPS time synchronising equipment has been received after repairs at OEM factory at Chennai. Visit of M/s GE engineer for restoring time synchronisation of Relays is scheduled during 4th Week of May 2024. Puspha:KPTCL: 02/08/2024 22:39:00: Attended, GPS is put back to service on 29.05.2024 after repairs Puspha:KPTCL: 01/12/2024 23:48:00: Attended Puspha:KPTCL: 17/02/2025 17:08:27: Problem with GPS time sync equipment is attended and complied | Complied | Complied
116/I/1 | Complete outage of 220kV/110kV Ranebennur SS, 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and Tripping of 220kV Bus-1 of 400kV/220kV Guttur SS and 220kV Bus-1 of 220kV/66kV Honnali SS of KPTCL | 13-01-2024 16:14 | During the antecedent conditions, the tripping of the 220kV Guttur bus coupler led to the 220kV buses operating in a split condition. 220kV Ranebennur Shiralkoppa was under outage. 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and 220kV Bus-1 of 220kV/66kV Honnali SS were being radially fed through 220kV Bus-1 of 400kV/220kV Guttur SS. At 16:14hrs, an overload occurred in the 400kV/220kV Guttur ICT-1, triggering the corresponding SPS and causing the 220kV Guttur Ranebennur line to trip. Given that the 400kV/220kV Guttur ICT-1 is linked to 220kV Bus-1 220kV Guttur Ranebennur line is 220kV Bus-2, the line trip did not impact the loading of the 400kV/220kV Guttur ICT-1. Subsequently, the 400kV/220kV Guttur ICT-1 tripped due to overload, resulting in a loss of power supply to 220kV Guttur Bus-1 Which inturn led complete outage of 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and Partial outage of 220kV/66kV Honnali SS. The tripping of the 220kV Guttur Ranebennur line led to a complete outage at the 220kV/110kV Ranebennur SS. | KPTCL to ensure SOP to be followed while carrying out testing / Maintenance works. | KPTCL | Puspha:KPTCL: 02/04/2024 21:26:11: Clear Instructions have been given to follow SOP while carrying out works in live condition | Complied | Pending
116/I/1 | Complete outage of 220kV/110kV Ranebennur SS, 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and Tripping of 220kV Bus-1 of 400kV/220kV Guttur SS and 220kV Bus-1 of 220kV/66kV Honnali SS of KPTCL | 13-01-2024 16:14 | During the antecedent conditions, the tripping of the 220kV Guttur bus coupler led to the 220kV buses operating in a split condition. 220kV Ranebennur Shiralkoppa was under outage. 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and 220kV Bus-1 of 220kV/66kV Honnali SS were being radially fed through 220kV Bus-1 of 400kV/220kV Guttur SS. At 16:14hrs, an overload occurred in the 400kV/220kV Guttur ICT-1, triggering the corresponding SPS and causing the 220kV Guttur Ranebennur line to trip. Given that the 400kV/220kV Guttur ICT-1 is linked to 220kV Bus-1 220kV Guttur Ranebennur line is 220kV Bus-2, the line trip did not impact the loading of the 400kV/220kV Guttur ICT-1. Subsequently, the 400kV/220kV Guttur ICT-1 tripped due to overload, resulting in a loss of power supply to 220kV Guttur Bus-1 Which inturn led complete outage of 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and Partial outage of 220kV/66kV Honnali SS. The tripping of the 220kV Guttur Ranebennur line led to a complete outage at the 220kV/110kV Ranebennur SS. | KPTCL to explore possibility of implementing SPS with load relief rather than feeder tripping. | KPTCL |  | Pending | Pending
116/I/1 | Complete outage of 220kV/110kV Ranebennur SS, 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and Tripping of 220kV Bus-1 of 400kV/220kV Guttur SS and 220kV Bus-1 of 220kV/66kV Honnali SS of KPTCL | 13-01-2024 16:14 | During the antecedent conditions, the tripping of the 220kV Guttur bus coupler led to the 220kV buses operating in a split condition. 220kV Ranebennur Shiralkoppa was under outage. 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and 220kV Bus-1 of 220kV/66kV Honnali SS were being radially fed through 220kV Bus-1 of 400kV/220kV Guttur SS. At 16:14hrs, an overload occurred in the 400kV/220kV Guttur ICT-1, triggering the corresponding SPS and causing the 220kV Guttur Ranebennur line to trip. Given that the 400kV/220kV Guttur ICT-1 is linked to 220kV Bus-1 220kV Guttur Ranebennur line is 220kV Bus-2, the line trip did not impact the loading of the 400kV/220kV Guttur ICT-1. Subsequently, the 400kV/220kV Guttur ICT-1 tripped due to overload, resulting in a loss of power supply to 220kV Guttur Bus-1 Which inturn led complete outage of 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and Partial outage of 220kV/66kV Honnali SS. The tripping of the 220kV Guttur Ranebennur line led to a complete outage at the 220kV/110kV Ranebennur SS. | KPTCL to revert back on increasing the ICT load set points. | KPTCL | Puspha:KPTCL: 02/04/2024 21:29:28: ICD load set points are reviewed and revised for Talaguppa, Guttur ICTs as per SRPC/SRLDC directions. A report in this regard will be submitted . | Complied | Pending
116/I/8 | Complete outage of 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and Tripping of 220kV Bus-1 of 220kV/66kV Honnali SS of KPTCL | 21-01-2024 09:05 | During the antecedent conditions 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and 220kV Bus-1 of 220kV/66kV Honnali SS were being radially fed through 400kV/220kV Guttur SS through 220kV Guttur-Davanagere-1,2 and 3 lines of which line 3 was under forced outage. 220kV Guttur Davanagere Line-3 tripped on R-N fault at 04:56 hrs. | KPTCL to address the time synchronisation issues at Guttur end. | KPTCL | Puspha:KPTCL: 01/12/2024 23:48:00: Attended on 22.11.2024 Puspha:KPTCL: 17/02/2025 17:09:03: Attended on 22.11.2024 | Complied | Pending
116/I/8 | Complete outage of 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and Tripping of 220kV Bus-1 of 220kV/66kV Honnali SS of KPTCL | 21-01-2024 09:05 | During the antecedent conditions 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and 220kV Bus-1 of 220kV/66kV Honnali SS were being radially fed through 400kV/220kV Guttur SS through 220kV Guttur-Davanagere-1,2 and 3 lines of which line 3 was under forced outage. 220kV Guttur Davanagere Line-3 tripped on R-N fault at 04:56 hrs. | KPTCL to ensure over load settings should not be less than 120% as recommended in CEA planning criteria. | KPTCL |  | Pending | Pending
116/I/8 | Complete outage of 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and Tripping of 220kV Bus-1 of 220kV/66kV Honnali SS of KPTCL | 21-01-2024 09:05 | During the antecedent conditions 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and 220kV Bus-1 of 220kV/66kV Honnali SS were being radially fed through 400kV/220kV Guttur SS through 220kV Guttur-Davanagere-1,2 and 3 lines of which line 3 was under forced outage. 220kV Guttur Davanagere Line-3 tripped on R-N fault at 04:56 hrs. | KPTCL to investigate non-operation of A/R in 220kV Guttur-Davangere line-3 and directionality issues at Davanagere end. | KPTCL | Puspha:KPTCL: 02/04/2024 21:44:38: Attended . AR scheme is working fine for all the three lines . OVer load settings and logics are reviewed at both the ends. | Complied | Pending
116/I/9 | Complete outage of 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and Tripping of 220kV Bus-1 of 220kV/66kV Honnali SS of KPTCL | 21-01-2024 13:26 | During the antecedent conditions 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and 220kV Bus-1 of 220kV/66kV Honnali SS were being radially fed through 400kV/220kV Guttur SS through 220kV Guttur-Davanagere-1,2 and 3 lines of which line-2 was under forced outage. Subsequently, 220kV Guttur Davanagere Line-1 tripped on Y-N fault. At Guttur end zone-1 protection operated and the 3ph line tripped. A/R did not operate at Guttur end. At Davanagere end the fault was sensed in zone-1 A/R operated and the line tripped on persistent fault. From PMU plot also it can be inferred that A/R operated and the line tripped on persistent fault. During the AR attempt of 220kV Guttur-Davanagere-1 line at Davanagere end, 220kV Guttur Davanagere Line-3 tripped at both ends on OC trip (Iy-4.4kA). Tripping of both lines led to complete outage of 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and Tripping of 220kV Bus-1 of 220kV/66kV Honnali SS of KPTCL. | KPTCL to address the time synchronisation issues at Guttur end. | KPTCL | Puspha:KPTCL: 01/12/2024 23:48:00: Attended on 22.11.2024 Puspha:KPTCL: 17/02/2025 17:09:41: Attended on 22.11.2024 and complied | Complied | Complied
116/I/9 | Complete outage of 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and Tripping of 220kV Bus-1 of 220kV/66kV Honnali SS of KPTCL | 21-01-2024 13:26 | During the antecedent conditions 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and 220kV Bus-1 of 220kV/66kV Honnali SS were being radially fed through 400kV/220kV Guttur SS through 220kV Guttur-Davanagere-1,2 and 3 lines of which line-2 was under forced outage. Subsequently, 220kV Guttur Davanagere Line-1 tripped on Y-N fault. At Guttur end zone-1 protection operated and the 3ph line tripped. A/R did not operate at Guttur end. At Davanagere end the fault was sensed in zone-1 A/R operated and the line tripped on persistent fault. From PMU plot also it can be inferred that A/R operated and the line tripped on persistent fault. During the AR attempt of 220kV Guttur-Davanagere-1 line at Davanagere end, 220kV Guttur Davanagere Line-3 tripped at both ends on OC trip (Iy-4.4kA). Tripping of both lines led to complete outage of 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and Tripping of 220kV Bus-1 of 220kV/66kV Honnali SS of KPTCL. | KPTCL to check the A/R operation in 220kV Guttur Davanagere Line-1 at Guttur end. | KPTCL | Puspha:KPTCL: 02/04/2024 21:39:30: AR Scheme is tested at both the ends and found to be working satisfactory. During line trripping occurred in March 2024 the lines have reclosed successfully. AR scheme is in service for all the three lines between Guttur and Davanagere and working satisfactory | Complied | Complied
116/I/9 | Complete outage of 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and Tripping of 220kV Bus-1 of 220kV/66kV Honnali SS of KPTCL | 21-01-2024 13:26 | During the antecedent conditions 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and 220kV Bus-1 of 220kV/66kV Honnali SS were being radially fed through 400kV/220kV Guttur SS through 220kV Guttur-Davanagere-1,2 and 3 lines of which line-2 was under forced outage. Subsequently, 220kV Guttur Davanagere Line-1 tripped on Y-N fault. At Guttur end zone-1 protection operated and the 3ph line tripped. A/R did not operate at Guttur end. At Davanagere end the fault was sensed in zone-1 A/R operated and the line tripped on persistent fault. From PMU plot also it can be inferred that A/R operated and the line tripped on persistent fault. During the AR attempt of 220kV Guttur-Davanagere-1 line at Davanagere end, 220kV Guttur Davanagere Line-3 tripped at both ends on OC trip (Iy-4.4kA). Tripping of both lines led to complete outage of 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and Tripping of 220kV Bus-1 of 220kV/66kV Honnali SS of KPTCL. | KPTCL to check the directionality of over current relay at Davanagere end and inform to SRPC & SRLDC. | KPTCL | Puspha:KPTCL: 02/04/2024 21:41:32: Presently at Davanagere end non directional current element is used .Presently SPS is provided for line over load ing conditions. Over load settings at Davanagere are reviewed. | Complied | Complied
116/I/9 | Complete outage of 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and Tripping of 220kV Bus-1 of 220kV/66kV Honnali SS of KPTCL | 21-01-2024 13:26 | During the antecedent conditions 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and 220kV Bus-1 of 220kV/66kV Honnali SS were being radially fed through 400kV/220kV Guttur SS through 220kV Guttur-Davanagere-1,2 and 3 lines of which line-2 was under forced outage. Subsequently, 220kV Guttur Davanagere Line-1 tripped on Y-N fault. At Guttur end zone-1 protection operated and the 3ph line tripped. A/R did not operate at Guttur end. At Davanagere end the fault was sensed in zone-1 A/R operated and the line tripped on persistent fault. From PMU plot also it can be inferred that A/R operated and the line tripped on persistent fault. During the AR attempt of 220kV Guttur-Davanagere-1 line at Davanagere end, 220kV Guttur Davanagere Line-3 tripped at both ends on OC trip (Iy-4.4kA). Tripping of both lines led to complete outage of 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and Tripping of 220kV Bus-1 of 220kV/66kV Honnali SS of KPTCL. | KPTCL to review the Overcurrent settings of Guttur and Davanagere ends. | KPTCL | Puspha:KPTCL: 02/04/2024 21:42:34: Over current settings are reviewed both at Guttur and Davanagere ends. Issue with over load logic have been attended at both ends. | Complied | Complied
116/I/11 | Complete Outage of 220kV/110kV Ghataprabha SS of KPTCL | 28-01-2024 10:13 | As per the information received from KPTCL, the incident at the 220/110kV Ghataprabha Substation occurred during the wiring work for integrating a new 220kV South Western Railway feeder bay into the Busbar protection scheme (CSC-150), which was being carried out by an external agency at the station while bus bar was in disabled condition. Due to a manual error during this process, the bus bar trip signal became high due to suspected DC positive extension trip to the Bar Bar trip, leading to tripping of both the buses. As a consequence, all elements connected to both buses tripped, resulting in a complete outage of the 220kV Ghataprabha substation. From the PMU plot, no fault was observed during the event. No DR and EL uploaded/available for analysis and ascertaining the bus bar operation as the same was disabled during the instance. | KPTCL to ensure strict compliance of SOP while carrying out Testing / Maintenance activities. | KPTCL | Puspha:KPTCL: 09/05/2024 15:20:42: Instructions have been given to the concerned field officers for strict compliance of SOP Puspha:KPTCL: 02/08/2024 22:35:52: Already communicated and complied to SRPC, Request to close the recommendation by SRPC | Pending | Pending
116/I/13 | Complete outage of 220kV Kadur, Arasikere, Bettedevarakere, Shiralkoppa and tripping of Bus-2 at Honnali, KB Cross and 400kV Bus-1 and Bus-2 at Talaguppa of KPTCL | 31-01-2024 14:40 | In the antecedent conditions, 220kV Kadur, Arasikere, Bettedevarakere, Shiralkoppa and Bus-2 at Honnali, KB Cross were radially connected to 220kV Shimoga SS. 220kV Arasikere-Nittur, 220kV Kadur-Dobaspet, 220kV Sirsi-Sharavathy D/C, 220kV Balligavi (Shiralkoppa)-Ranebennur, 220kV Shimoga-Chikkamangalur were under out condition. Effectively the section highlighted in yellow is being fed from 220kV Shimoga- Anthrasanahalli, 220kV Shimoga-Hassan and 400/220kV ICTs at Talaguppa. | KPTCL to test Main-2 Siemens relay at Anthrasanahalli end. | KPTCL | Puspha:KPTCL: 02/08/2024 22:34:19: AR Scheme is checked both in M1 and M2 relays. Problem in M2 relay scheme w.r.t AR was rectified Puspha:KPTCL: 01/12/2024 23:48:00: The relay was tested and the AR logic issue was rectified. Puspha:KPTCL: 17/02/2025 17:10:41: Main-2 relay was ested and issue with logic is rectified . The issue is Attended and complied Puspha:KPTCL: 17/02/2025 17:10:52: Main-2 relay was tested and issue with logic is rectified . The issue is Attended and complied | Complied | Complied
116/III/2 | 400kV DHONI MUNIRABAD | 03-02-2024 22:09 | Line tripped at Munirabad end only on the operation of PSB in REL670 relay | KPTCL/PGCIL SR-I to replace the B-POLE auxiliary contact of Main CB. | KPTCL | Puspha:KPTCL: 02/04/2024 21:37:16: As informed by Power grid incident occurred due voltage variation. Over voltage was sensed. In Munirabad 01 numbers of CVTs of Doni line failed and other was recommended for repplacement. Hence two numbers of 400kV CVTs are arranged by KPTCL.. Replacement of CVTs willl be done within a weeks time Puspha:KPTCL: 09/05/2024 15:23:13: Tripping of the line was due tp voltage circuit problems. CVTs were not available for R&B phase of Doni line has been replaced by new CVTs and commissioned on 24.04.2024. Puspha:KPTCL: 02/08/2024 22:33:01: Attended, it was CVT issue. New CVTs have been provided by KPTCL and the issue is set right. Puspha:KPTCL: 01/12/2024 23:48:00: Attended and complied Puspha:KPTCL: 17/02/2025 17:11:26: Attended and complied | Complied | Complied
116/III/13 | 400 kV GUTTUR - HIRIYUR 2 | 19-02-2024 14:03 | The line tripped due to an oversight logic link in the Y and B phase logics leading to the trip extended from the Y and B 1-phase trip relay, consequently resulting in a trip on the PDR. | KPTCL to furnish the detailed report on this event. | KPTCL | Puspha:KPTCL: 02/04/2024 21:32:39: The incident occurred while modifying the PSL logic for ZOne-1 extension setting which was provided earlier Puspha:KPTCL: 17/02/2025 22:41:07: Tripping occurred while modifying the logic,, issue is rectified | Complied | Complied
116/III/6 | 400KV-KOLAR AC - MYLASANDRA- 1 | 07-02-2024 17:20 | B-N fault in the line. Multiple AR attempts at Mylasandra needs review | KPTCL to furnish the detailed report after testing of A/R operation to SRPC. | KPTCL | Puspha:KPTCL: 01/12/2024 23:48:00: AR scheme was tested by availing line shut down and found to be working satisfactory | Complied | Complied
117/I/1 | Complete outage of 220kV Kadur, Arasikere, Bet-tedevarakere, Shiralkoppa and tripping of Bus-2 at Honnali, KB Cross and 400kV Bus-1 and Bus-2 at Talaguppa of KPTCL | 22-02-2024 14:18 | In the antecedent conditions, 220kV Kadur, Arasikere, Bettedevarakere, Shiralkoppa and Bus-2 at Honnali, KB Cross were radially connected to 220kV Shimoga SS. 220kV Arasikere-Nittur, 220kV Kadur-Do-baspet, 220kV Sirsi-Sharavathy D/C, 220kV Balligavi (Shiralkoppa)-Ranebennur, 220kV Shimoga-Chikkamangalur were under out condition. Effectively the section highlighted in yellow is being fed from 220kV Shimoga-Anthrasanahalli, 220kV Shimoga-Hassan and 400/220kV ICTs at Talaguppa. | KPTCL to furnish the Shimoga SPS to OCC forum for approval. | KPTCL | Puspha:KPTCL: 17/02/2025 22:45:24: Attended and complied. | Complied | Complied
117/I/1 | Complete outage of 220kV Kadur, Arasikere, Bet-tedevarakere, Shiralkoppa and tripping of Bus-2 at Honnali, KB Cross and 400kV Bus-1 and Bus-2 at Talaguppa of KPTCL | 22-02-2024 14:18 | In the antecedent conditions, 220kV Kadur, Arasikere, Bettedevarakere, Shiralkoppa and Bus-2 at Honnali, KB Cross were radially connected to 220kV Shimoga SS. 220kV Arasikere-Nittur, 220kV Kadur-Do-baspet, 220kV Sirsi-Sharavathy D/C, 220kV Balligavi (Shiralkoppa)-Ranebennur, 220kV Shimoga-Chikkamangalur were under out condition. Effectively the section highlighted in yellow is being fed from 220kV Shimoga-Anthrasanahalli, 220kV Shimoga-Hassan and 400/220kV ICTs at Talaguppa. | KPTCL to maintain RoW of Transmission lines in and around Shimoga area. | KPTCL | Puspha:KPTCL: 09/05/2024 15:26:50: RoW issues due to growth of vegetation is attended by TLM wing in Shimoga-Antharasanahally line. Nelamangala Talaguppa 400kV line. Puspha:KPTCL: 17/02/2025 22:45:24: The matter is referred to the Transmission Line maintenance wing for strict compliance. | Complied | Complied
117/I/1 | Complete outage of 220kV Kadur, Arasikere, Bet-tedevarakere, Shiralkoppa and tripping of Bus-2 at Honnali, KB Cross and 400kV Bus-1 and Bus-2 at Talaguppa of KPTCL | 22-02-2024 14:18 | In the antecedent conditions, 220kV Kadur, Arasikere, Bettedevarakere, Shiralkoppa and Bus-2 at Honnali, KB Cross were radially connected to 220kV Shimoga SS. 220kV Arasikere-Nittur, 220kV Kadur-Do-baspet, 220kV Sirsi-Sharavathy D/C, 220kV Balligavi (Shiralkoppa)-Ranebennur, 220kV Shimoga-Chikkamangalur were under out condition. Effectively the section highlighted in yellow is being fed from 220kV Shimoga-Anthrasanahalli, 220kV Shimoga-Hassan and 400/220kV ICTs at Talaguppa. | KPTCL to remove the temporary arrangement (tapping) on 220 kV Shimoga-Anthrasanahalli line for connecting to Bettedevarekere station and make permanent system by LILOing. | KPTCL | Puspha:KPTCL: 09/05/2024 15:27:56: Presently, Bettadavarekere LIS is owned and maintained by VJNL. There is no continous loading. SRPC recommendation regarding operating Bettadavarekere in LILO mode is taken up with CEE,TZ, Hassan. Puspha:KPTCL: 17/02/2025 22:54:52: | Complied | Complied
117/I/1 | Complete outage of 220kV Kadur, Arasikere, Bet-tedevarakere, Shiralkoppa and tripping of Bus-2 at Honnali, KB Cross and 400kV Bus-1 and Bus-2 at Talaguppa of KPTCL | 22-02-2024 14:18 | In the antecedent conditions, 220kV Kadur, Arasikere, Bettedevarakere, Shiralkoppa and Bus-2 at Honnali, KB Cross were radially connected to 220kV Shimoga SS. 220kV Arasikere-Nittur, 220kV Kadur-Do-baspet, 220kV Sirsi-Sharavathy D/C, 220kV Balligavi (Shiralkoppa)-Ranebennur, 220kV Shimoga-Chikkamangalur were under out condition. Effectively the section highlighted in yellow is being fed from 220kV Shimoga-Anthrasanahalli, 220kV Shimoga-Hassan and 400/220kV ICTs at Talaguppa. | KPTCL to review the overcurrent settings of ICT at Talaguppa and requested to adopt as per SR Protection Protocol. | KPTCL | Puspha:KPTCL: 09/05/2024 15:25:35: ICT settings at Talaguppa are reviewed and complied to SRPC/SRLDC. Puspha:KPTCL: 02/08/2024 22:33:01: Att | Complied | Complied
117/I/3 | Complete outage of 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and Tripping of 220kV Bus-1 of 220kV/66kV Honnali SS of KPTCL | 23-02-2024 14:10 | During the antecedent conditions 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS, and 220kV Bus-1 of 220kV/66kV Honnali SS were being radially fed through 400kV/220kV Guttur SS through 220kV Guttur-Davanagere-1,2 and 3 lines of which line-2 was under forced outage from 22-02-2024 15:17hrs. The triggering incident is the Y-N fault in 220kV Guttur Davanagere Line-1. At Davanagere end, the fault was sensed in zone-1. Auto reclo-sure operated and the line tripped on persistent fault. At Guttur end, the fault was sensed Z1 and AR did not get operated and 3ph tripped. With the tripping of 220kV Guttur-Davanagere-1 and non-availability 220kV Guttur-Davanagere-2, 220kV Guttur Davanagere Line-3 got over loaded. Subse-quently, 220kV Guttur Davanagere Line-3 tripped At the Davanagere end on over current protection. Tripping of 220kV Guttur-Davanagere-1&3 leadto the complete outage of 220kV/66kV Davanagere SS, 220kV/66kV Hosadurga SS, 220kV/66kV Benkikere SS and Tripping of 220kV Bus-1 of 220kV/66kV Honnali SS of KPTCL. | 1.KPTCL to maintain the RoW in and around Guttur- Davangere stretch and monitor once in 15 days. 2.KPTCL to review the overcurrent settings at Davangere end. 3.KPTCL to furnish the Davangere SPS logic to OCC forum for the approval. 4.Protection audit to be carried out at 400/220 kV Guttur and 220kV Davanagere substations by a team comprising of PGCIL SR-II, SRLDC and SRPC Secretariat. | KPTCL |  | Pending | Pending
117/III/1 | HVDC TALCHER - KOLAR POLE 1 AT KOLAR | 24-02-2024 07:16 | During B-N fault in 400kV Kolar-Hoody-2, AR did not operate in Hoody end. Talcher- Kolar Pole-1 got blocked during the fault and needs review. | KPTCL to check the A/R scheme at Hoody end. | KPTCL | Puspha:KPTCL: 09/05/2024 15:23:51: AR scheme will be tested by availing Line shut down. Line shut down to be approved in OCC Puspha:KPTCL: 02/08/2024 22:31:16: Attended. Recently during line shut down relay testing AR scheme testing etc conducted by Powergrid at Hoody S S Puspha:KPTCL: 17/02/2025 22:44:27: Attended, during OCC approved shut down scheme checked in presence of Powergrid officials | Complied | Complied
117/III/9 | Tripping of 400 kV Raichur Raichur_ PG 2 and 400/220 kV ICT-1 AT Raichur | 16-03-2024 16:49 | Y-N fault in 400kV RAICHUR - RAICHUR PG-2 line. At RTPS end AR opera tion started, however, LBB operated leading to a 3ph trip and DT send to the remote end and tripping of 400/220kV ICT-1 which is on the same dia | KPCL to modify the LBB initiation logic in the PSL and also check the same for all tie breakers. | KPCL | EE (E )/CEED:KPCL: 09/05/2024 12:37:32: The issue has been addressed to OEM & the same will be rectified during next shut down of lines after obtaining shut down clearance from OCC forum, SRPC. EE (E )/CEED:KPCL: 03/06/2024 15:08:13: The issue has been addressed to OEM & the same will be rectified during next shut down of lines after obtaining shut down clearance from OCC forum, SRPC. EE (E )/CEED:KPCL: 04/07/2024 14:19:19: The issue has been addressed to OEM & the same will be rectified during next shut down of lines after obtaining shut down clearance from OCC forum, SRPC. EE (E )/CEED:KPCL: 06/08/2024 16:55:57: The issue has been addressed to OEM & the same will be rectified during next shut down of lines after obtaining shut down clearance from OCC forum, SRPC EE (E )/CEED:KPCL: 06/11/2024 12:25:31: The issue has been addressed to OEM & the same will be rectified during next shut down of lines after obtaining shut down clearance from OCC forum, SRPC. EE (E )/CEED:KPCL: 02/12/2024 14:42:59: The issue has been addressed to OEM & the same will be rectified during next shut down of lines after obtaining shut down clearance from OCC forum, SRPC. EE (E )/CEED:KPCL: 02/01/2025 12:18:50: The issue has been addressed to OEM & the same will be rectified during next shut down of lines after obtaining shut down clearance from OCC forum, SRPC. EE (E ) EE (E )/CEED:KPCL: 06/02/2025 14:55:47: The issue has been addressed to OEM & the same will be rectified during next shut down of lines after obtaining shut down clearance. EE (E )/CEED:KPCL: 01/03/2025 14:29:11: Few elements have LBB retrip feature and remaining will be done during coming short shtdown for which Hard wiring is also required. For the lines will be completed by June-2025. For Units will be completed by Dec -2025 during OH works EE (E )/CEED:KPCL: 02/07/2025 10:47:08: Few elements have LBB retrip feature and remaining will be done during coming short shtdown for which Hard wiring is also required. the lines and units will be completed by Dec-2025.during OH works EE (E )/CEED:KPCL: 04/08/2025 10:31:39: The problem hass been rectified by modifying the LBB trip circuit, however the PSL will be modified by availing the shutdown and will be completed by DEC 2025. EE (E )/CEED:KPCL: 30/08/2025 14:55:02: The problem hass been rectified by modifying the LBB trip circuit, however the PSL will be modified by availing the shutdown and will be completed by DEC 2025. EE (E )/CEED:KPCL: 04/10/2025 11:43:15: The problem hass been rectified by modifying the LBB trip circuit, however the PSL will be modified by availing the shutdown and will be completed by DEC 2025. EE (E )/CEED:KPCL: 04/11/2025 10:04:03: The problem hass been rectified by modifying the LBB trip circuit, however the PSL will be modified by availing the shutdown and will be completed by DEC 2025 EE (E )/CEED:KPCL: 04/12/2025 16:42:28: The problem hass been rectified by modifying the LBB trip circuit, however the PSL will be modified by availing the shutdown and will be completed by DEC 2025 | Complied | Complied
118/I/1 | Complete Outage of 220kV/110kV/11kV Raichur KA SS of KPTCL 220kV Upper Jurala PH of TSGENCO | 29-03-2024 22:47 | - | KPTCL to check the CTs Healthiness of all CTs connected to power transformer. | KPTCL |  | Pending | Pending
118/I/1 | Complete Outage of 220kV/110kV/11kV Raichur KA SS of KPTCL 220kV Upper Jurala PH of TSGENCO | 29-03-2024 22:47 | - | KPTCL to resolve the time syn issues f 220/110kV PTR-1 at Raichur (KA). | KPTCL |  | Pending | Pending
118/I/1 | Complete Outage of 220kV/110kV/11kV Raichur KA SS of KPTCL 220kV Upper Jurala PH of TSGENCO | 29-03-2024 22:47 | - | KPTCL to review the non-availability issues of SCADA SOE of 220kV RTPS. | KPTCL |  | Pending | Pending
118/I/3 | Complete outage of 220kV Bettedaverekere LIS of KPTCL | 31-03-2024 11:36 | 220kV Bettedaverekere LIS is tapped from 220kV Shimoga Anthrasanahalli Line. The triggering incident was B-N fault in 220kV Shimoga Anthrasanahalli Line due to B-phase jumper cut in at Location No. 423. At both ends, the fault was sensed in zone-1. A/R operated and the line tripped on persistent fault. However, the same could not be verified due to non-submission of DR. Tripping of the line resulted in complete outage of 220kV Bettedaverekere LIS. | KPTCL to ensure downloading of DRs for the events and suitable instruction may be given to the field. | KPTCL |  | Pending | Pending
118/I/3 | Complete outage of 220kV Bettedaverekere LIS of KPTCL | 31-03-2024 11:36 | 220kV Bettedaverekere LIS is tapped from 220kV Shimoga Anthrasanahalli Line. The triggering incident was B-N fault in 220kV Shimoga Anthrasanahalli Line due to B-phase jumper cut in at Location No. 423. At both ends, the fault was sensed in zone-1. A/R operated and the line tripped on persistent fault. However, the same could not be verified due to non-submission of DR. Tripping of the line resulted in complete outage of 220kV Bettedaverekere LIS. | KPTCL to expedite the proper LILO arrangement (220kV Shimoga-Anthrasanahalli Line) for 220kV Bettedaverekere LIS. | KPTCL | Puspha:KPTCL: 17/02/2025 22:42:25: The matter is being persued with CEE, Operations Hassan Zone for taking over of the substation by VJNL and to overcome tap connection in main grid line. | Pending | Pending
118/I/4 | Tripping of 220kV Bus-1 220kV/110kV Kemar SS and Complete Outage of 220kV/110kV Kavoor SS and 220kV/110kV MSEZ SS of KPTCL | 06-04-2024 18:19 | At 18:19 hours, while charging 220kV/110kV Kemar Transformer-3, the 86HV relay was not in a reset condition. Consequently, the initiation signal to the HV LBB Relay (Alstom MCT model Static relay) persisted, resulting in a continuous presence of the signal. Due to a malfunction, the NC interlock contact of the 86HV relay (a manual reset component of Alstom MVAJ type) in the HV breaker closing circuit remained engaged, allowing the breaker to close even though the 86HV relay was not fully reset. However, only the Y&B poles closed, while the R-pole remained open. As a result of the transformer charging current, the LBB in the transformer activated, causing a trip signal to be sent to 220kV BUS-1 through the 96 Relays in the Bus bar Panel. While finding the reason for not closing R-pole of the breaker, it was discovered that the closing coil of the R-pole was faulty and was subsequently replaced. | KPTCL to expediate the procurement of numerical relay for differential protection of 100MVA Trafo-2. | KPTCL | Puspha:KPTCL: 02/02/2025 22:16:03: Attended Puspha:KPTCL: 06/02/2025 22:01:36: Attended and complied, requested to close the recommendations | Complied | Complied
118/I/4 | Tripping of 220kV Bus-1 220kV/110kV Kemar SS and Complete Outage of 220kV/110kV Kavoor SS and 220kV/110kV MSEZ SS of KPTCL | 06-04-2024 18:19 | At 18:19 hours, while charging 220kV/110kV Kemar Transformer-3, the 86HV relay was not in a reset condition. Consequently, the initiation signal to the HV LBB Relay (Alstom MCT model Static relay) persisted, resulting in a continuous presence of the signal. Due to a malfunction, the NC interlock contact of the 86HV relay (a manual reset component of Alstom MVAJ type) in the HV breaker closing circuit remained engaged, allowing the breaker to close even though the 86HV relay was not fully reset. However, only the Y&B poles closed, while the R-pole remained open. As a result of the transformer charging current, the LBB in the transformer activated, causing a trip signal to be sent to 220kV BUS-1 through the 96 Relays in the Bus bar Panel. While finding the reason for not closing R-pole of the breaker, it was discovered that the closing coil of the R-pole was faulty and was subsequently replaced. | SOP to be followed strictly. Interlock should be maintained for both the coils of 86 trip relay. | KPTCL | Puspha:KPTCL: 10/02/2025 09:42:37: Clear instructions are given to the shift operators. SOP is posted on the C&R panel. | Complied | Complied
118/I/1 | Complete Outage of 220kV/110kV/11kV Raichur KA SS of KPTCL 220kV Upper Jurala PH of TSGENCO | 29-03-2024 22:47 | The triggering incident is the failure of B phase 110kV CTs connected to HV side of 20MVA, 110/11kV RIMA Make, Power Transformer-6, which led to fire due to oil expel from CT | 1.KPTCL to check the CTs Healthiness of all CTs connected to power transformer. 2.KPTCL to resolve the time syn issues f 220/110kV PTR-1 at Raichur (KA). 3.KPTCL to review the non-availability issues of SCADA SOE of 220kV RTPS. | KPTCL |  | Pending | Pending
118/I/3 | Complete outage of 220kV Bettedaverekere LIS of KPTCL | 31-03-2024 11:36 | 220kV Bettedaverekere LIS is tapped from 220kV Shimoga Anthrasanahalli Line. The triggering incident was B-N fault in 220kV Shimoga Anthrasanahalli Line due to B-phase jumper cut in at Location No. 423. At both ends, the fault was sensed in zone-1. A/R operated and the line tripped on persistent fault. However, the same could not be verified due to non-submission of DR. Tripping of the line resulted in complete outage of 220kV Bettedaverekere LIS. | 1.KPTCL to expedite the proper LILO arrangement (220kV Shimoga-Anthrasanahalli Line) for 220kV Bettedaverekere LIS. 2.KPTCL to ensure downloading of DRs for the events and suitable instruction may be given to the field. | KPTCL | Puspha:KPTCL: 02/08/2024 22:27:27: The matter is reffered to CEE,TZ Hassan | Pending | Pending
118/I/4 | Tripping of 220kV Bus-1 220kV/110kV Kemar SS and Complete Outage of 220kV/110kV Kavoor SS and 220kV/110kV MSEZ SS of KPTCL | 06-04-2024 18:19 | At 18:19 hours, while charging 220kV/110kV Kemar Transformer-3, the 86HV relay was not in a reset condition. Consequently, the initiation signal to the HV LBB Relay (Alstom MCT model Static relay) persisted, resulting in a continuous presence of the signal. Due to a malfunction, the NC interlock contact of the 86HV relay (a manual reset component of Alstom MVAJ type) in the HV breaker closing circuit remained engaged, allowing the breaker to close even though the 86HV relay was not fully reset. However, only the Y&B poles closed, while the R-pole remained open. As a result of the transformer charging current, the LBB in the transformer activated, causing a trip signal to be sent to 220kV BUS-1 through the 96 Relays in the Bus bar Panel. While finding the reason for not closing R-pole of the breaker, it was discovered that the closing coil of the R-pole was faulty and was subsequently replaced. | 1.SOP to be followed strictly. Interlock should be maintained for both the coils of 86 trip relay. 2.KPTCL to expediate the procurement of numerical relay for differential protection of 100MVA Trafo-2. | KPTCL | Puspha:KPTCL: 02/08/2024 22:26:53: New Numerical Differential Relay GE make , P643 is commissioned | Complied | Complied
119/I/1 | Complete Outage of 220kV Nadhihal SS , 220kV/110kV Bijapur SS, 220kV/110kV Aheri SS, 220kV/110kV Indi SS of KPTCL | 22-04-2024 15:53 | The triggering incident is the initial R-N fault in 220kV Nandihal-Bijapur-1. The fault was sensed in Z1 at Bijapur end with a fault current of and since AR is disabled 3ph tripped. At Nandihal end, the fault was sensed in Z1 however the breaker failed to open and LBB operated. However, it was observed that the breakers did not open at Nandihal end but DT was sent to Kudgi end for all the 4 feeders. With the receipt of DT at Kudgi end all the feeders at Kudgi connected to Nandihal tripped. However, the fault was still being fed through 220kV Nandihal-BB Wadi-1&2, 220kV Nandihal-GM-Navar and 220kV Nandihal-Bijapur-2. After the tripping of 220kV Nandihal-Bijapur-1 at Bijapur end, 220kV Nandihal-Bijapur-1 at Nandihal end sensed the fault in Z1ext. The breakers were observed not to have opened. The fault after around 400ms developed into Z1 fault in 220kV Nandihal- Bijapur-2 at Bijapur and the line tripped at Bijapur end. However, the fault was being fed through BB Wadi lines and no breaker operation was observed Nandihal end. 220kV Nandihal-BB Wadi lines -1 and 2 tripped on over current protection operation after around 1.2 sec from the initial fault. This led to Complete Outage of 220kV Nadhihal Pooling Station, 220kV GM Navar SS, 220kV/110kV Bijapur SS, 220kV/110kV Indi SS, 220kV Vaishali and 220kV/110kV Aheri | KPTCL /M/s Siemens Gamesa to check the healthiness of all breakers at 220kV Nandhihal SS | KPTCL | Puspha:KPTCL: 01/12/2024 23:48:00: Attended. Bus Coupler Breaker issue was attended by M/s Siemns Gamesa Ltd | Complied | Pending
119/I/1 | Complete Outage of 220kV Nadhihal SS , 220kV/110kV Bijapur SS, 220kV/110kV Aheri SS, 220kV/110kV Indi SS of KPTCL | 22-04-2024 15:53 | The triggering incident is the initial R-N fault in 220kV Nandihal-Bijapur-1. The fault was sensed in Z1 at Bijapur end with a fault current of and since AR is disabled 3ph tripped. At Nandihal end, the fault was sensed in Z1 however the breaker failed to open and LBB operated. However, it was observed that the breakers did not open at Nandihal end but DT was sent to Kudgi end for all the 4 feeders. With the receipt of DT at Kudgi end all the feeders at Kudgi connected to Nandihal tripped. However, the fault was still being fed through 220kV Nandihal-BB Wadi-1&2, 220kV Nandihal-GM-Navar and 220kV Nandihal-Bijapur-2. After the tripping of 220kV Nandihal-Bijapur-1 at Bijapur end, 220kV Nandihal-Bijapur-1 at Nandihal end sensed the fault in Z1ext. The breakers were observed not to have opened. The fault after around 400ms developed into Z1 fault in 220kV Nandihal- Bijapur-2 at Bijapur and the line tripped at Bijapur end. However, the fault was being fed through BB Wadi lines and no breaker operation was observed Nandihal end. 220kV Nandihal-BB Wadi lines -1 and 2 tripped on over current protection operation after around 1.2 sec from the initial fault. This led to Complete Outage of 220kV Nadhihal Pooling Station, 220kV GM Navar SS, 220kV/110kV Bijapur SS, 220kV/110kV Indi SS, 220kV Vaishali and 220kV/110kV Aheri | KPTCL /M/s Siemens Gamesa to furnish a detailed report after analyzing the event covering all the aspects/points as raised above by PCSC | KPTCL | Puspha:KPTCL: 01/12/2024 23:48:00: Action taken report furnished to SRPC by M/s Siemens Gamesa, SRPC is requested to close the recommendations | Complied | Pending
119/I/1 | Complete Outage of 220kV Nadhihal SS , 220kV/110kV Bijapur SS, 220kV/110kV Aheri SS, 220kV/110kV Indi SS of KPTCL | 22-04-2024 15:53 | The triggering incident is the initial R-N fault in 220kV Nandihal-Bijapur-1. The fault was sensed in Z1 at Bijapur end with a fault current of and since AR is disabled 3ph tripped. At Nandihal end, the fault was sensed in Z1 however the breaker failed to open and LBB operated. However, it was observed that the breakers did not open at Nandihal end but DT was sent to Kudgi end for all the 4 feeders. With the receipt of DT at Kudgi end all the feeders at Kudgi connected to Nandihal tripped. However, the fault was still being fed through 220kV Nandihal-BB Wadi-1&2, 220kV Nandihal-GM-Navar and 220kV Nandihal-Bijapur-2. After the tripping of 220kV Nandihal-Bijapur-1 at Bijapur end, 220kV Nandihal-Bijapur-1 at Nandihal end sensed the fault in Z1ext. The breakers were observed not to have opened. The fault after around 400ms developed into Z1 fault in 220kV Nandihal- Bijapur-2 at Bijapur and the line tripped at Bijapur end. However, the fault was being fed through BB Wadi lines and no breaker operation was observed Nandihal end. 220kV Nandihal-BB Wadi lines -1 and 2 tripped on over current protection operation after around 1.2 sec from the initial fault. This led to Complete Outage of 220kV Nadhihal Pooling Station, 220kV GM Navar SS, 220kV/110kV Bijapur SS, 220kV/110kV Indi SS, 220kV Vaishali and 220kV/110kV Aheri | Time synch issues to be rectified 220Kv Nandhihal SS, 220kV Bagewadi & 220kVBijapur SS | KPTCL |  | Pending | Pending
119/I/3 | Complete Outage of 220kV/66kV Chintamani SS and 220kV/66kV Srinivaspura SS of KPTCL | 30-04-2024 12:31 | As per the reports submitted, the triggering incident was R-N fault in 220kV Kolar Chintamani Line2 at 12:21 Hrs. At Kolar end fault was sensed in Zone-2 carrier aided with a fault current of 5.2kA and at a distance of 19km and since AR was disabled 3ph tripped. At Chintamani end fault was sensed only by one main (Main 1) in Zone 1 with a fault current of 2.3kA and since AR was disabled 3ph tripped. With the tripping of 220kV Kolar Chintamani Line-2, the 220kV Chintamani and | Healthiness of PLCC communication between Kolar PG & Chintamani (KAR) to be checked | KPTCL | Puspha:KPTCL: 17/02/2025 22:43:37: Attended, PLCC link between Kolar PG-Chintamani is healthy | Complied | Complied
119/I/3 | Complete Outage of 220kV/66kV Chintamani SS and 220kV/66kV Srinivaspura SS of KPTCL | 30-04-2024 12:31 | As per the reports submitted, the triggering incident was R-N fault in 220kV Kolar Chintamani Line2 at 12:21 Hrs. At Kolar end fault was sensed in Zone-2 carrier aided with a fault current of 5.2kA and at a distance of 19km and since AR was disabled 3ph tripped. At Chintamani end fault was sensed only by one main (Main 1) in Zone 1 with a fault current of 2.3kA and since AR was disabled 3ph tripped. With the tripping of 220kV Kolar Chintamani Line-2, the 220kV Chintamani and | KPTCL to provide another channel to enable Auto reclosure for Kolar-Chintamani lines at both ends | KPTCL | Puspha:KPTCL: 02/08/2024 22:25:50: OPGW laying completed, end equipments are supplied to both the ends. Work is under progress Puspha:KPTCL: 17/02/2025 22:43:37: OPGW link is established, AR will be enabled in coordination with PGCIL | Complied | Complied
119/I/10 | Complete Outage of 220kV/110kV NRS SS of KPTCL | 10-05-2024 23:32 | As per the reports submitted, the triggering incident is the tripping of all the elements connected to 220kV NRS station due to the maloperation of BBP at 220kV NRS station. | KPTCL to rectify the time sync issues at 220kV NRS SS | KPTCL | Puspha:KPTCL: 02/08/2024 22:25:50: Attended | Complied | Complied
119/I/10 | Complete Outage of 220kV/110kV NRS SS of KPTCL | 10-05-2024 23:32 | As per the reports submitted, the triggering incident is the tripping of all the elements connected to 220kV NRS station due to the maloperation of BBP at 220kV NRS station. | KPTCL to upgrade the firmware as recommended by OEM and carry out bus bar stability check. | KPTCL | Puspha:KPTCL: 02/08/2024 22:25:50: Aattended Puspha:KPTCL: 01/12/2024 23:48:00: Firmware upgradation of BBP is done at NRS and complied. SRPC is requested to close this recommendation as the same has been attended by KPTCL | Complied | Complied
119/VI/12 | 400kV-Guttur-BTPS-1 | 13-05-2024 00:26 | 400kV Guttur BTPS line tripped on DPR Zone-1 R & B phase 81.38Kms Il1-5.09kA & Il3-5.08kA due to 2-ph fault 3ph trip operated. | KPTCL to furnish the compliance report. | KPTCL |  | Pending | Pending
119/VI/13 | 400kV Raichur - Raichur PG 2 | 13-05-2024 02:47 | On 13.05.2024 at 02:47Hrs Raichur-PG2 line tripped on B-Ph Differential protection, ZCom trip. | KPCL to furnish the remedial action taken. | KPCL | EE (E )/CEED:KPCL: 03/07/2024 17:02:40: Time synchronization of Raichur PG-2 distance relays have been done and rectified by PGCIL. in coordination with RTPS. Requested to close the point | Complied | Complied
120/I/4 | Complete Outage of 220kV/66kV Manyata SS,220kV/66kV HBR Layout SS 220kV Bus-3&4 of 220kV Yelahanka SS and 220kV Bus-1 of 220kV/66kV Shakarinagar SS of KPTCL | 24-05-2024 16:50 | As per the reports submitted, the triggering incident was B-N fault in 220kV Shakar Nagar Yelahanka Line-1. At Shakar Nagar end, the fault was sensed in zone-1 and the line tripped. At the same time, 220kV Shakar Nagar Peenya line tripped only at Peenya end on SOTF protection. Subsequently, for the same fault 220kV Manyata ITI line tripped at ITI end on High set earth fault protection (IN>4). At Yelahanka end, Bus couplers of Bus section-3 and 4 tripped on zero sequence over current protection. This led to loss of power supply to all elements connected to 220kV Yelahanka Bus Section-3 and 4. (220kV Yelahanka Yelahanka_PG Line-1, 220kV Yelahanka Shakarnagar Line-1&2). These trippings led to complete outage of 220kV/66kV Manyata SS, 220kV/66kV HBR Layout SS 220kV Bus-3 & 4 of 220kV Yelahanka SS and 220kV Bus-1 of 220kV/66kV Shakarinagar | KPTCL to ensure proper LILO arrangement for all 66kV and above networks in Karnataka network including the LILO arrangement for 220kV Manyata -Hebbal line. | KPTCL |  | Pending | Pending
120/I/4 | Complete Outage of 220kV/66kV Manyata SS,220kV/66kV HBR Layout SS 220kV Bus-3&4 of 220kV Yelahanka SS and 220kV Bus-1 of 220kV/66kV Shakarinagar SS of KPTCL | 24-05-2024 16:50 | As per the reports submitted, the triggering incident was B-N fault in 220kV Shakar Nagar Yelahanka Line-1. At Shakar Nagar end, the fault was sensed in zone-1 and the line tripped. At the same time, 220kV Shakar Nagar Peenya line tripped only at Peenya end on SOTF protection. Subsequently, for the same fault 220kV Manyata ITI line tripped at ITI end on High set earth fault protection (IN>4). At Yelahanka end, Bus couplers of Bus section-3 and 4 tripped on zero sequence over current protection. This led to loss of power supply to all elements connected to 220kV Yelahanka Bus Section-3 and 4. (220kV Yelahanka Yelahanka_PG Line-1, 220kV Yelahanka Shakarnagar Line-1&2). These trippings led to complete outage of 220kV/66kV Manyata SS, 220kV/66kV HBR Layout SS 220kV Bus-3 & 4 of 220kV Yelahanka SS and 220kV Bus-1 of 220kV/66kV Shakarinagar | KPTCL to implement LDP at Puttenhalli for 220kV Sahakarnagar-Puttenhalli l4ine | KPTCL | Puspha:KPTCL: 17/02/2025 22:47:48: will be attended | Pending | Pending
120/I/4 | Complete Outage of 220kV/66kV Manyata SS,220kV/66kV HBR Layout SS 220kV Bus-3&4 of 220kV Yelahanka SS and 220kV Bus-1 of 220kV/66kV Shakarinagar SS of KPTCL | 24-05-2024 16:50 | As per the reports submitted, the triggering incident was B-N fault in 220kV Shakar Nagar Yelahanka Line-1. At Shakar Nagar end, the fault was sensed in zone-1 and the line tripped. At the same time, 220kV Shakar Nagar Peenya line tripped only at Peenya end on SOTF protection. Subsequently, for the same fault 220kV Manyata ITI line tripped at ITI end on High set earth fault protection (IN>4). At Yelahanka end, Bus couplers of Bus section-3 and 4 tripped on zero sequence over current protection. This led to loss of power supply to all elements connected to 220kV Yelahanka Bus Section-3 and 4. (220kV Yelahanka Yelahanka_PG Line-1, 220kV Yelahanka Shakarnagar Line-1&2). These trippings led to complete outage of 220kV/66kV Manyata SS, 220kV/66kV HBR Layout SS 220kV Bus-3 & 4 of 220kV Yelahanka SS and 220kV Bus-1 of 220kV/66kV Shakarinagar | KPTCL to rectify the Bus Bar Protection at Puttenhally (SIFANG make CSC 150 type) in CONSULTATION WITH OEM | KPTCL | Puspha:KPTCL: 02/08/2024 22:23:27: ATtended.BBP taken in to service Puspha:KPTCL: 05/08/2024 10:45:46: Attended. After rectification bus bar protection taken in to service on 19.07.2024 | Complied | Pending
120/VI/2 | 400 kV Kaiga - Guttur 2 | 02-06-2024 22:54 | Guttur | KPTCL to rectify the DR time synchronisation at Guttur station | KPTCL | Puspha:KPTCL: 01/12/2024 23:48:00: Attended on 22.11.2024 | Complied | Complied
121/I/2 | Tripping of 220kV Bus-1 of 220kV/110kV Kemar SS and Complete Outage of 220kV/110kV Kavoor SS and 220kV/110kV MSEZ SS | 26-06-2024 09:34 | During antecedent conditions, 220kV/110kV Kemar is operating with Bus split condition at 220kV level. 220kV/110kV Kavoor SS and 220kV/110kV MSEZ SS are being radially connected to 220kV Bus-1 of Kemar SS. As per the reports submitted, the triggering incident was RYB_N fault in 220kV UPCL Kemar Line-1&2 due to lightning. For both lines, the fault was sensed in zone-1 at both ends and the lines tripped. Tripping of both lines led to loss of power supply to 220kV Kemar Bus-1 which in turn led to complete outage of 220kV/110kV Kavoor SS and 220kV/110kV MSEZ SS. | KPTCL may install TLAs in the lightning prone areas | KPTCL | Puspha:KPTCL: 28/09/2024 22:34:29: The matter is reffered to CEE, TRansmission ZOne Hassan and SEE,W&M Circle Mangalore. Further action is being taken up by them. | Pending | Pending
121/I/3 | Complete Outage of 220kV/66kV Adakanahally SS, 220kV/66kV Begur SS, 220kV/66kV Chamrajnagar SS, 220kV/66kV Madhuvanahalli SS, 220kV/66kV Hebbani SS of KPTCL and tripping of 220kV Bus-1 of 220kV/66kV Kadakola | 01-07-2024 02:53 | 220kV/66kV Adakanahally SS, 220kV/66kV Begur SS, 220kV/66kV Chamrajnagar SS, 220kV/66kV Madhuvanahalli SS, 220kV/66kV Hebbani SS are being radially fed though 220kV Bus-1 of 220kV/66kV Kadakola SS. As per the reports submitted, the triggering incident was Y-N fault in 220kV Mysore Hunsur Line-1 at 0.6kM from Mysore end. At both ends, the fault was sensed in zone-1 and Y-pole opened. After around 300ms, an R-N fault was observed in the line. Both ends sensed the fault in zone-1 and the line tripped at both ends. At the same time, 220kV Kadakola Kaniyambetta tripped only at Kadakola end on zone-1 . Also, Main-1 relay(Alstom make MICOM P747 type ) of 220kV B-phase Bus-1 BBP at Kadakola operated tripping all the elements connected to the Bus. The loss of power supply to 220kV Kadakola Bus-1 resulted in complete outage of 220kV/66kV Adakanahally SS, 220kV/66kV Begur SS, 220kV/66kV Chamrajnagar SS, 220kV/66kV Madhuvanahalli SS, 220kV/66kV Hebbani SS. Simultaneously, at 220kV/66kV Adakanahally SS, 220kV Adakanahally Kadakola line-1 and 2 tripped due to under-frequency operation in the M1 relay. The under-frequency function, enabled for the Bangalore Islanding Scheme (BIS), tripped both lines when the frequency dropped to 47.9 Hz. | Air leakage issue in Bus coupler CB at Kadakola to be rectified at earliest. | KPTCL | Puspha:KPTCL: 12/11/2024 10:31:38: Bus COupler CB over hauling is done and the issue is attended at Kadakola Sub station Puspha:KPTCL: 01/12/2024 23:48:00: Attended and complied Puspha:KPTCL: 17/02/2025 17:14:40: Bus Coupler CB over hauling has been done and it is taken in to service. | Complied | Pending
121/I/3 | Complete Outage of 220kV/66kV Adakanahally SS, 220kV/66kV Begur SS, 220kV/66kV Chamrajnagar SS, 220kV/66kV Madhuvanahalli SS, 220kV/66kV Hebbani SS of KPTCL and tripping of 220kV Bus-1 of 220kV/66kV Kadakola | 01-07-2024 02:53 | 220kV/66kV Adakanahally SS, 220kV/66kV Begur SS, 220kV/66kV Chamrajnagar SS, 220kV/66kV Madhuvanahalli SS, 220kV/66kV Hebbani SS are being radially fed though 220kV Bus-1 of 220kV/66kV Kadakola SS. As per the reports submitted, the triggering incident was Y-N fault in 220kV Mysore Hunsur Line-1 at 0.6kM from Mysore end. At both ends, the fault was sensed in zone-1 and Y-pole opened. After around 300ms, an R-N fault was observed in the line. Both ends sensed the fault in zone-1 and the line tripped at both ends. At the same time, 220kV Kadakola Kaniyambetta tripped only at Kadakola end on zone-1 . Also, Main-1 relay(Alstom make MICOM P747 type ) of 220kV B-phase Bus-1 BBP at Kadakola operated tripping all the elements connected to the Bus. The loss of power supply to 220kV Kadakola Bus-1 resulted in complete outage of 220kV/66kV Adakanahally SS, 220kV/66kV Begur SS, 220kV/66kV Chamrajnagar SS, 220kV/66kV Madhuvanahalli SS, 220kV/66kV Hebbani SS. Simultaneously, at 220kV/66kV Adakanahally SS, 220kV Adakanahally Kadakola line-1 and 2 tripped due to under-frequency operation in the M1 relay. The under-frequency function, enabled for the Bangalore Islanding Scheme (BIS), tripped both lines when the frequency dropped to 47.9 Hz. | KPTCL to furnish the DR &EL at Kadakola end to SRPC &SRLDC. | KPTCL |  | Pending | Pending
121/I/3 | Complete Outage of 220kV/66kV Adakanahally SS, 220kV/66kV Begur SS, 220kV/66kV Chamrajnagar SS, 220kV/66kV Madhuvanahalli SS, 220kV/66kV Hebbani SS of KPTCL and tripping of 220kV Bus-1 of 220kV/66kV Kadakola | 01-07-2024 02:53 | 220kV/66kV Adakanahally SS, 220kV/66kV Begur SS, 220kV/66kV Chamrajnagar SS, 220kV/66kV Madhuvanahalli SS, 220kV/66kV Hebbani SS are being radially fed though 220kV Bus-1 of 220kV/66kV Kadakola SS. As per the reports submitted, the triggering incident was Y-N fault in 220kV Mysore Hunsur Line-1 at 0.6kM from Mysore end. At both ends, the fault was sensed in zone-1 and Y-pole opened. After around 300ms, an R-N fault was observed in the line. Both ends sensed the fault in zone-1 and the line tripped at both ends. At the same time, 220kV Kadakola Kaniyambetta tripped only at Kadakola end on zone-1 . Also, Main-1 relay(Alstom make MICOM P747 type ) of 220kV B-phase Bus-1 BBP at Kadakola operated tripping all the elements connected to the Bus. The loss of power supply to 220kV Kadakola Bus-1 resulted in complete outage of 220kV/66kV Adakanahally SS, 220kV/66kV Begur SS, 220kV/66kV Chamrajnagar SS, 220kV/66kV Madhuvanahalli SS, 220kV/66kV Hebbani SS. Simultaneously, at 220kV/66kV Adakanahally SS, 220kV Adakanahally Kadakola line-1 and 2 tripped due to under-frequency operation in the M1 relay. The under-frequency function, enabled for the Bangalore Islanding Scheme (BIS), tripped both lines when the frequency dropped to 47.9 Hz. | KPTCL to rectify the issue of R-phase limb of CB of Bastipura Kadakola line. CB may be replaced if necessary. | KPTCL | Puspha:KPTCL: 28/09/2024 22:33:23: New Circuit Breaker is arranged for replacement of 220kV Bastipura line-1 &2 existing CBs. Replacement of one of the 100MVA Power Transformers is under progress at Kadakola. Replacement of Bastipura line CBs will be taken up after Dasara Celebrations. Puspha:KPTCL: 12/11/2024 10:31:38: Replacement of Bastipura Line CB is under progess at Kadakola Sub station Puspha:KPTCL: 17/02/2025 22:52:01: Attended, New CB commissioned for Bastipura -1 line on 04.12.2024 | Complied | Pending
121/I/5 | Complete Outage of 220kV/33kV SVIPL SS and 220kV BARC SS and Tripping of 220kV Bus-1 of 220kV/66kV Tallak SS | 11-07-2024 11:18 | 220kV/66kV Tallak SS is operating with split bus condition at 220kV level. As per the reports submitted, due to high RE generation in the downstream of 220kV Tallak, SS, 220kV Tallak Hiriyur line got overloaded upto 880A and the line tripped on over loading at Tallak end. However the R and Y poles of breaker failed to open causing LBB to operate and all elements connected to the Bus-1 of 220kV Tallak tripped. Since, 230kV/33kV Sagitur SS and 220kV BARC SS are being radially connected to 220kV Bus-1 of 220kV/66kV Tallak SS, the bus outage resulted in complete outage of 230kV/33kV Sagitur SS and 220kV BARC SS. | KPTCL to review the overload and overcurrent protection enabled in many 220kV lines. | KPTCL |  | Pending | Pending
121/I/5 | Complete Outage of 220kV/33kV SVIPL SS and 220kV BARC SS and Tripping of 220kV Bus-1 of 220kV/66kV Tallak SS | 11-07-2024 11:18 | 220kV/66kV Tallak SS is operating with split bus condition at 220kV level. As per the reports submitted, due to high RE generation in the downstream of 220kV Tallak, SS, 220kV Tallak Hiriyur line got overloaded upto 880A and the line tripped on over loading at Tallak end. However the R and Y poles of breaker failed to open causing LBB to operate and all elements connected to the Bus-1 of 220kV Tallak tripped. Since, 230kV/33kV Sagitur SS and 220kV BARC SS are being radially connected to 220kV Bus-1 of 220kV/66kV Tallak SS, the bus outage resulted in complete outage of 230kV/33kV Sagitur SS and 220kV BARC SS. | KPTCL to trigger DR for any protection operation at Thalak. | KPTCL | Puspha:KPTCL: 17/02/2025 22:47:48: Attended , for any protection operation DR will be generated | Complied | Pending
121/I/6 | Complete Outage of MANYATA - 220KV, ITI - 220KV, HBR_LAYOUT - 220KV | 12-07-2024 11:54 | As per the reports submitted, the 220kV Yelahanka-Yelahanka PG line-2 tripped at the Puttenahalli end due to the operation of the 96-trip relay, with no fault in the line. Pre-fault current for 220kV Puttenahalli-Yelahanka PG line 1 was recorded as 787 A, 777 A, and 759 A. At 11:52:00.814 Hrs, after tripping of 220kV Yelahanka-Yelahanka PG line 2 an I>4 trip was triggered at Yelahanka end with currents of 1472 A, 1477 A, and 1455 A, exceeding the SPS setting of 1250 A. | KPTCL to review the overload and overcurrent protections enabled in many 220kV lines. | KPTCL |  | Pending | Pending
121/I/6 | Complete Outage of MANYATA - 220KV, ITI - 220KV, HBR_LAYOUT - 220KV | 12-07-2024 11:54 | As per the reports submitted, the 220kV Yelahanka-Yelahanka PG line-2 tripped at the Puttenahalli end due to the operation of the 96-trip relay, with no fault in the line. Pre-fault current for 220kV Puttenahalli-Yelahanka PG line 1 was recorded as 787 A, 777 A, and 759 A. At 11:52:00.814 Hrs, after tripping of 220kV Yelahanka-Yelahanka PG line 2 an I>4 trip was triggered at Yelahanka end with currents of 1472 A, 1477 A, and 1455 A, exceeding the SPS setting of 1250 A. | KPTCL to review the SPS logic /participating loads i.r.o the SPS for the overloading of the Yelahanka PG-Puttenahalli and the revised SPS to be approved by OCC forum. | KPTCL |  | Pending | Pending
121/II/3 | Tripping of 220kV Bus-2 of 220kV Sharavathy PH of KPCL | 18-06-2024 13:14 | The bus bar protection operated leading to the tripping of elements connected to South-West Bus (Bus-2) and bus sectionalizer. Unit-6 ,7, 8 &10 which were connected to Bus-2 tripped on Bus bar protection. However, during the bus fault, Unit-2 also tripped on GT differential protection. | KPCL to maintain proper clearance and RoW in and around substation premises. | KPCL | EE (E )/CEED:KPCL: 02/09/2024 10:37:12: Clearances Maintained. Requested to close the point. | Complied | Complied
121/V/1 | Tripping of 400kV YTPS BPS-2 | 26-06-2024 16:42 | YTPS & BPS A/R Not operated | KPCL to submit the action taken report. | KPCL | EE (E )/CEED:KPCL: 02/09/2024 10:37:12: The Tie breaker control is kept in Switchyard control for successful operation of A/R function. Requested to close the point. | Complied | Complied
121/v/2 | Tripping of 400kV YTPS BPS-2 | 26-06-2024 14:32 | YTPS & BPS A/R not operated | KPCL to submit the action taken report. | KPCL | EE (E )/CEED:KPCL: 02/09/2024 10:37:12: The Tie breaker control is kept in Switchyard control for successful operation of A/R function. Requested to close the point. | Complied | Complied
122/I/1 | Complete Outage of CHIKKAMAGALURU - 220KV | 17-07-2024 14:55 | As per the reports submitted, the triggering incident was Y-N fault in 220kV Shimoga Chikmangalore Line. At Shimoga end, all three poles tripped but the same could not be verified due to non-submission of DR. At Chikkamangalore end, the fault was sensed in Zone-1 and Y-pole opened. During dead time, B-N fault was also observed in the same line, however no protection operated at Chikkamangalore end. This fault was cleared by 220kV Chikkamangalore Hassan line on Zone-3 protection at Hassan end with a delay of 800ms. Subsequently, the Breaker of 220kV Chikkamangalore Shimoga line at Chikkamangalore tripped on pole discrepancy. Tripping of both lines led to complete outage of 220kV/66kV Chikkamangalore SS. | KPTCL to examine the reason for the Non operation of Main-2 relay at the time of reclose at Chikamagalur end | KPTCL | Puspha:KPTCL: 12/11/2024 10:31:38: Issue in AR logic in Shimoga line is rectified at Shimoga SUb station Puspha:KPTCL: 08/12/2024 06:42:40: AR Logic issue was rectified and complied. | Complied | Complied
122/I/1 | Complete Outage of CHIKKAMAGALURU - 220KV | 17-07-2024 14:55 | As per the reports submitted, the triggering incident was Y-N fault in 220kV Shimoga Chikmangalore Line. At Shimoga end, all three poles tripped but the same could not be verified due to non-submission of DR. At Chikkamangalore end, the fault was sensed in Zone-1 and Y-pole opened. During dead time, B-N fault was also observed in the same line, however no protection operated at Chikkamangalore end. This fault was cleared by 220kV Chikkamangalore Hassan line on Zone-3 protection at Hassan end with a delay of 800ms. Subsequently, the Breaker of 220kV Chikkamangalore Shimoga line at Chikkamangalore tripped on pole discrepancy. Tripping of both lines led to complete outage of 220kV/66kV Chikkamangalore SS. | KPTCL to expedite to replace the Main-I relay at Chikamagalur end | KPTCL | Puspha:KPTCL: 17/02/2025 17:03:32: Attended on 21.01.2025. Main I REL 670 ABB Make relay of Shimoga Bay repaired and taken into service on 21.01.2025 | Complied | Complied
122/I/1 | Complete Outage of CHIKKAMAGALURU - 220KV | 17-07-2024 14:55 | As per the reports submitted, the triggering incident was Y-N fault in 220kV Shimoga Chikmangalore Line. At Shimoga end, all three poles tripped but the same could not be verified due to non-submission of DR. At Chikkamangalore end, the fault was sensed in Zone-1 and Y-pole opened. During dead time, B-N fault was also observed in the same line, however no protection operated at Chikkamangalore end. This fault was cleared by 220kV Chikkamangalore Hassan line on Zone-3 protection at Hassan end with a delay of 800ms. Subsequently, the Breaker of 220kV Chikkamangalore Shimoga line at Chikkamangalore tripped on pole discrepancy. Tripping of both lines led to complete outage of 220kV/66kV Chikkamangalore SS. | KPTCL to resolve the DR time synchronisation issue at Chikmagalur end | KPTCL | Puspha:KPTCL: 12/11/2024 10:31:38: Attended Puspha:KPTCL: 01/12/2024 23:48:00: Attended and complied | Complied | Complied
122/I/3 | Tripping of 220kV Bus-1 and 2 of 400kV/220kV Jagalur SS and Complete Outage of 220kV/66kV Chitradurga SS, 220kV/66kV Tallak SS, 220kV/66kV Kudligi SS of KPTCL and 220kV Barc SS, 220kV Sagitur SS of KPTCL | 22-07-2024 11:47 | As per the reports submitted, the triggering incident was the tripping of 220kV Chitradurga-Hiriyur line on suspected over current protection operation (I>2, Ir-955A Iy-1019A Ib-961A) as the flow reached above 320MW. With the tripping of the 220kV Chitradurga-Hiriyur line, the flow increased in 220kV Chitradurga-Tallak and 220kV Tallak-Hiriyur. By which the over current has picked up in 220kV Tallak-Hiriyur at Tallak end | KPTCL to provide feedback to the Planning wing to carry out necessary studies to plan transmission system. | KPTCL | Puspha:KPTCL: 12/11/2024 10:31:38: DR configuration is verified. DRs and Events are configured for start and trip protection functions both | Complied | Pending
122/I/3 | Tripping of 220kV Bus-1 and 2 of 400kV/220kV Jagalur SS and Complete Outage of 220kV/66kV Chitradurga SS, 220kV/66kV Tallak SS, 220kV/66kV Kudligi SS of KPTCL and 220kV Barc SS, 220kV Sagitur SS of KPTCL | 22-07-2024 11:47 | As per the reports submitted, the triggering incident was the tripping of 220kV Chitradurga-Hiriyur line on suspected over current protection operation (I>2, Ir-955A Iy-1019A Ib-961A) as the flow reached above 320MW. With the tripping of the 220kV Chitradurga-Hiriyur line, the flow increased in 220kV Chitradurga-Tallak and 220kV Tallak-Hiriyur. By which the over current has picked up in 220kV Tallak-Hiriyur at Tallak end | KPTCL to rectify the DR time synchronisation issue at Guttur station. | KPTCL | Puspha:KPTCL: 01/12/2024 23:48:00: Attended on 22.11.2024 | Complied | Pending
122/I/3 | Tripping of 220kV Bus-1 and 2 of 400kV/220kV Jagalur SS and Complete Outage of 220kV/66kV Chitradurga SS, 220kV/66kV Tallak SS, 220kV/66kV Kudligi SS of KPTCL and 220kV Barc SS, 220kV Sagitur SS of KPTCL | 22-07-2024 11:47 | As per the reports submitted, the triggering incident was the tripping of 220kV Chitradurga-Hiriyur line on suspected over current protection operation (I>2, Ir-955A Iy-1019A Ib-961A) as the flow reached above 320MW. With the tripping of the 220kV Chitradurga-Hiriyur line, the flow increased in 220kV Chitradurga-Tallak and 220kV Tallak-Hiriyur. By which the over current has picked up in 220kV Tallak-Hiriyur at Tallak end | KPTCL to resolve the non-triggering of DR of Siemens relay of Jagalur ICTs. | KPTCL | Puspha:KPTCL: 17/02/2025 16:57:37: As per the settings, first SPS operation will come followed by OCR tripping. In Siemens relays, DRs are triggered for SPS operation during subsequent OCR tripping events are generated. In view of this SRPC is requested to close this recommendation. | Pending | Pending
122/I/3 | Tripping of 220kV Bus-1 and 2 of 400kV/220kV Jagalur SS and Complete Outage of 220kV/66kV Chitradurga SS, 220kV/66kV Tallak SS, 220kV/66kV Kudligi SS of KPTCL and 220kV Barc SS, 220kV Sagitur SS of KPTCL | 22-07-2024 11:47 | As per the reports submitted, the triggering incident was the tripping of 220kV Chitradurga-Hiriyur line on suspected over current protection operation (I>2, Ir-955A Iy-1019A Ib-961A) as the flow reached above 320MW. With the tripping of the 220kV Chitradurga-Hiriyur line, the flow increased in 220kV Chitradurga-Tallak and 220kV Tallak-Hiriyur. By which the over current has picked up in 220kV Tallak-Hiriyur at Tallak end | KPTCL to review the overload and overcurrent settings of all the elements in the system. | KPTCL |  | Pending | Pending
122/I/5 | Tripping of 220kV Bus-2 of 220kV Vajramatti SS and Complete outage of 220kV Kavatagi LIS | 26-07-2024 06:13 | During antecedent conditions, 220kV Kavatagi LIS was radially fed from 220kV Vajramatti Bus-2. The triggering incident is the R-N fault on the 220kV Vajramatti-Mahalingapur-2 line led to tripping at the Mahalingapur end, while a suspected DC supply issue at Vajramatti prevented the circuit breaker from operating, causing tripping of lines connected to remote ends on Z-2 for elements connected to Bus-2 and Bus coupler, leading to the complete outage of 220kV Kavatagi LIS and a generation loss of 150MW at Alamatti PH. | KPTCL to ensure to enable Auto reclosure in all lines | KPTCL | Puspha:KPTCL: 12/11/2024 10:37:39: Main-1 relays are not compatible for configuring AR, hence proposed for replacement of these relays. After replacing Main-1 relays AR will be put in to service | Pending | Pending
122/I/5 | Tripping of 220kV Bus-2 of 220kV Vajramatti SS and Complete outage of 220kV Kavatagi LIS | 26-07-2024 06:13 | During antecedent conditions, 220kV Kavatagi LIS was radially fed from 220kV Vajramatti Bus-2. The triggering incident is the R-N fault on the 220kV Vajramatti-Mahalingapur-2 line led to tripping at the Mahalingapur end, while a suspected DC supply issue at Vajramatti prevented the circuit breaker from operating, causing tripping of lines connected to remote ends on Z-2 for elements connected to Bus-2 and Bus coupler, leading to the complete outage of 220kV Kavatagi LIS and a generation loss of 150MW at Alamatti PH. | KPTCL to examine the reason of tripping of 220kV Mahalingapura-Atani line during the incident and requested to furnish the detailed report in this regard. | KPTCL | Puspha:KPTCL: 28/09/2024 22:28:09: Verified. DEF setting in Main-1 relay is revised at Athani Sub station for Mahaingapura lne Puspha:KPTCL: 01/12/2024 23:48:00: Attended. DEF setting enabled in Main-1 relay of Mahalingapura line at Athani is reviewed | Complied | Pending
122/I/5 | Tripping of 220kV Bus-2 of 220kV Vajramatti SS and Complete outage of 220kV Kavatagi LIS | 26-07-2024 06:13 | During antecedent conditions, 220kV Kavatagi LIS was radially fed from 220kV Vajramatti Bus-2. The triggering incident is the R-N fault on the 220kV Vajramatti-Mahalingapur-2 line led to tripping at the Mahalingapur end, while a suspected DC supply issue at Vajramatti prevented the circuit breaker from operating, causing tripping of lines connected to remote ends on Z-2 for elements connected to Bus-2 and Bus coupler, leading to the complete outage of 220kV Kavatagi LIS and a generation loss of 150MW at Alamatti PH. | KPTCL to resolve the DR time synchronization issue at Vajramatti end | KPTCL | Puspha:KPTCL: 12/11/2024 10:37:39: Will be attended by the Substation | Pending | Pending
122/I/5 | Tripping of 220kV Bus-2 of 220kV Vajramatti SS and Complete outage of 220kV Kavatagi LIS | 26-07-2024 06:13 | During antecedent conditions, 220kV Kavatagi LIS was radially fed from 220kV Vajramatti Bus-2. The triggering incident is the R-N fault on the 220kV Vajramatti-Mahalingapur-2 line led to tripping at the Mahalingapur end, while a suspected DC supply issue at Vajramatti prevented the circuit breaker from operating, causing tripping of lines connected to remote ends on Z-2 for elements connected to Bus-2 and Bus coupler, leading to the complete outage of 220kV Kavatagi LIS and a generation loss of 150MW at Alamatti PH. | SRLDC and KPTCL to comply IEGC Regulations and ensure to furnish the detailed report within the specified timeline. | KPTCL | Puspha:KPTCL: 12/11/2024 10:31:38: Will be complied by KPTCL Puspha:KPTCL: 17/02/2025 17:13:06: Regulations will be followed by KPTCL | Complied | Pending
122/I/8 | Complete Outage of 220kV/66kV Hiriyur_KA SS and 220kV Enercon and 220kV Azure SS | 05-08-2024 09:41 | 220kV Enercon and 220kV Azure SS are being radially connected to 220kV/66kV Hiriyur_KA SS. As per the reports submitted, the triggering incident was R-phase CT flashover in 66kV Bus sectionaliser in 220kV/66kV Hiriyur_KA SS which subsequently became an RYB-N fault. At the same time, due to DC supply failure, CTDs of all lines and Transformers tripped causing complete outage of 220kV/66kV Hiriyur_KA SS which in turn led to complete outage of 220kV Enercon and 220kV Azure SS. | KPTCL to disable CTD in all lines. | KPTCL | Puspha:KPTCL: 28/09/2024 22:26:42: CTD is disabled for all line Circuit Breakers at Hiriyur. | Complied | Complied
122/I/8 | Complete Outage of 220kV/66kV Hiriyur_KA SS and 220kV Enercon and 220kV Azure SS | 05-08-2024 09:41 | 220kV Enercon and 220kV Azure SS are being radially connected to 220kV/66kV Hiriyur_KA SS. As per the reports submitted, the triggering incident was R-phase CT flashover in 66kV Bus sectionaliser in 220kV/66kV Hiriyur_KA SS which subsequently became an RYB-N fault. At the same time, due to DC supply failure, CTDs of all lines and Transformers tripped causing complete outage of 220kV/66kV Hiriyur_KA SS which in turn led to complete outage of 220kV Enercon and 220kV Azure SS. | KPTCL to ensure the DC source is sufficient to cater the loads and distribution of load to be completed | KPTCL | Puspha:KPTCL: 08/12/2024 06:42:40: Attended, necessary modifications are done in the DCDB.As a permanent measure additional DCDB will be privided | Complied | Complied
122/II/6 | Tripping of 400kV Bus-1 of 400kV/220kV Talguppa SS | 03-08-2024 15:54 | As per the reports submitted, 400/220kV Talaguppa ICT-2 HV side was charged one day prior to the event. Before charging of the ICT-2, ICT-1 and 3 were carrying around 230MW each. During the charging of the LV side of ICT-2 and breaker was closed for few seconds where in each ICT-1,2,3 was carrying around 165MW, heavy arcing was observed at ICT-2 220kV side Y-phase and ICT-2 was immediately hand tripped | KPTCL/KPCL to review the PSS settings at Sharavathy station | KPCL | EE (E )/CEED:KPCL: 01/10/2024 15:32:19: PSS Settings at SGS shall be reviewed. | Complied | Complied
122/II/6 | Tripping of 400kV Bus-1 of 400kV/220kV Talguppa SS | 03-08-2024 15:54 | As per the reports submitted, 400/220kV Talaguppa ICT-2 HV side was charged one day prior to the event. Before charging of the ICT-2, ICT-1 and 3 were carrying around 230MW each. During the charging of the LV side of ICT-2 and breaker was closed for few seconds where in each ICT-1,2,3 was carrying around 165MW, heavy arcing was observed at ICT-2 220kV side Y-phase and ICT-2 was immediately hand tripped | KPTCL to review the bus coupler settings at Kemar and Kadur substation. | KPTCL | Puspha:KPTCL: 28/09/2024 22:25:51: Reviewed, Bus Coupler connected CT ratio is changed from 600/1 to 800/1 and over current settings reviewed accordingly | Complied | Complied
122/II/9 | Tripping of 220kV Bus-1 of 220kV Somanahalli SS of KPTCL | 13-08-2024 09:51 | 220kV Somanahalli North Bus is connected to 220kV Somanahalli Bidadi Line-1&2 with bus coupler in open condition. As per the reports submitted, the triggering incident was high resistance R-N fault in 220kV Bidadi Somanahalli Line-1. At Bidadi end, the fault was sensed in zone-2 and tripped with a delay of 350ms. The line was holding at Somanahalli end. At the same time, 220kV Bidadi Somanahalli Line-2 tripped only at Somanahalli end on zone-4 protection. Tripping of both lines led to loss of power supply to North bus. | KPTCL to expedite to complete the R&M works at Somanahally station | KPTCL | Puspha:KPTCL: 12/11/2024 10:31:38: Presently, controls of all line bays shifted to new CRP mounted in Bay KIOSKs. Shifting of controls of Power Transformers and Bus Couplers is under progress. | Pending | Pending
122/VI/5 | 220KV-BIDADI-SOMANAHALLI-2 | 13-08-2024 09:51 | KPTCL stated that at BIDADI SS, the GPS device is faulty. The device will be rectified | KPTCL to rectify the GPS device at Bidadi substation | KPTCL | Puspha:KPTCL: 12/11/2024 10:31:38: The device is sent to M/s SANDs factory at Chennai for repairs | Complied | Complied
122/VI/6 | 220KV-BIDADI-SOMANAHALLI-2 | 13-08-2024 09:51 | KPTCL stated that the issue has been covered under Substation automation. | KPTCL to expediate to complete the substation automation works at 220kV Somanahalli substation. | KPTCL | Puspha:KPTCL: 12/11/2024 10:31:38: Works are under progress, line bays completed | Pending | Pending
122/VI/8 | 220KV-KADAKOLA-KANIYAMPETTA | 8-08-2024 14:19 | KADAKOLA - 220KV | KPTCL to furnish the report on DR time synchronization issue at Kadakola end. | KPTCL |  | Pending | Pending
123/I/2 | Complete outage of 220kV/66kV Lingsugur SS, 220kV/110kV Bagewadii SS, 220kV Baluti SS, 220kV/66kV Kushtagi SS, 220kV/66kV Gangavathi SS, 220kV/66kV Kushtagi SS, 220kV/66kV Narayanpur SS, 220kV/66kV Mallat SS, 220kV/66kV Sindhanur SS of KPTCL, 220kV Almatti PH of KPCL, 220kV/33kV Fortune Five SS, 220kV,33kV Atria SS, 220kV/33kV Bagewadri_RBRK SS. | 28-08-2024 11:31 | During antecedent conditions, 220kV Lingapur Gangavathi Line-1&2, 220kV Nandhihal Bagewadi Line-1&2 were under outage. As per the reports submitted, the triggering incident was tripping of 220kV Shahpur-Lingsugur Line. Subsequently 220kV RTPS- Mallat line, 220kV RTPS-Lingsugur-1&2 and 220kV ADPH- Bagalkot line 1&2 tripped on over load. Tripping of all these lines resulted in complete outage of 220kV/66kV Lingsugur SS, 220kV/110kV Bagewadii SS, 220kV Baluti SS, 220kV/66kV Kushtagi SS, 220kV/66kV Gangavathi SS, 220kV/66kV Kushtagi SS, 220kV/66kV Narayanpur SS, 220kV/66kV Mallat SS, 220kV/66kV Sindhanur SS of KPTCL, 220kV Almatti PH of KPCL, 220kV/33kV Fortune Five SS, 220kV,33kV Atria SS, 220kV/33kV Bagewadri_RBRK SS. | KPCL to rectify the issue with P444 relays at KPCL end. | KPCL | EE (E )/CEED:KPCL: 06/11/2024 12:22:20: Issue has been discussed with OEM and action will be taken as per OEM reccommendations. EE (E )/CEED:KPCL: 02/12/2024 14:49:00: Issue has been discussed with OEM and action will be taken as per OEM reccommendations. EE (E )/CEED:KPCL: 02/01/2025 12:15:19: Issue has been discussed with OEM and action will be taken as per OEM reccommendations. | Complied | Complied
123/I/2 | Complete outage of 220kV/66kV Lingsugur SS, 220kV/110kV Bagewadii SS, 220kV Baluti SS, 220kV/66kV Kushtagi SS, 220kV/66kV Gangavathi SS, 220kV/66kV Kushtagi SS, 220kV/66kV Narayanpur SS, 220kV/66kV Mallat SS, 220kV/66kV Sindhanur SS of KPTCL, 220kV Almatti PH of KPCL, 220kV/33kV Fortune Five SS, 220kV,33kV Atria SS, 220kV/33kV Bagewadri_RBRK SS. | 28-08-2024 11:31 | During antecedent conditions, 220kV Lingapur Gangavathi Line-1&2, 220kV Nandhihal Bagewadi Line-1&2 were under outage. As per the reports submitted, the triggering incident was tripping of 220kV Shahpur-Lingsugur Line. Subsequently 220kV RTPS- Mallat line, 220kV RTPS-Lingsugur-1&2 and 220kV ADPH- Bagalkot line 1&2 tripped on over load. Tripping of all these lines resulted in complete outage of 220kV/66kV Lingsugur SS, 220kV/110kV Bagewadii SS, 220kV Baluti SS, 220kV/66kV Kushtagi SS, 220kV/66kV Gangavathi SS, 220kV/66kV Kushtagi SS, 220kV/66kV Narayanpur SS, 220kV/66kV Mallat SS, 220kV/66kV Sindhanur SS of KPTCL, 220kV Almatti PH of KPCL, 220kV/33kV Fortune Five SS, 220kV,33kV Atria SS, 220kV/33kV Bagewadri_RBRK SS. | KPTCL to relook into the overcurrent & overload settings on their 220 kV lines. And also take necessary actions to strengthen the system | KPTCL | Puspha:KPTCL: 05/11/2024 11:39:00: Over current and over load settings are reviwed for Shahapur line at Lingasugur | Complied | Complied
123/I/3 | Complete outage of 220kV/66kV Kadakola SS, 220kV/66kV Adakanahalli SS, 220kV/66kV Chamrajnagar SS, 220kV/66kV Madhuvanahalli SS, 220kV/66kV Hebbani SS, 220kV/66kV TK Halli SS of KPTCL and 220kV/66kV Kaniyambetta SS of KSEB. | 28-08-2024 11:38 | During antecedent conditions, 220kV TK Halli Kanakpura, 220kV Vajamangala TK Halli, 220kV Kadakola Hootagally are in open condition. As per the reports submitted, the triggering incident was R-phase jumper failure in 220kV Mysore Kadakola Line-2. Subsequently, 220kV Mysore Kadakola Line-1 and 220kV Kaniyambetta Kunnamangalam line tripped on over loading. Tripping of all these lines led to complete outage of 220kV/66kV Kadakola SS, 220kV/66kV Adakanahalli SS, 220kV/66kV Chamrajnagar SS, 220kV/66kV Madhuvanahalli SS, 220kV/66kV Hebbani SS, 220kV/66kV TK Halli SS of KPTCL and 220kV/66kV Kaniyambetta SS of KSEB. | KPTCL to relook into the overcurrent/overload settings on lines. And also take necessary actions to strengthen the system. | KPTCL | Puspha:KPTCL: 05/11/2024 11:39:00: Over current /Over load settings are reviewed at Kadakola. | Complied | Pending
123/I/3 | Complete outage of 220kV/66kV Kadakola SS, 220kV/66kV Adakanahalli SS, 220kV/66kV Chamrajnagar SS, 220kV/66kV Madhuvanahalli SS, 220kV/66kV Hebbani SS, 220kV/66kV TK Halli SS of KPTCL and 220kV/66kV Kaniyambetta SS of KSEB. | 28-08-2024 11:38 | During antecedent conditions, 220kV TK Halli Kanakpura, 220kV Vajamangala TK Halli, 220kV Kadakola Hootagally are in open condition. As per the reports submitted, the triggering incident was R-phase jumper failure in 220kV Mysore Kadakola Line-2. Subsequently, 220kV Mysore Kadakola Line-1 and 220kV Kaniyambetta Kunnamangalam line tripped on over loading. Tripping of all these lines led to complete outage of 220kV/66kV Kadakola SS, 220kV/66kV Adakanahalli SS, 220kV/66kV Chamrajnagar SS, 220kV/66kV Madhuvanahalli SS, 220kV/66kV Hebbani SS, 220kV/66kV TK Halli SS of KPTCL and 220kV/66kV Kaniyambetta SS of KSEB. | Switching operations to be done as per instructions of KAR SLDC. | KPTCL | Puspha:KPTCL: 05/11/2024 11:39:00: Clear Instructions are given to concerned sub stations in this regard | Complied | Pending
123/I/5 | Complete Outage of 220kV Madhuvanahalli SS, 220kV Chamrajnagar SS and 220kV Hebbani SS. | 28-08-2024 12:15 | At 11.56 Hrs, Hebbani 66kV bus was charged taking supply from Tubinakere 220kV Sub station through 66kV Tubinakere_mandya_KK Hally_Malavalli_Hadli_Shimsha_Hebbani link. 220kV Bus at Hebbani was back charged and supply extended to 220kV Madhuvanahally SS and 220kV Chamarajanagar SS. 220kV Chamarajanagar- Begur D/c line was kept open during this incident. It is reported that at 12.09 Hrs 66kV KK Hally-Shimsha line tripped at KK Hally end due to over load resulting in de energisation of 220kV/66kV Chamrajnagar SS, 220kV/66kV Madhuvanahalli SS, and 220kV/66kV Hebbani SS | KPTCL to relook into the overcurrent/overload settings on lines. And also take necessary actions to strengthen the system. | KPTCL | Puspha:KPTCL: 12/11/2024 10:31:38: Over current/over load settings in 220kV lines will be modified by availing approval from the Higher management | Complied | Complied
123/I/6 | Complete Outage of 220kV Raichur_KA of KPTCL of and 220kV Upper Jurala_PH of TSGENCO | 28-08-2024 15:20 | During antecedent conditions, 220kV Upper Jurala_PH Jurala Line-1&2 were under outage. The triggering incident was R-N fault in 220kV Raichur RTPS Line-2. At the same time, 220kV Raichur RTPS Line-1 also tripped at RTPS end. Tripping of both lines led to loss of power evacuation at 220kV Upper Jurala_PH leading to tripping of all units on over frequency. This led to complete outage of 220kV Raichur_KA SS and 220kV Upper Jurala_PH. | KPCL to enable auto reclosure at RTPS end on 220 kV Raichur RTPS D/C line. | KPCL | EE (E )/CEED:KPCL: 06/11/2024 12:22:20: AR Will be enabled in co-ordination with KPTCL after getting clearance from KPTCL regarding PLCC Checks EE (E )/CEED:KPCL: 02/12/2024 14:49:00: Issue has been discussed with OEM and action will be taken as per OEM reccommendations. EE (E )/CEED:KPCL: 02/01/2025 12:15:19: AR Will be enabled in co-ordination with KPTCL after getting clearance from KPTCL regarding PLCC Checks EE (E )/CEED:KPCL: 06/02/2025 14:53:36: Retrofitting of ABB make REL511 relays with GE make D60 numerical relays as Main-I distance protection is completed for all the lines except RTPS-Mallat line and will be completed by March-2025. Two Bus will be made operational after completion of above works. EE (E )/CEED:KPCL: 01/03/2025 14:23:15: etrofitting of ABB make REL511 relays with GE make D60 numerical relays as Main-I distance protection is completed for all the lines except RTPS-Mallat line and will be completed by March-2025. Two Bus will be made operational after completion of above works by Mar 2025. EE (E )/CEED:KPCL: 02/07/2025 10:38:15: All relays installation works completed and AR Will be enabled in co-ordination with KPTCL after getting clearance from KPTCL regarding PLCC Checks. | Complied | Complied
123/I/6 | Complete Outage of 220kV Raichur_KA of KPTCL of and 220kV Upper Jurala_PH of TSGENCO | 28-08-2024 15:20 | During antecedent conditions, 220kV Upper Jurala_PH Jurala Line-1&2 were under outage. The triggering incident was R-N fault in 220kV Raichur RTPS Line-2. At the same time, 220kV Raichur RTPS Line-1 also tripped at RTPS end. Tripping of both lines led to loss of power evacuation at 220kV Upper Jurala_PH leading to tripping of all units on over frequency. This led to complete outage of 220kV Raichur_KA SS and 220kV Upper Jurala_PH. | KPTCL to ensure to carry out periodic maintenance of substation | KPTCL | Puspha:KPTCL: 17/02/2025 16:43:40: Maintenance activities are carried out on regular basis Puspha:KPTCL: 02/03/2025 23:54:12: Being followed , periodic maintenance activities are carried out in the Substation | Complied | Complied
123/I/6 | Complete Outage of 220kV Raichur_KA of KPTCL of and 220kV Upper Jurala_PH of TSGENCO | 28-08-2024 15:20 | During antecedent conditions, 220kV Upper Jurala_PH Jurala Line-1&2 were under outage. The triggering incident was R-N fault in 220kV Raichur RTPS Line-2. At the same time, 220kV Raichur RTPS Line-1 also tripped at RTPS end. Tripping of both lines led to loss of power evacuation at 220kV Upper Jurala_PH leading to tripping of all units on over frequency. This led to complete outage of 220kV Raichur_KA SS and 220kV Upper Jurala_PH. | KPTCL to review the time delay settings of all Distance protection set in all relays at 220kV Raichur station | KPCL | Puspha:KPTCL: 05/11/2024 18:07:03: Zone-4 operation is at KPCL end, recommendation to be complied by KPCL EE (E )/CEED:KPCL: 06/02/2025 14:47:44: The settings will be revised in co ordination with CERT, KPTCL by May 2025. EE (E )/CEED:KPCL: 01/03/2025 14:23:15: Zone 4 settings are set to 0.5 sec as per KPTCL reccommendation. It is requested to close the point. | Complied | Complied
123/I/7 | Tripping of 220kV Bus of 400kV/220kV Kalaburgi SS, 220kV Bus-2 of 220kV/110kV Sedam, 220kV Bus-1 of 220kV/110kV 220kV Shahpur SS and complete outage of 220kV/110kV Gangapur SS, 220kV/110kV Humnabad SS, 220kV/110kV Kapanoor SS 220kV/110kV Halabarga sations and 220kV Avada IPP | 01-09-2024 03:15 | The triggering incident is the tripping of 400/220kV ICTs at Kalburgi on Over Flux Protection which led to 220kV Bus-2 of 220kV/110kV Sedam, 220kV Bus-1 of 220kV/110kV 220kV Shahpur SS and complete outage of 220kV/110kV Gangapur SS, 220kV/110kV Humnabad SS, 220kV/110kV Kapanoor SS 220kV/110kV Halabarga sations and 220kV Avada IPP | In addition to LGBR, KA-SLDCs to factor in MVAR injection also in managing grid-operation involving decisions relating to bus-split operation | KPTCL | Puspha:KPTCL: 12/11/2024 10:31:38: The matter is reffered to SLDC for further needful action by them | Complied | Pending
123/I/7 | Tripping of 220kV Bus of 400kV/220kV Kalaburgi SS, 220kV Bus-2 of 220kV/110kV Sedam, 220kV Bus-1 of 220kV/110kV 220kV Shahpur SS and complete outage of 220kV/110kV Gangapur SS, 220kV/110kV Humnabad SS, 220kV/110kV Kapanoor SS 220kV/110kV Halabarga sations and 220kV Avada IPP | 01-09-2024 03:15 | The triggering incident is the tripping of 400/220kV ICTs at Kalburgi on Over Flux Protection which led to 220kV Bus-2 of 220kV/110kV Sedam, 220kV Bus-1 of 220kV/110kV 220kV Shahpur SS and complete outage of 220kV/110kV Gangapur SS, 220kV/110kV Humnabad SS, 220kV/110kV Kapanoor SS 220kV/110kV Halabarga sations and 220kV Avada IPP | KPTCL to furnish the DR of Kalaburgi ICT to SRLDC/SRPC to verify the operation | KPTCL |  | Pending | Pending
123/II/3 | Tripping of 400kV Bus-1 and 2 at 400kV/220kV Guttur SS of KPTCL | 22-08-2024 19:54 | As per the reports submitted, the triggering incident was 400V Bus-2 BBP malopertion due to relay cable fault in 400kV/220kV Guttur ICT-2. At the same time, due to error in isolator selection, 400kV Bus-1 BBP also operated leading to tripping of all elements connected to 400kV Bus-1 and 400kV Bus-2 at 400kV/220kV Guttur SS. | KPTCL to rectifly all cable related issues at Guttur station. | KPTCL | Puspha:KPTCL: 05/11/2024 18:07:03: The matter is referred to CEE,TZ, Tumkur to make arrangements for new control cables for replacement of fauty control cables Puspha:KPTCL: 12/11/2024 10:37:39: The matter is reffered to CEE,TZ ,Tumkur fr arranginf new control cables for replacement of faulty control cables at Guttur Puspha:KPTCL: 17/02/2025 17:17:31: Control cable with minor problems are rectified by using heathy spare cores. Control cables with major problems are replaced as and when reported. Request has been given by site to supply spare control cables for using during emergency. . | Complied | Complied
123/VI/1 | 220KV-MYSORE-KADAKOLA-1 | 28-08-2024 11:38 | KADAKOLA - 220KV DR TIME SYNC ISSUE | KPTCL to rectify the DR Time synchronization issue at Kadakola Station | KPTCL | Puspha:KPTCL: 12/11/2024 10:31:38: GPS time synchronising equipment is in working condition, relay configuration issue w.r.t GPS time sync issue will be verified in coordination with OEM | Complied | Complied
123/VI/2 | 220KV-LINGSUGUR-RTPS-2 | 28-08-2024 13:29 | DR TIME SYNC ISSUE AT 220kV Lingasur SS | KPTCL to rectify the DR Time synchronization issue at Lingsugur Station | KPTCL |  | Pending | Pending
123/VI/3 | 220KV-LINGSUGUR-BASAVANA_BAGEWADI-1 | 28-08-2024 13:29 | DR Time sync Issue at LINGSUGUR - 220KV | KPTCL to rectify the DR Time synchronization issue at Lingsugur Station | KPTCL | Puspha:KPTCL: 12/11/2024 10:44:55: The GPS device is sent to OEM factoy at Chennai for repairs | Complied | Complied
123/VI/4 | 220KV-BASAVANA_BAGEWADI-NARAYANPUR-2 | 28-08-2024 13:29 | DR Time Sync Issue at BASAVANA_BAGEWADI - 220KV | KPTCL to furnish the report regarding the action taken to rectify the DR time syn issue at Basavana Bagewadi station | KPTCL |  | Pending | Pending
123/VI/5 | LINGSUGUR - 220KV | 28-08-2024 13:29 | DR TIME SYNC ISSUE | KPTCL to rectify the DR Time synchronization issue at Lingsugur Station. | KPTCL | Puspha:KPTCL: 12/11/2024 10:44:09: The GPS time sync device is sent for repairs to OEM factory at Chennai | Complied | Complied
123/VI/6 | RAICHUR_KA - 220KV | 28-08-2024 15:20 | DR TIME SYNC ISSUE | KPTCL to rectify the DR Time synchronization issue at Raichur Station | KPTCL |  | Pending | Pending
123/VI/7 | 220KV-RTPS-RAICHUR_KA-2 | 28-08-2024 15:20 | DR TIME SYNC ISSUE | KPTCL to rectify the DR Time synchronization issue at Raichur Station. | KPTCL |  | Pending | Pending
123/VI/8 | 400KV-KAIGA-GUTTUR-2 | 28-08-2024 17:40 | DR TIME SYNC ISSUE | KPTCL to rectify the DR Time synchronization issue at Guttur Station | KPTCL | Puspha:KPTCL: 05/11/2024 18:07:03: The work is awarded by EEE,TL&SS Guttur. Work will be taken up. Puspha:KPTCL: 01/12/2024 23:48:00: Attended on 22.11.2024 Puspha:KPTCL: 17/02/2025 17:15:01: Attended on 22.11.2024 | Complied | Complied
123/VI/11 | 400KV-NELAMANGALA-TALGUPPA-1 | 03-09-2024 05:56 | DR TIME SYNC ISSUE | KPTCL to rectify the DR Time synchronization issue at Talaguppa Station | KPTCL | Puspha:KPTCL: 05/11/2024 18:07:03: SANDS make GPS time sync equipment provided at Talaguppa is faulty and the same is send to repairs at OEM factory at Chennai. Once the device us received time sync problem will be rectifed Puspha:KPTCL: 17/02/2025 17:19:47: After repairs GPS time sync device is put back to service on 30.12.2024 Puspha:KPTCL: 17/02/2025 22:54:52: | Complied | Complied
123/VI/17 | 220KV-AMBEWADI-XELDEM-1 | 15-09-2024 15:13 | DR TIME SYNC ISSUE | KPTCL to rectify the DR Time synchronization issue at Ambewadi Station. | KPTCL | Puspha:KPTCL: 05/11/2024 18:07:03: GPS equipment is provided and it is in working condition at Ambewadi . Time sync issue with few will be rectified | Complied | Complied
124/I/3 | Complete Outage of 220kV/66kV Kolar SS, 220kV/66kV Sarjapura SS, 220kV/66kV Bangarpet SS of KPTCL | 21-09-2024 19:25 | 220kV/66kV Malur SS was operating with split bus condition at 220kV level with 220kV Kolar Kolar_PG line-1&2 radially feeding 220kV Malur Bus-2. 220kV/66kV Sarjapura SS was being radially fed from 220kV Malur Bus-2. 220kV/66kV Bangarpet SS was being radially fed from 220kV/66kV Kolar SS. As per the reports submitted, the triggering incident is the R-Y fault in 220kV Kolar Kolar_PG -1, during which 220kV Kolar Kolar_PG -2 over reached and tripped in Z1 at Kolar_PG only. Tripping of both these lines led to complete outage of 220kV/66kV Kolar SS which inturn led to complete outage of 220kV/66kV Bangarpet SS, 220 Bus-2 of Malur and 220kV/66kV Sarjapura SS. | KPTCL/PGCIL SR-II to expedite to enabling Auto reclosure on 230kV KolarKolar PG D/c | KPTCL | Puspha:KPTCL: 08/12/2024 06:42:40: The work of providing OPGW is under progress, Once OPGW communication link is established AR will be enabled. | Complied | Complied
124/I/3 | Complete Outage of 220kV/66kV Kolar SS, 220kV/66kV Sarjapura SS, 220kV/66kV Bangarpet SS of KPTCL | 21-09-2024 19:25 | 220kV/66kV Malur SS was operating with split bus condition at 220kV level with 220kV Kolar Kolar_PG line-1&2 radially feeding 220kV Malur Bus-2. 220kV/66kV Sarjapura SS was being radially fed from 220kV Malur Bus-2. 220kV/66kV Bangarpet SS was being radially fed from 220kV/66kV Kolar SS. As per the reports submitted, the triggering incident is the R-Y fault in 220kV Kolar Kolar_PG -1, during which 220kV Kolar Kolar_PG -2 over reached and tripped in Z1 at Kolar_PG only. Tripping of both these lines led to complete outage of 220kV/66kV Kolar SS which inturn led to complete outage of 220kV/66kV Bangarpet SS, 220 Bus-2 of Malur and 220kV/66kV Sarjapura SS. | KPTCL to ensure Double Bus configuration at Kolar station. | KPTCL | Puspha:KPTCL: 08/12/2024 06:42:40: To ensure double bus configuration at Kolar R&M work is being taken up. It is in tendering stage, LIO will be issued by CEE,T&P shortly. | Complied | Complied
124/I/3 | Complete Outage of 220kV/66kV Kolar SS, 220kV/66kV Sarjapura SS, 220kV/66kV Bangarpet SS of KPTCL | 21-09-2024 19:25 | 220kV/66kV Malur SS was operating with split bus condition at 220kV level with 220kV Kolar Kolar_PG line-1&2 radially feeding 220kV Malur Bus-2. 220kV/66kV Sarjapura SS was being radially fed from 220kV Malur Bus-2. 220kV/66kV Bangarpet SS was being radially fed from 220kV/66kV Kolar SS. As per the reports submitted, the triggering incident is the R-Y fault in 220kV Kolar Kolar_PG -1, during which 220kV Kolar Kolar_PG -2 over reached and tripped in Z1 at Kolar_PG only. Tripping of both these lines led to complete outage of 220kV/66kV Kolar SS which inturn led to complete outage of 220kV/66kV Bangarpet SS, 220 Bus-2 of Malur and 220kV/66kV Sarjapura SS. | KPTCL to provide Line differential Protection for 230kV Kolar Kolar PG line | KPTCL | Puspha:KPTCL: 08/12/2024 06:42:40: Provision for Line differential protection for Kolar-Kolar lines will be made under R&M works. | Complied | Complied
124/I/3 | Complete Outage of 220kV/66kV Kolar SS, 220kV/66kV Sarjapura SS, 220kV/66kV Bangarpet SS of KPTCL | 21-09-2024 19:25 | 220kV/66kV Malur SS was operating with split bus condition at 220kV level with 220kV Kolar Kolar_PG line-1&2 radially feeding 220kV Malur Bus-2. 220kV/66kV Sarjapura SS was being radially fed from 220kV Malur Bus-2. 220kV/66kV Bangarpet SS was being radially fed from 220kV/66kV Kolar SS. As per the reports submitted, the triggering incident is the R-Y fault in 220kV Kolar Kolar_PG -1, during which 220kV Kolar Kolar_PG -2 over reached and tripped in Z1 at Kolar_PG only. Tripping of both these lines led to complete outage of 220kV/66kV Kolar SS which inturn led to complete outage of 220kV/66kV Bangarpet SS, 220 Bus-2 of Malur and 220kV/66kV Sarjapura SS. | KPTCL to reconductor 230kV Kolar Kolar PG line with HTLS conductor. | KPTCL | Puspha:KPTCL: 08/12/2024 06:42:40: Reconductoring of Kolar-Kolar PGCIL D/c line by Drake equivalent HPC is in tendering stage. | Complied | Complied
124/I/4 | Complete Outage of 220kV Exora SS, 220kV ITI and 220kV Vikas Tech Park SS and Tripping of 220kV Bus-1 of 400kV/220kV Hoody SS of KPTCL | 29-09-2024 17:51 | 400kV/220kV Hoody SS was operating with bus split condition at 220kV level with 220kV Hoody Malur line being the only source. 220kV Exora SS, 220kV ITI and 220kV Vikas Tech Park SS were being radially fed from 220kV Hoody Bus-1. As per the reports submitted, the triggering incident was tripping of 220kV Hoody Malur Line-1 on RN fault. Tripping of the only connected line resulted in outage of 220kV Bus-1 of 400kV/220kV Hoody SS which inturn resulted in complete outage of 220kV Exora SS, 220kV ITI and 220kV Vikas Tech Park SS. | KPTCL to carry out regular maintenance of the station. | KPTCL | Puspha:KPTCL: 08/12/2024 06:42:40: Letter in this regard is communicated to the operational wing concerned. | Complied | Complied
124/I/4 | Complete Outage of 220kV Exora SS, 220kV ITI and 220kV Vikas Tech Park SS and Tripping of 220kV Bus-1 of 400kV/220kV Hoody SS of KPTCL | 29-09-2024 17:51 | 400kV/220kV Hoody SS was operating with bus split condition at 220kV level with 220kV Hoody Malur line being the only source. 220kV Exora SS, 220kV ITI and 220kV Vikas Tech Park SS were being radially fed from 220kV Hoody Bus-1. As per the reports submitted, the triggering incident was tripping of 220kV Hoody Malur Line-1 on RN fault. Tripping of the only connected line resulted in outage of 220kV Bus-1 of 400kV/220kV Hoody SS which inturn resulted in complete outage of 220kV Exora SS, 220kV ITI and 220kV Vikas Tech Park SS. | KPTCL to review the high set over current element for bus sectionalizer protection settings | KPTCL | Puspha:KPTCL: 08/12/2024 06:42:40: At 400/220kV Hoody Substation for the 220kV Buses Bus Bar Protection is provided and it is in service. However, for 220kV buses in Hoody 220/66kV Substation Bus Bar Protection is being provided under R&M works. In view of the above, Bus Sectionaliser high set setting (current pick up 30KA with 100msec time delay ) will be retained. The setting will not overlap with any other protection settings. | Complied | Complied
124/I/5 | Complete Outage of 220/33kV Energon and Tripping of 220kV Bus-1 of 220/110kV Vajramatti SS | 30-09-2024 13:17 | In the antecedent conditions 220/33kV Energon station was radially connected to 220kV Bus-1 of Vajramatti. As per the reports submitted, the triggering incident is the fault in 220kV Bagalkot-Vajramatti-1, the fault was sensed in Z1 and 3ph tripped at Bagalkot end, at Vajramatti end the fault was sensed in Z1 and the breaker failed to open. LBB did not operate at Vajramatti end | KPTCL /NTPC to review the relay settings for all 220kV NTPC- Vajramatti lines | KPTCL | Puspha:KPTCL: 08/12/2024 06:42:40: Zone-2 over reaching is observed at Kudagi NTPC end. 220kV Kudagi NTPC to Vajramatti D/c line is being LILOed at 220kV Bilagi Substation. The modified line lengths due to LILO of these lines at new Bilagi SS is communicated to NTPC Kudagi for calculating revised reaches by NTPC. | Complied | Complied
124/I/8 | Complete Outage of 220/66kV Khodays | 03-10-2024 05:51 | 220/66kV Khodays is equipped with single bus and 2 lines 220kV Somanahalli-Khodays and 220kV Subramanyapura-Khodays. The triggering incident is suspected charging of 220kV Somanahalli-Harohalli on fault, during which 220kV Khodays-Somanhalli tripped at Khodays end on Z2 extension. However, 3ph tripped and closed again within 40 ms which led to the operation of LBB and led to tripping of one and only Bus at Khodays. This led to the Complete Outage of 220/66kV Khodays. | KPTCL to upload the revised User report after rectifying the Summary of the event in SPHOORTI portal | KPTCL | Puspha:KPTCL: 08/12/2024 06:42:40: Revised user report updated in the SRLDC portal. | Complied | Complied
124/IV/1 | 400KV-PAVAGADA_PG-DEVANAHALLI-2 | 25-09-2024 14:57 | As per the reports submitted, the triggering incident was YN fault in the line due to insulator failure at Loc 107. At Pavagada end, the line tripped on operation of Zone-1 distance protection. A/R operated but again the line tripped due to persistent fault. At Devanahalli end the line tripped on operation of Zone-1 distance protection. A/R did not get operated. | KPTCL to furnish the reason for non-availability of the Station SoE of the tripping events | KPTCL | Puspha:KPTCL: 08/12/2024 06:42:40: Station SOE was not available .Additional DRs to clarify AR operation was furnished. | Complied | Complied
124/IV/2 | 400KV-NELAMANGALA-TALGUPPA-1 | 26-09-2024 12:03 | As per the reports submitted, the triggering incident was RN fault in the line. At both ends the line tripped on operation of Zone-1 distance protection. A/R did not get operated at both ends | KPTCL to enable Auto reclosure on 400kV Nelamngala-Talguppa Line -1 | KPTCL | Puspha:KPTCL: 01/12/2024 23:29:56: Line is kept in non auto mode due to insulator replacement pending near Nelamangala limits. Puspha:KPTCL: 08/12/2024 06:42:40: Directions have been given to enable AR with current limit logic at Nelamangala end, the logic will be incorporated and AR scheme will be tested by availing line shut down | Complied | Complied
124/IV/5 | 220KV-SEDAM-TANDUR-1 | 07-10-2024 10:20 | As per the reports submitted, the triggering incident was YN fault in the line. At Sedam end the line tripped on operation of Zone-1 distance protection. A/R not operated and the line tripped on three-phase. At Tandur end the line tripped on operation of Zone-2, time-trip, distance protection. The line tripped on three-phase due to non-receipt of carrier from the remote end | KPTCL to review the non-operation of Auto reclosure at Sedam end. | KPTCL | Puspha:KPTCL: 27/11/2024 23:09:32: operation of I>4 current element used for block Auto reclosure for high fault current operated and hence 3 phase trip issued at Sedam end during the incident. Hence tripping is in order Puspha:KPTCL: 01/12/2024 23:29:56: Tripping is in order. AR was blocked and 3 phase trip issued due to high fault current .. | Complied | Complied
124/VI/1 | 400KV-TALGUPPA-HASSAN-1 | 26-09-2024 12:06 | DR TIME SYNC ISSUE AT HASSAN - 400KV | KPTCL to furnish the action plan taken regarding this event | KPTCL | Puspha:KPTCL: 08/12/2024 06:42:40: Directions have been given to enable AR with current limit logic at Nelamangala end, the logic will be incorporated and AR scheme will be tested by availing line shut down | Complied | Complied
124/VI/2 | 220KV-HOODY-MALUR-1 | 29-09-2024 17:51 | HOODY - 220KV | KPTCL to furnish the action plan taken regarding this event. | KPTCL | Puspha:KPTCL: 08/12/2024 06:42:40: Letter is adressed to CEE,TZ,Bangalore to prioratise line maintainance issues and to prioratise lines in Bangalore city limits for frequent maintainance | Complied | Complied
124/VI/3 | 220KV-VAJRAMATTI-BAGALKOT-2 | 30-09-2024 13:17 | BAGALKOT - 220KV | KPTCL to furnish the action plan taken regarding this event. | KPTCL | Puspha:KPTCL: 10/12/2024 22:26:53: At Vajramatti end problem with the Bagalkot line-1 Circuit Breaker is attended. Problem with LBB protection was rectified at vajramatti substation | Complied | Complied
124/VI/4 | 220KV-BAGALKOT-VAJRAMATTI-1 | 30-09-2024 13:17 | BAGALKOT - 220KV | KPTCL to furnish the action plan taken regarding this event. | KPTCL | Puspha:KPTCL: 10/12/2024 22:26:53: At Vajramatti end problem with the Bagalkot line-1 Circuit Breaker is attended. Problem with LBB protection was rectified at vajramatti substation | Complied | Complied
124/VI/5 | 220KV-BAGALKOT-VAJRAMATTI-1 | 30-09-2024 13:17 | VAJRAMATTI - 220KV | KPTCL to furnish the action plan taken regarding this event | KPTCL | Puspha:KPTCL: 10/12/2024 22:26:53: At Vajramatti end problem with the Bagalkot line-1 Circuit Breaker is attended. Problem with LBB protection was rectified at vajramatti substation | Complied | Complied
124/VI/6 | 220KV-MAHALINGAPURA-VAJRAMATTI-1 | 30-09-2024 13:17 | MAHALINGAPURA - 220KV | KPTCL to furnish the action plan taken regarding this event. | KPTCL | Puspha:KPTCL: 08/12/2024 06:42:40: DC ground issues and issue with non operation of LBB proection at Vajramatti is rectified | Complied | Complied
124/VI/8 | 220KV-SUBRAMANYAPURA-KHODAYS-1 | 03-10-2024 05:51 | KHODAYS - 220KV | KPTCL to furnish the action plan taken regarding this event | KPTCL | Puspha:KPTCL: 10/12/2024 22:26:53: Problem with DC grounding due control cables rectified at Khodays substation | Complied | Complied
124/VI/10 | 220KV-SUBRAMANYAPURA-PEENYA-1 | 09-10-2024 12:48 | PEENYA - 220KV | KPTCL to furnish the action plan taken regarding this event. | KPTCL | Puspha:KPTCL: 08/12/2024 06:42:40: Letter is adressed to CEE,TZ,Bangalore to prioratise line maintainance issues and to prioritize lines in Bangalore city limits for frequent maintainance | Complied | Complied
124/VI/14 | 400KV-DONI-GUTTUR-1 | 17-10-2024 20:26 | DONI - 400KV | KPTCL to furnish the action plan taken regarding this event. | KPTCL | Puspha:KPTCL: 10/12/2024 22:26:53: During the incident at Guttur end due to high fault current logic AR was blocked and 3 phase trip was issued . AT Doni end AR was successful. No visual fault was detected during line inspection | Complied | Complied
125/I/7 | Complete outage of 220kV/66kV Hebbal SS and 220kV/66kV CPRI SS of KPTCL | 01-11-2024 13:11 | During antecedent condition, 220kV Manyatha-Hebbal line was under idle charged condition from Manyatha end. As per the reports submitted, the triggering incident was RY fault in the 220kV Sahakarinagar-Hebbal line. The line tripped at Sahakarinagar end on operation of Zone-2(Time trip) distance protection. Tripping of 220kV Sahakarinagar-Hebbal line resulted in main supply failure to Hebbal 220kV Sub station and CPRI EHT resulting in the complete outage of Hebbal SS. | KPTCL to reduce the time delay for Zone-2 to 100ms for 220kV Sahakarinagar-Hebbal line. | KPTCL | Puspha:KPTCL: 04/01/2025 22:03:34: Directions have been given to review the Zone-2 time delay at Sahakarinagar end (Hebbal line) to 150msec Puspha:KPTCL: 02/02/2025 22:14:08: Attended, Zone-2 delay revised to 150 msec | Complied | Pending
125/I/7 | Complete outage of 220kV/66kV Hebbal SS and 220kV/66kV CPRI SS of KPTCL | 01-11-2024 13:11 | During antecedent condition, 220kV Manyatha-Hebbal line was under idle charged condition from Manyatha end. As per the reports submitted, the triggering incident was RY fault in the 220kV Sahakarinagar-Hebbal line. The line tripped at Sahakarinagar end on operation of Zone-2(Time trip) distance protection. Tripping of 220kV Sahakarinagar-Hebbal line resulted in main supply failure to Hebbal 220kV Sub station and CPRI EHT resulting in the complete outage of Hebbal SS. | KPTCL to take steps to convert Tapping arrangement for supply to CPRI through a proper LILO arrangement. | KPTCL | Puspha:KPTCL: 04/01/2025 22:03:34: The matter is taken up with the higher management | Pending | Pending
125/II/5 | Tripping of 400kV Bus-1 of 400kV/220kV Mylasandra SS of KPTCL | 31-10-2024 08:44 | As per the reports submitted, the triggering incident was maloperation of 86ZT relay (operates when SF6 gas pressure goes low) of main bays of elements connected to 400kV Bus-1. Tripping of all main bays connected to 400kV Bus-1 resulted in loss of power supply to 400kV Bus-1 of 400kV/220kV Mylasandra SS. | KPTCL to furnish the root cause analysis of 86ZT operation in consultation with OEM, and furnish action taken based on their advice. | KPTCL | Puspha:KPTCL: 04/01/2025 22:03:34: EEE, Mylasandra has taken up the matter with the OEM. OEM Reply is awaited. | Pending | Pending
125/II/7 | Tripping of 220kV South East bus of 220kV Sharavathy PH | 11-11-2024 14:27 | As per the reports submitted, the triggering incident was tripping of Sharavathy Unit-3 on loss of excitation. However, LBB operated as the breaker of Unit-3 failed to open tripping all elements connected to the 220kV South East bus of 220kV Sharavathy PH. | KPTCL to rectify the SCADA SoE | KPTCL | Puspha:KPTCL: 04/01/2025 22:03:34: As confirmed by the SCADA wing the issue is rectified | Complied | Complied
126/II/8 | Tripping of 400kV Bus-2 of RTPS of KPCL | 14-12-2024 13:49 | As per the reports submitted, the triggering incident was tripping of 400kV RTPS Bus-2 on operation of BBP due to initiation of LBB trip from Tie breaker of GT-2. This led to tripping of all elements connected to 400kV RTPS Bus-2. | KPCL to enable retrip feature (time delay of 100ms) for LBB operation. | KPCL | EE (E )/CEED:KPCL: 06/02/2025 14:47:44: Planned to takeup works and will be completed by June 2025 EE (E )/CEED:KPCL: 01/03/2025 14:29:11: Few elements have LBB retrip feature and remaining will be done during coming short shtdown for which Hard wiring is also required. For the lines will be completed by June-2025. For Units will be completed by Dec -2025 during OH works EE (E )/CEED:KPCL: 02/07/2025 10:49:07: Few elements have LBB retrip feature and remaining will be done during coming short shtdown for which Hard wiring is also required. Fthe lines and units will be completed by December-2025. EE (E )/CEED:KPCL: 04/08/2025 10:31:39: 02/07/2025 10:49:07: Few elements have LBB retrip feature and remaining will be done during coming short shtdown for which Hard wiring is also required. Fthe lines and units will be completed by December-2025 EE (E )/CEED:KPCL: 30/08/2025 14:55:02: Few elements have LBB retrip feature and remaining will be done during coming short shtdown for which Hard wiring is also required. The lines and units will be completed by December-2025 EE (E )/CEED:KPCL: 04/10/2025 11:44:13: Few elements have LBB retrip feature and remaining will be done during coming short shtdown for which Hard wiring is also required. The lines and units will be completed by December-2025 EE (E )/CEED:KPCL: 04/11/2025 10:04:03: Few elements have LBB retrip feature and remaining will be done during coming short shtdown for which Hard wiring is also required. The lines and units will be completed by December-2025 EE (E )/CEED:KPCL: 04/12/2025 16:42:28: Few elements have LBB retrip feature and remaining will be done during coming short shtdown for which Hard wiring is also required. The lines and units will be completed by December-2025 EE (E )/CEED:KPCL: 04/10/2025 11:44:13: Few elements have LBB retrip feature and remaining will be done during coming short shtdown for which Hard wiring is also required. The lines and units will be completed by December-2025 EE (E )/CEED:KPCL: 01/01/2026 10:09:46: Few elements have LBB retrip feature and remaining will be done during coming short shtdown for which Hard wiring is also required. The lines and units will be completed by MARCH-2026 EE (E )/CEED:KPCL: 03/02/2026 12:02:39: Few elements have LBB retrip feature and remaining will be done during coming short shtdown for which Hard wiring is also required. The lines and units will be completed by MARCH-2026 EE (E )/CEED:KPCL: 05/03/2026 16:09:10: Few elements have LBB retrip feature and remaining will be done during coming short shtdown for which Hard wiring is also required. The lines and units will be completed by MAY-2026 EE (E )/CEED:KPCL: 06/04/2026 09:26:42: Few elements have LBB retrip feature and remaining will be done during coming short shtdown for which Hard wiring is also required. The lines and units will be completed by July-2026 | Pending | Pending
126/III/5 | 400KV/220KV NELAMANGALA-ICT-3 | 29-11-2024 12:00 | In the antecedent condition the 400/220kV ICT-3 was in R,Y and Spare combination as B-phase was out of service. As per the reports submitted, ICT-3 tripped during the operational check in Nitrogen | 1.KPTCL to follow SOP and furnish the revised SOP to SRPC and SRLDC. 2.KPTCL to provide the Station SOE. | KPTCL | Puspha:KPTCL: 05/02/2025 22:21:13: 1). Operation of group relays Events are generated in the BCU, the same will be uploaded in the SRLDC portal. 2). Directions given for isolating the transformer mounted protection DC of spare transformer of the ICT bank while carrying out the work. | Complied | Complied
126/III/7 | 400KV-NARENDRA-GUTTUR-1 | 07-12-2024 21:46 | As per the reports submitted, 400kV Guttur Narendra line-1 tripped only at Guttur end due to PD relay operation. At Narendra end the line was holding. As per the information furnished by Guttur end, troubleshooting was done and found CB DC-2 circuit in CB protection panel wires grounded resulting tripped on PD relay. Tripping of the same requires review. | 1.KPTCL to furnish the detailed information regarding cable replacement works at 400kV Guttur SS. 2.KPTCL to carry out thorough yard cleaning at 400kV Guttur SS. | KPTCL | Puspha:KPTCL: 05/02/2025 22:21:13: 1)Suspected control cables are replaced, Details of Control cables replaced is furnished to SRPC 2) Yard cleaning work is completed | Complied | Complied
127/II/1 | Tripping of 220kV Bus-2 at 220/66kV YERRAANDAHALLI | 19-12-2024 13:58 | In the antecedent conditions, 220/66kV YERRAANDAHALLI is operating in bus split condition at 220kV level, where in 220kV Bus-2 was radially connected to 220kV Yerrahandalli Hosur line. The triggering incident is the R-N fault in the 220kV Yerrahandalli-Hosur line, the line tripped at both ends on Z1 protection. The tripping of the only line connected to Bus-2 led to the tripping of 220kV Bus-2 at 220/66kV YERRAANDAHALLI. | 1.KPTCL to rectify the DR time sync issue at Yerandanahally station. 2.KPTCL to rectify the non-availability of SCADA SOE. 3.KPTCL to put Main-1 relay at Yerraandahalli end in service. 4.KPTCL to replace the electromechanical relay with numerical relay for ICT HV side backup Overcurrent/Earth Fault protection. | KPTCL | Puspha:KPTCL: 04/03/2025 22:24:34: 1. GPS time sync issue is yet to be rectified. 2. Non availability of SCADA SOE is referred to SCADA wing for rectification. Puspha:KPTCL: 09/04/2025 06:36:03: GPS time sync issue will be rectified during visit of M/s GE engineer, expect to complete within this month | Complied | Complied
127/III/1 | 400KV-DONI-GUTTUR-1 | 22-12-2024 09:45 | As per the reports submitted, 400kV Doni-Guttur line-1 tripped only at Guttur end. As per the information furnished by KPTCL, CB TC-1 failed while rectifying TC-1 fuses, TC-2 fuse was removed resulting in DC fail to CB (CB tripped on CTD). Tripping is not in order. | 1.KPTCL to deactivate the CTD for lines. 2.KPTCL to follow SOP during Testing and Maintenance works. | KPTCL | Puspha:KPTCL: 02/03/2025 23:54:12: CTD has been deactivated for all line breakers. To follow SOP during working directions have ben given to the concerned. | Complied | Complied
127/III/6 | 400KV/220KV GUTTUR-ICT-2 | 29-12-2024 20:19 | As per the reports submitted, 400/220kV Guttur ICT-2 tripped on operation of PDR due to DC earth fault. As per the information furnished by KPTCL, it is suspected that trip coil wires grounded extending trip command to Y and B poles further R pole tripped on PDR. Tripping is not in order. | KPTCL to expedite replacement of the faulty cable. | KPTCL | EE (E )/CEED:KPCL: 01/03/2025 14:23:15: As the event 127III/6 doesnot related to KPCL it is requested to modify the utility. Puspha:KPTCL: 04/03/2025 22:24:34: The suspected 10Cx2.5ksqmm control cable is isolated,, for replacement new control cables have to be procured. | Pending | Pending
127/VI/1 | 220KV-YERRAANDAHALLI-HOSUR-1 | 21-12-2024 13:23 | In the antecedent conditions, 220/66kV YERRAANDAHALLI is operating in bus split condition at 220kV level, where in 220kV Bus-2 was radially connected to 220kV Yerrahandalli Hosur line. The triggering incident is the R-N fault in the 220kV Yerrahandalli-Hosur line, at Hosur end, the fault was sensed in Z1 and AR operated and was successful and the line was holding. At Yerrahandalli end the fault was sensed in Z1 and 3ph tripped as AR is disabled. The tripping of the only line connected to Bus-2 only at Yerrahandalli end led to the tripping of 220kV Bus-2 at 220/66kV YERRAANDAHALLI. As per the remarsks submitted by KPTCL, Transient line faultLoad loss of 100MVA Trafo-3 connected to Bus-2: 36MW. | KPTCL to rectify the DR time sync issues at YERRAANDAHALLI SS. | KPTCL | Puspha:KPTCL: 04/03/2025 22:24:34: Yet to be attended | Pending | Pending
127/VI/8 | 400KV/220KV GUTTUR-ICT-2 | 29-12-2024 20:19 | As per the reports submitted, 400/220kV Guttur ICT-2 tripped on operation of PDR due to DC earth fault. As per the information furnished by KPTCL, it is suspected that trip coil wires grounded extending trip command to Y and B poles further R pole tripped on PDR . Tripping is not in order. | KPTCL to rectify the DR time sync issues at Guttur. | KPTCL | Puspha:KPTCL: 04/03/2025 22:24:34: GPS time sync equipment is in healthy working condition at Guttur. ICT-2 bay all numerical relays are time synchronised with GPS clock. Puspha:KPTCL: 09/04/2025 06:28:55: Attended by replacing faulty communication cable | Complied | Complied
127/VI/10 | 220KV-SEDAM-TANDUR-1 | 10-01-2025 00:30 | During antecedent conditon, 220kV Sedam Tandur line-1 was idle charged from sedam end. As per the reports submitted, the triggering incident was BN fault in the line. At Sedam end, the line tripped on operation of Zone-2(time-trip) distance protection. At Tandur end the line was in open condition. Tripping is in order. | KPTCL to rectify the DR time sync issues at Sedam. | KPTCL | Puspha:KPTCL: 04/03/2025 22:24:34: The GPS device is sent to M/s SANDs factory at Chennai Puspha:KPTCL: 09/04/2025 06:31:09: After repairs GPS time sync equipment is restored. | Complied | Complied
128/I/1 | Complete Outage of 220kV Exora SS, 220kV Vikas Tech and Bus-1 outage at 220kV Malur SS of KPTCL | 23-01-2025 13:02 | 220kV Malur SS was operating with split bus condition with 220kV Hoody Malur line feeding 220kV Malur Bus-1. 220kV Exora and 220kV Vikas Tech Park were being radially fed from 220kV Malur Bus-1. As per the reports submitted, the triggering incident was tripping of 220kV Hoody Malur line on operation of Earth fault protection at Malur end for fault in 220kV Hoody Sobha line. Tripping of this line led to loss of power supply to 220kV Malur Bus-1 which intrun led to complete outage of 220kV Exora SS and 220kV Vikas Tech Park. | 1.KPTCL to upload all relevant Disturbance Records (DRs) related to the event in the SPOORTHI Portal for comprehensive analysis and documentation 2.KPTCL to recheck ANY TRIP logic for all relays to ensure correct protection operation and prevent unintended trippings 3.KPTCL to review the logic inbuilt through overcurrent element 4.KPTCL to expedite replacement of PLCC card at Hoody end of 220kV Hoody-Shobha Dreams line | KPTCL | Puspha:KPTCL: 02/04/2025 23:34:12: Hoody Shobha Dreams line DR file uploaded in the SRLDC web portall | Complied | Complied
128/I/2 | Complete Outage of 220kV Exora SS, 220kV Vikas Tech and Bus-1 Outage at 220kV Malur SS of KPTCL | 26-01-2025 10:07 | 220kV Malur SS was operating with split bus condition with 220kV Hoody Malur line feeding 220kV Malur Bus-1. 220kV Exora and 220kV Vikas Tech Park were being radially fed from 220kV Malur Bus-1. As per the reports submitted, the triggering incident was Y-N fault in 220kV Hoody Malur line. Tripping of this line led to loss of power supply to 220kV Malur Bus-1 which intrun led to complete outage of 220kV Exora SS and 220kV Vikas Tech Park. | 1.KPTCL to maintain the Right of Way (ROW) of 220kV Hoody-Malur line and ensure necessary clearance to prevent recurrent tripping due to vegetation interference 2.KPTCL to rectify the DR time synchronisation issue at 220kV Hoody end of 220kV Hoody Malur line 3.Issue of data freezing at Hoody/Malur to be rectified by KPTCL 4.SCADA SoE to be made available at Hoody end by KPTCL 5.Enabling of A/R of radial line to be examined by KPTCL | KPTCL | Puspha:KPTCL: 09/04/2025 06:26:39: Considering frequent line faults due to ROW and jumper cut issues reported repeatedly, the matter is reffered to CEE,Operations Bangalore | Complied | Complied
128/I/6 | Complete Outage of 220kV/66kV Nittur SS of KPTCL | 07-02-2025 14:52 | During antecedent conditions, 220kV Nittur Arasikere was under outage as per SLDC instructions. 220kV/66kV Nittur was being radially fed through 220kV Nittur Neamangala line. As per the reports submitted, the triggering incident was B-N fault in 220kV Nittur Nelamangala line and the line tripped. Tripping of the only connected line led to complete outage of 220kv/66kV Nittur SS. | 1.KPTCL to resolve the non-operation of Auto reclosure at Nittur end 2.KPTCL to resolve the Time Synch issues at Nittur | KPTCL | Puspha:KPTCL: 09/04/2025 06:33:55: During the tripping the line was kept in non auto mode as the substation is being operated radially. Presently kept in auto mode at Nittur end. Regarding GPS time sync issue the matter is being pursued with concerned CEE, Operations | Complied | Complied
128/I/7 | Tripping of 220kV Bus-1 of 400kV/220kV Nelamangala SS, Complete Outage of 220kV/66kV Penya SS,20kV/110kV Nittur SS, 220kV/110kV Anchepalya SS of KPTCL | 11-02-2025 13:42 | As per the reports submitted, the triggering incident was B-N fault in 66kV downstream at Anchepalya. At the same time, 220kV Nelamangala Bus-1 BBP maloperated and all elements connected to 220kV Nelamangala Bus-1 tripped. Tripping of 220kV Bus-1 of 400kV/220kV Nelamangala SS led to complete Outage of 220kV/66kV Penya SS, 20kV/110kV Nittur SS, 220kV/110kV Anchepalya SS of KPTCL | 1.KPTCL to consult with the OEM and implement the necessary modifications to Bus Bar Protection settings by enabling the Central Unit (CU) block function when the Peripheral Unit (PU) is in OFF condition at Nelamangala Substation 2.KPTCL to review the cause for tripping of 220kV/66kV PTR-1 at Anchepalya SS | KPTCL |  | Pending | Pending
128/III/6 | 400KV/220KV TALGUPPA-ICT-1 | 28-01-2025 16:35 | As per the reports submitted, the triggering incident was the tripping of the ICT due to the maloperation of the LV-side overflux relay, resulting in a three-phase trip. However, the V/f plot, as shown below, indicates that there was no significant over flux during the event. | 1.KPTCL to expedite the replacement of static relay with numerical relay | KPTCL | Puspha:KPTCL: 09/04/2025 06:26:39: Procurement action initiated by EEE, Operations Talaguppa | Complied | Complied
128/III/15 | 400KV/220KV TALGUPPA-ICT-2 | As per the reports submitted, 315MVA 400/220kV Talguppa ICT-2 tripped on operation PRV trip as PRV limit switch has failed. Tripping is not in order. | 14-02-2025 09:51 | 1.KPTCL to carry out thorough inspection before re-energizing the equipment | KPTCL | Puspha:KPTCL: 09/04/2025 06:22:22: Necessary precautions and guidelines are given to the substation to follow in future | Complied | Complied
128/IV/5 | 400KV-KAIGA-GUTTUR-2 | 31-01-2025 12:35 | As per the reports submitted, the triggering incident is the B-N fault in the line. At Kaiga end, the fault was sensed in Z1, AR operated and tripped due to persistent fault. At Guttur end, the fault was sensed in Z1 and B-pole opened. However, AR did not operate after the dead time and AR locked out after around 1.1 sec from the fault leading to 3ph trip at Guttur end. | 1.KPTCL to rectify the reason for blocking of A/R operation by Main-2 relay, D60 | KPTCL | Puspha:KPTCL: 09/04/2025 06:20:10: Rectified. Issue with D60 Main-2 relay was referred to M/s GE. As per GE recommendations AR logics are modified and attended | Complied | Complied
128/VI/4 | 220KV-HOODY-MALUR-1 | 26-01-2025 10:07 | As per the reports submitted, 220kV Malur SS was operating with split bus condition with 220kV Hoody Malur line feeding 220kV Malur Bus-1 during antecedent conditions. 220kV Exora and 220kV Vikas Tech Park were being radially fed from 220kV Malur Bus-1. The triggering incident was Y-N fault in 220kV Hoody Malur line at a distance of 6km from Hoody end. A/r is in disabled condition since the line is radial. At Hoody end, line tripped on operation of Zone-1 distance protection. At Malur end, the line was holidng and later hand tripped. Tripping of this line led to loss of power supply to 220kV Malur Bus-1 which intrun led to complete outage of 220kV Exora SS and 220kV Vikas Tech Park | 1.KPTCL to rectify the DR time sync issue at Hoody SS. | KPTCL | Puspha:KPTCL: 09/04/2025 06:18:45: GPS time sync equipment provided under R&M scope is faulty, the matter is being persued with the R&M turn key agency M//s GE Ltd. Expect to attend within a month's time Puspha:KPTCL: 09/04/2025 06:20:56: The matter is being pursued with the agency executed the R&M work of Hoody 220 Puspha:KPTCL: 07/08/2025 21:48:16: The faulty GPS antenna has been replaced. at Hoody Subsation. GPS master clock is lagging. The issue is being resolved by taking online support from OEM Masi Bus | Complied | Complied
129/I/2 | Grid Disturbance in North Karnataka | 19-02-2025 14:01 | At 220kV Narendra_KA SS, during antecedent conditions, isolators of both buses were under closed condition. While carrying out 100MVA Trafo-1 CB dismantling work crane came in arcing zone (B phase) of 220kV Narendra_KA Bus resulting in a BN fault. 220kV Bus zone-1 & 2 operated (since isolators of both buses were in closed condition). This resulted in the tripping of all the elements connected to 220kV Narendra_KA SS. This eventually led to complete outage of 2220kV/110kV Narendra_KA SS, 220kV/110kV Ambewadi SS, 220kV Naghjeri PH, 220kV/ Kanabargi SS, 220kV/110kV Soudatti SS, 220kV/110kV Bidnal SS, 220kV/110kV Hubli SS, 220kV/110kV Belagaum SS, 220kV/110kV Athani SS, 220kV/110kV Kudachi SS, 220kV/110kV Haveri SS, 220kV/66kV Shiggaon SS, 220kV/110kV Mughalkod SS, 220kV/110kV Chikkodi SS, 220kV/110kV Kanagala SS, 220kV/110kV Aequs, 220kV/110kV Indal, 220kV/33kV Tadas SS. | 1.KPTCL to follow SOP while carrying out maintenance works. 2.KPTCL to furnish the reason for Mahaingapura to Soudatti line-2 tripping during the incident. 3.KPTCL to disable the overload/overcurrent protection enabled in their 220kV system. 4.Manual tripping shall be under instruction of SLDC. In case of emergency tripping of feeders should be for relieving of constraints. | KPTCL | Puspha:KPTCL: 07/07/2025 07:21:12: Strict instructions given regarding following SOP while taking uo the work. | Complied | Complied
129/I/3 | Complete Outage of 220kV/66kV Bidadi_KA SS, 220kV Toyota and Tripping of 220kV Bus-2 of 220kV/66kV Somanahalli_KA SS of KPTCL | 20-02-2025 10:52 | During antecedent conditions, 220kV Somanahalli_KA Bidadi_KA line-1 was under outage and there was bus split operation at 220kV Somanahalli_KA SS with 220kV Somanahalli Bus-2 being fed from 220kV Bidadi Somanahalli Line-2. 220kV Toyota is being radially fed from 220kV/66kV Bidadi SS. The triggering incident was 220kV Bus-1 fault at 220kV/110kV Bidadi_KA SS due to failure of isolator rigid bus clamp in 220kV Somanahalli_KA Bidadi_KA line 2 bay. Due to non-operation of 220kV Bus-1 BBP at 220kV/110kV Bidadi_KA SS, the fault was cleared by tripping of 220kV Bidadi connected lines. Tripping of all connected lines led to complete outage of 220kV/66kV Bidadi_KA SS , 220kV Toyota and Tripping of 220kV Bus-2 of 220kV/66kV Somanahalli_KA SS | 1.KPTCL to expedite replacement of the Faulty Busbar protection at 220kV Bidadi SS. 2.KPTCL to ensure compliance of the relevant recommendations of the 98th PCSC meeting during non availability of Bus Bar protection. 3.KPTCL to rectify the DR time sync issues at 220kV Bidadi SS. 4.KPTCL to examine and replace/ strengthen weak structures/conductors etc and carry out hotspot at Bidaai SS. Compliance report may obtained from field. | KPTCL | Puspha:KPTCL: 09/07/2025 22:26:23: 1. BBP replacement is in tedering stage in Corporate office. 2). Reducing reverse zone time delay is not envisaged considering the very short transmission lines from Bidadi 220kV bus 3). GPS time sync unit put back to service after repairs, relay wise time synchronization is to be ensured. 4. No such weak structures available in the 220kV Switchyard | Pending | Pending
129/I/4 | Complete Outage of 220kV/66kV Dobbaspet SS of KPTCL | 21-02-2025 15:10 | During antecedent conditions, 220kV Dobaspet Kadur line was under outage. Hence 220kV Dobaspet SS was radially fed from 400kV/220kV Neelamangala SS. The triggering incident was BN fault in 220kV Dobaspet Neelamangala line and the line tripped. Due to tripping of the only connected line, there was complete loss of supply at 220kV/66kV Dobaspet SS. | 1.KPTCL to maintain the ROW of the 220kV Dobospet- Nelmangala line. 2.KPTCL to rectify DR time syn issuse at 220kV Dobbaspet SS. 3.KPTCL to resolve the non-availability of SCADA SOE at 220kV Dobbaspet SS. 4.KPTCL to rectify PLCC issues 5.KPTCL to furnish reason for non-opertaion of SOTF/TOR at Nelamangala. | KPTCL | EE (E )/CEED:KPCL: 03/05/2025 14:53:56: Issue is related to KPTCL . Hence Utility responsible to changed & followed up with KPTCL. Puspha:KPTCL: 09/07/2025 22:37:50: 1. Will be followed 2. SAS to be restored | Pending | Pending
129/I/6 | Tripping of 220kV Bus-1 of 220kV Infosys Switching Station and Complete Outage of 220kV/66kV Infosys Pooling Station, 220kV//66kV Gowribidanur SS, 220kV/66kV Mittemari SS, 220kV/66kV Sira SS and 220kV/66kV KIADB DBPura SS | 26-02-2025 11:09 | During antecedent conditions, 220kV KIADB DB Pura were under outage. 220kV/66kV Infosys Pooling Station, 220kV/66kV Mittemari SS, 220kV/66kV Sira SS and 220kV/66kV KIADB-DBPura SS were being radially fed from 220kV Bus-1 of 220kV Infosys Switching Station. As per the reports submitted, the triggering incident was R-N fault in 220kV Hiriyur Infosys Line-1. At the same time, 220kV Sira Infosys Line-2, 220kV bus coupler of 220kV Infosys Switching Station and 220kV Madhugiri Gowribidanur line tripped. Tripping of all these lines led to complete outage of 220kV//66kV Gowribidanur SS and radial stations connected to 220kV Bus-1 of 220kV Infosys Switching Station. | 1.KPTCL to furnish the action taken for Infosys - Sira line-2 at Infosys end tripping instantaneously on Zone-3 operation. 2.KPTCL to disable the Earth Fault High set in Buscoupler Breaker. 3.One DR Trigger time is wrong | KPTCL | Puspha:KPTCL: 07/07/2025 07:23:16: 1. Sire-2 tripping at Infosys is suspected due to PSB. The same was ensured through DR transplay, 2), Bus Coupler EF settings is disabled | Complied | Complied
129/I/8 | Complete Outage of 220kV/66kV Chikkamangaluru SS | 04-03-2025 14:57 | 220kV/66kV Chikkamangaluru is radially fed from 220kV MRS Shimoga Chikkamangaluru, 220kV Hassan_PG Chikkamanagaluru. As per the reports submitted,at 14:57hrs, the triggering incident was B-N fault in 220kV MRS Shimoga Chikkamangaluru and the line tripped. At 15:08hrs, YB-N fault was observed in 220kV Hassan_PG Chikkamanagaluru. At Hassan end, the fault was sensed in zone-1. Line was holding at Chikkamanagaluru end. Tripping of the only source led to complete outage of 220kV/66kV Chikkamangaluru SS. | 1.KPTCL to keep A/R in Auto Mode at Chikamagalur end. | KPTCL | Puspha:KPTCL: 07/07/2025 07:24:10: Attended. AR is in service for both the lines at Chikamagalur | Complied | Complied
129/I/10 | Complete Outage of 220kV/66kV Exora SS, 220kV/66kV Vikas Tech and 220kV Bus-1 Outage at 220kV/66kV Malur SS of KPTCL | 06-03-2025 13:10 | 220kV Malur SS was operating with split bus condition with 220kV Hoody Malur line feeding 220kV Malur Bus-1. 220kV/66kV Exora and 220kV/66kV Vikas Tech Park were being radially fed from 220kV Malur Bus-1. As per the reports submitted, the triggering incident was RN fault in 220kV Hoody Malur line. Tripping of this line led to loss of power supply to 220kV Malur Bus-1 which intrun led to complete outage of 220kV Exora SS and 220kV Vikas Tech Park. | 1.KPTCL to rectify the DR time synchronisation issue at 220kV Hoody end in 220kV Hoody Malur line. 2.Compliance report of attending the Kolar- Malur line would be submitted. 3.Feedback to Planning on strengthening the system to be given 4.Possibility of implementin A/r on Kolar-Malur may be looked into 5.KPTCL to revert back, 220kV Hoody Malur data freezing and SCADA SoE not available at Hoody end. | KPTCL | Puspha:KPTCL: 09/07/2025 22:26:23: 1. PO is placed for procurement of new GPS device 2) & 3) Hpody Malur line issues are referred to CEE,TZ,BBangalore for rectification 4). Hoody-malur line pass through densely populated city limits in Bangalore, considering the safety issues AR is not enabled for this S/c line which is presently operating in radial mode | Pending | Pending
129/I/11 | Complete outage of 220kV/66kV Naganathpura SS, 220kV/66kV HSR SS, 220kV/66kV Koramangala SS, 220kV/66kV Nimhans SS of KPTCL | 07-03-2025 13:10 | During antecedent conditions, 220kV EDC Nimhans, 220kV HSR Hoody, 220kV HSR EPIP were under open condition. As per the reports submitted, the triggering incident was RY-N fault in 220kV HSR Mylasandra Line. At HSR end, the fault was sensed in zone-1 and the line tripped immediately. At Naganathpura end, the fault was picked up in zone-3 and the line was holding. At the same time, 220kV Mylasandra HSR line-1 tripped on zone-1 at Mylasandra end. Subsequently, 220kV Mylasandra HSR Line-2 and 220kV Mylasandra Naganathpura lines tripped on zone-2 at Mylasansra end. Tripping of all these lines led to complete outage of 220kV/66kV Naganathpura SS, 220kV/66kV HSR SS, 220kV/66kV Koramangala SS, 220kV/66kV Nimhans SS. | 1.KPTCL to resolve the non-availability of SCADA SOE at Mylasandra, HSR and Naganathapura. | KPTCL | Puspha:KPTCL: 09/07/2025 22:28:00: The matter has been referred to SCADA wing for rectification Puspha:KPTCL: 01/08/2025 21:48:11: The matter is referred to SEE,SCADA through email dt 19th July 2025, The issues are being rectified by SEE<SCADA Puspha:KPTCL: 07/08/2025 21:36:02: Non receipt of SCADA SOE is referred to SCADA wing. In consultation with SRLDC the SCADA SOE not available issues will be resolved. | Pending | Pending
129/I/13 | Complete Outage of 220kV/110kV MK Hubli SS of KPTCL | 11-03-2025 13:43 | 220kV/110kV MK Hubli SS is radially fed from 400kV/220kV Narendra_PG SS. Triggering incident was RY fault in 220kV MK Hubli Narendra_PG line-1 and 2 at a distance of 4.8km from Narendra_PG end due to fire under tower no. 19 and 20. Tripping of both connected lines resulted in the complete outage of 220kV/110kV MK Hubli SS. | 1.KPTCL to rectify DR time synch issues at 220kV MK Hubli SS. 2.KPTCL TL to sensitise the farmers on the ROW. | KPTCL | Puspha:KPTCL: 09/07/2025 22:29:14: 1). Due to problem with SIFANG SAS GPS time synchronization of relays not available at present. Action is being taken for restoration of SIFANG SAS at MK Hubli Puspha:KPTCL: 02/09/2025 22:19:14: Action is being taken by EEE,Operations Division Belgaum for replacement of faulty GPS equipment provided along with SIFANG SAS Puspha:KPTCL: 15/09/2025 22:57:42: Action taken by EEE,Operations Belgaum for replacement of faulty GPS equipment by procuring the new one Puspha:KPTCL: 07/11/2025 22:27:12: Yet to be completed Puspha:KPTCL: 03/02/2026 15:07:08: 1. For new GPS PO is placed to M/s SANDs 2. Communicated to concerned field officers Puspha:KPTCL: 03/02/2026 15:15:18: New GPS time synchronising equipment has been provided at MK Hubli Substation, OEM viisit awaited for installation and commissioning. After put in to service it will be updated to SRPC | Pending | Pending
129/II/2 | Tripping of 220kV Bus-2 of Narendra_PG SS of PGCILSR-2 | 12-03-2025 07:26 | As per the reports submitted, the triggering incident was maloperation of LBB initiation in 211 bay (corresponds to 220kV Narendra MK Hubli-1) line due to auxillary relay (21.2 relay) maloperation. After 200ms, LBB trip operated and all elements connected to 220kV Narendra Bus-2 tripped. | 1.KPTCL to enable retrip for LBB operation MK Hubli Line 1&2 2.KPTCL to enable DT for LBB operation for MK Hubli Line 1&2 | KPTCL | Puspha:KPTCL: 09/07/2025 22:31:58: 1. Required support is being extended to Powergoid Narendra SS in this regard 2). Once OPGW link is established DT will be configured for LB/Busbar operation | Pending | Pending
129/IV/12 | 400KV-KAIGA-GUTTUR-2 | 10-03-2025 20:53 | As per the reports submitted, the triggering incident was RN fault in the line. At Kaiga end, the line tripped on operation of Zone-1 distance protection. A/R operated successfully and the line was holding. At Guttur end, the line tripped on operation of Zone-1 distance protection. A/R didnt get operated due to suspected relay issue. Tripping needs review. | 1.KPTCL to furnish the reason for unsuccessful A/R. 2. KPTCL to rectify the DR time sync issues. | KPTCL | Puspha:KPTCL: 07/07/2025 07:26:28: AR issue of D60 relay is resolved in consultation with OEM, kept under observation | Complied | Complied
129/V/1 | 400KV-NELAMANGALA HASSAN-1 | 01-03-2025 15:40 | As per the reports submitted, the triggering incident was BN fault in the line due to vegetation fire between location no 935 & 936 near Bhavikere village limits. At Nelamnagala end, the line tripped on operation of Zone-1 distance protection. At Hassan end, the line tripped on operation of Zone-2, time-trip, protection due to non receipt of carrier from the remote end. A/R kept in Non-Auto mode (since last 1 year) due to multiple trippings in the line. Tripping needs review. | KPTCL to rectify the PLCC channels. | KPTCL | Puspha:KPTCL: 09/07/2025 22:30:02: PLCC healthiness is checked and found to be OK for 400kV Nelamangala Hassan Line Puspha:KPTCL: 07/08/2025 21:53:11: Attended | Complied | Complied
129/VI/5 | 220KV-DOBBASPET-NELAMANGALA-1 | 21-02-2025 15:10 | During antecedent conditions, 220kV Dobaspet Kadur line was under outage. Hence 220kV Dobaspet SS was radially fed from 400kV/220kV Neelamangala SS. The triggering incident was BN fault in 220kV Dobaspet Neelamangala line and the line tripped. Due to tripping of the only connected line, there was complete loss of supply at 220kV/66kV Dobaspet SS | KPTCL to rectify the DR time sync issues at Dobbaspet SS. | KPTCL | Puspha:KPTCL: 09/07/2025 22:33:08: Due to problem with the existing SAS DR time sync issue is present, restoration of SAS is under progress | Pending | Pending
129/VI/12 | 220KV-HOODY-MALUR-1 | 06-03-2025 13:10 | 220kV Malur SS was operating with split bus condition with 220kV Hoody Malur line feeding 220kV Malur Bus-1. 220kV/66kV Exora and 220kV/66kV Vikas Tech Park were being radially fed from 220kV Malur Bus-1. As per the reports submitted, the triggering incident was RN fault in 220kV Hoody Malur line. Tripping of this line led to loss of power supply to 220kV Malur Bus-1 which intrun led to complete outage of 220kV Exora SS and 220kV Vikas Tech Park. | KPTCL to rectify the DR time sync issues at Hoody SS. | KPTCL | Puspha:KPTCL: 07/07/2025 07:25:28: PO placed for new GPs unit , supply awaited Puspha:KPTCL: 04/12/2025 16:13:14: As verified by the OEM earlier the PO was placed and new antenna was procured. While commissioning the same by OEM it was found that it is not compatible for the GPS unit. Hence action has been taken to purchase the compatible GPS unit from the OEM. Puspha:KPTCL: 04/12/2025 17:13:15: As verified by the OEM earlier the PO was placed and new antenna was procured. While commissioning the same by OEM it was found that it is not compatible for the GPS unit. Hence action has been taken to purchase the compatible GPS unit from the OEM. | Pending | Pending
129/VI/21 | 220KV-NARENDRA-M K HUBLI-1 | 11-03-2025 13:43 | 220kV/110kV MK Hubli SS is radially fed from 400kV/220kV Narendra_PG SS. Triggering incident was RY fault in 220kV MK Hubli Narendra_PG line-1 and 2 at a distance of 4.8km from Narendra_PG end due to fire under tower no. 19 and 20. Tripping of both connected lines resulted in the complete outage of 220kV/110kV MK Hubli SS. | KPTCL to rectify the DR time sync issues at MK Hubli SS. | KPTCL | Puspha:KPTCL: 09/07/2025 22:34:12: GPS time synch issue is due to problem with the SIFANG SAS will be rectified | Pending | Pending
129/VI/27 | 220KV-KADAKOLA-KANIYAMPETTA | 16-03-2025 19:32 | As per the reports submitted, the triggering incident as a high resistance R-N fault in the line. At Kadakola end, the fault was sensed in zone-1. A/R operated and the line tripped on persistant fault. Though no delayed fault clearance is observed in the line, the fault behaviour at Kaniyampetta could not be analysed as the DR submitted is not clear. | KPTCL to furnish the action taken report. | KPTCL | Puspha:KPTCL: 09/07/2025 22:35:46: It is TOR for Karnataka end, tripping is in order for Karnataka, Observations to be attended by KSEB | Pending | Pending
130/I/2 | Complete Outage of 220kV/66kV Yerrandahally SS, 220kV/66kV Jigani SS, 220kV/66kV Electronic City SS | 14-03-2025 12:15 | The triggering incident was R-N fault in 220kV Somanahally Mylasandra Line-1 and the line tripped. After 3S, R-N fault was observed in 220kV Somanahally Electronic city line and the line tripped. Subsequently, 220kV Somanahlly Mylasandra Line-2 and 220kV Electronic city Shobha dreams lines tripped on over loading. Tripping of all these lines led to loss of power supply to 220kV/66kV Yerrandahally SS, 220kV/66kV Jigani SS, 220kV/66kV Electronic City SS. | 1.KPTCL to rectify the DR time sync issue at Somanahalli, Keonics, Sobha Dreams SS. 2.KPTCL to plan and implement SPS at Mylasandra SS. 3.KPTCL to ensure proper ROW clearances for lines emanating from Somanahalli and Mylasandra stations. | KPTCL | Puspha:KPTCL: 07/07/2025 07:27:09: Somanahally DR time sync issue attended on 3.7.2025 | Complied | Complied
130/I/3 | Complete Outage of 220kV/66kV Yerrandahally SS, 220kV/66kV Jigani SS, 220kV/66kV Electronic City SS | 15-03-2025 12:42 | 220 kV Somanahalli - Mylasandra line 1 & 2 tripped at 12:42 Hrs and 12:45 hrs respectively at both ends on Distance Protection relay Along with that Somanahalli - Khodays and Somanahalli- Keonics City line tripped at 12:45 hrs and 12:46 hrs on Distance Protection relay. | 1.KPTCL to ensure ROW for lines passing through Khodays area. 2.KPTCL to inspect Shobha Dreams and Keonics SS and submit compliance report in respect of protection and communication issues to SRPC. | KPTCL | Puspha:KPTCL: 09/07/2025 23:02:14: PSAG -01 compliance is furnished to SRPC on 05.07.2025 through Email dated 5th July 2025 | Complied | Complied
130/I/5 | Complete Outage of 220kV/66kV Exora SS, 220kV/66kV Vikas Tech and 220kV Bus-1 Outage at 220kV/66kV Malur SS of KPTCL | 19-03-2025 14:09 | 220kV Malur SS was operating with split bus condition with 220kV Hoody Malur line feeding 220kV Malur Bus-1. 220kV/66kV Exora and 220kV/66kV Vikas Tech Park were being radially fed from 220kV Malur Bus-1. As per the reports submitted, the triggering incident was RN fault in 220kV Hoody Malur line. Tripping of this line led to loss of power supply to 220kV Malur Bus-1 which intrun led to complete outage of 220kV Exora SS and 220kV Vikas Tech Park. | 1.KPTCL to rectify the DR tiem sync issue at 220kV Hoody SS 2.KPTCL to rectify the SCADA SoE at Hoody end. | KPTCL | Puspha:KPTCL: 09/07/2025 22:39:37: 1). PO has been placed for procurement of new GPS unit 2. The matter is referred to SCADA wing for rectification Puspha:KPTCL: 07/08/2025 21:54:10: EEE, Operations Narendra is coordinating with Powergrid for arranging Line outage. Wiring modifications will be done byb Powergrid Puspha:KPTCL: 03/09/2025 22:52:25: The faulty GPS antenna has ben replace by new one. To rectify the problem with GPS clock deputation of Masibus service person is awaited | Complied | Complied
130/I/9 | Complete Outage of 220kV/66kV Nagnatpura SS of KPTCL | 28-03-2025 17:59 | The triggering incident was 66kV side RYB CT failure in 66kV/11kV Transformer-1 at 220kV/66/11kV Nagnatpura SS. During the fault, 150MVA 220/66kV PTR-2 tripped on Over Current protection (as per FIR) and it is suspected that 220/66kV PTR-1 failed to trip and isolate the fault leading to the feeding of the fault for around 10s until 220kV remote line tripped at remote ends on suspected DEF protection operation. This led to the Complete Outage of 220kV/66kV Nagnatpura SS of KPTCL | 1.KPTCL to contact OEM ascertain why the faut was not sensed by PTR-1 and furnish the findings. 2.KPTCL to rectify the SCADA SOE issues at Mylasandra and HSR SS | KPTCL | Puspha:KPTCL: 09/07/2025 23:01:02: Compliance report is submitted to SRPC/SRLDC through email dated 18.05.2025 | Complied | Complied
130/I/11 | Complete Outage of 220kV/66kV Khodays SS and 220kV/66kV Subramanyapura SS of KPTCL | 04-04-2025 10:15 | 220kV/66kV Khodays and 220kV/66kV Subramanyapura SS were being radially fed through 220kV Somanahally Khodays and 220kV Subramanyapura Penya. As per the reports submitted, the triggering incident was R-N fault in 220kV Somanahally Khodays line at a distance of 3km from Somanahally end at 10:16hrs due to jumper cut. At Somanahalli end, zone-1 protection operated and the line tripped. At Khodays end, zone-2 protection operated and the line tripped with a delay of approx 320ms. The line tripped at both ends and A/R did not operate. At 12:46hrs, a YB-n fault was observed in 220kV Subramanyapura Penya line due to entry of tree branches into arc zone of the line. At Subramanyapura end, the fault was sensed in zone-1 and the line tripped. Tripping of both lines led to complete outage of 220kV/66kV Khodays and 220kV/66kV Subramanyapura SS of KPTCL. | 1.KPTCL to ensure proper ROW for Subramanyapura Peenya line 2.KPTCL to rectify the Carrier signal issue for Somanahally Khodays line 3.KPTCL to recity the DR time sync issue at Khodays and Somanahalli SS. | KPTCL | Puspha:KPTCL: 09/07/2025 22:58:37: 1). The matter is referred to TLI wing 2. Carrier issue of 220kV Somanahally-Khodays has been rectified | Complied | Complied
130/II/1 | Tripping of 220kV Bus-1 of Hubli | 18-03-2025 05:47 | The triggering incident is the B-ph jumper failure on the 220kV Hubli-Bidnal line-1 line between CT and wave trap which led to Z1 fault at Bidnal and a Z2 fault at Hubli end. The fault at Bidnal resulted in a 3-phase trip, while at Hubli, the absence of carrier signal led to a Z2 time trip. Duringthe same time Bus-1 BBP tripped at Hubli, which led to the Tripping of 220kV Bus-1 of Hubli | 1.KPTCL to standardize the DR as per FOLD recommendations. 2.KPTCL to consult OEM regarding the BUSBAR operation at SRS Hubli SS. 3.KPTCL to rectify the DR time sync issue at Hubli SS 4.KPTCL to install LDP for 220kV Hubli-Bidnal-1& 2 | KPTCL | Puspha:KPTCL: 09/07/2025 23:03:05: 2. As per OEM recommendations BBP settings are reviewed at SRS Hubli Substation | Complied | Complied
130/II/2 | Tripping of 400kV Bus-2 of 400kV YTPS of KPCL | 03-04-2025 00:10 | Triggering incident was BN fault in 400kV YTPS BPS line-1. At BPS end, fault was sensed in Zone-1. At YTPS end, the fault was sensed in Zone-2 and carrier was received. Due to non-opening of B-pole 411 CB of BPS line-1 which was connected to Bus-2, LBB operated resulting in the tripping of all the main breakers of Bus-2. This resulted in loss of power supply to 400kV Bus-2 of YTPS generating station. | KPTCL to rectify the SCADA SOE issues at at 400kV BPS | KPTCL | Puspha:KPTCL: 09/07/2025 22:56:51: The matter is referred to SCADA wing for rectification | Complied | Complied
130/III/2 | 220KV-SEDAM- TANDUR-1 | 22-03-2025 13:52 | As per the reports submitted, the triggering incident is the tripping of the line during the retrofitting Annunciator window to 220kV Tandur line C& R panel at 220kV Sedam station | KPTCL to follow SOP. | KPTCL | Puspha:KPTCL: 07/07/2025 07:28:13: Clear instructions are given to field officers concerned | Complied | Complied
130/III/4 | 400KV/220KV TALGUPPA-ICT-1 | 25-03-2025 15:11 | As per reports submitted, the triggering incident is the PRV maloperation of 400/220kV 315MVA ICT-1 due to rain water entering into the broken marshalling box Causing the transformer trip. | KPTCL to ensure the healthiness of the other ICT marshalling boxes | KPTCL | Puspha:KPTCL: 07/07/2025 07:39:41: Atttended | Complied | Complied
130/III/7 | 220 kV-Yerraandahalli- Hosur-1 | 03-04-2025 23:45 | As per the reports furnished, during antecedent conditions the line was under idle charged condition from Yerrandahalli end. Triggering incident was YN fault in the line at a distance of 0.9km from Yerrandahalli end. At Yerrandahalli end, line tripped on operation of Zone-1 distance protection and A/R not operated. At the same time, 100MVA 220kV/66kV Transformer3 Yerandahally end tripped on operation of HV side high set EF protection and the same needs review. List of elements tripped during the event: 220kV-Yerandahalli-Hosur-1 and 100MVA 220kV/66kV Transformer3 Yerrandahalli. | KPTCL to submit the DR of the incident | KPTCL |  | Pending | Pending
130/III/11 | 400KV-Talaguppa- Hassan-1 | 05-04-2025 19:45 | As per the reports submitted, the triggering incident was operation of Over stage-1 protection at Talaguppa end and DT was received at Hassan end. The line tripped at both ends. From the DR at Talaguppa end, the voltages observed are Vr-266.0, Vy-135.0, and Vb-145.0. The significant difference of voltage between and R-phase and other phases need review. | KPTCL to the check the healthiness of the R &B Phase CVTs as well | KPTCL | Puspha:KPTCL: 07/07/2025 07:56:37: R&B phase CVTs are checked and found to be healthy. Y phase CVT replaced by new CVT Puspha:KPTCL: 01/08/2025 21:45:12: Attended. SRPC is requested to close the recommendation | Complied | Complied
130/IV/9 | 400KVGUTTURBTPS- 1 | 03-04-2025 00:22 | As per the reports furnished, the triggering incident was YN fault in the line at a distance of 102km from Guttur end and 50km from BTPS end due to insulator decapping. At Guttur end, fault was sensed in Zone-1, and A/R was not operated due to a carrier fail condition. At BTPS end, A/R operated and line tripped even though the fault was not persistent after reclose. Non-operation of A/R at Guttur end and operation of A/R lockout without persistent fault at BTPS end need review. | 1.KPCL to review Operation of A/R lockout. 2. KPTCL to review Non-operation of A/R at Guttur end. | KPTCL | Puspha:KPTCL: 07/07/2025 07:36:50: DC grounding issues in the CRP are attended at Guttur end | Complied | Complied
130/IV/14 | 400KVHEBBANAHALLIUPCL- 1 | 08-04-2025 15:19 | As per the reports submitted, the triggering incident was a slow developing B-n fault in the line. At both ends, the fault was sensed in zone-1. At Hebbanahalli end, A/R did not operate and the line tripped. At UPCL end, A/R operated and the line was holding. Non operation of A/R at Hebbanahalli ends need review. | KPTCL to review the non-operation of A/R at Hebbanahalli end. | KPTCL | Puspha:KPTCL: 09/07/2025 22:56:03: Attended , PLCC healthiness has been checked and found to be healthy | Complied | Complied
130/IV/19 | 400KVKALABURAGIYTPS- 2 | 18-04-2025 14:51 | As per the reports submitted, the triggering incident is the R-N fault in the line. At YTPS end, the fault was sensed in Z1, AR did not operate and 3ph trip. At Kalaburgi end, the fault was sensed in Z2 carrier aided trip AR operated and was successful and the line was holding. | 1.KPTCL to review the non-availability of SCADA SOE at Kalaburgi end 2.KPCL to review the non-operation of AR at YTPS end. | KPTCL | Puspha:KPTCL: 09/07/2025 22:55:25: 1. Regarding SCADA SOE the matter is referred to SCADA wing for rectification Puspha:KPTCL: 07/08/2025 21:39:16: Resolved. Kalaburgi SOE is available. The same has been verified by SRLDC also | Complied | Complied
130/VI/5 | 220KV-SEDAM-TANDUR-1 | 22-03-2025 13:50 | DR time synchronization was not observed at SEDAM - 220KV | KPTCL to resolve the time synchronization issue | KPTCL | Puspha:KPTCL: 09/07/2025 23:03:39: Will be rectified Puspha:KPTCL: 07/08/2025 21:37:15: GPS equipment is in healthy condition. Network issue will be resolved by taking online support of M/s Kalkitech | Complied | Complied
130/VI/11 | 400KV-GUTTUR-BTPS-1 | 25-03-2025 19:13 | DR Time Synchronization issue at GUTTUR - 400KV | KPTCL to resolve the time synchronization issue | KPTCL | Puspha:KPTCL: 06/07/2025 23:13:39: GPS time sync of relays is ensured at Guttur except few old version relays. Puspha:KPTCL: 02/09/2025 22:16:45: At Guttur time sync is working fine | Complied | Complied
130/VI/14 | 220KV-SOMANAHALLI-KHODAYS-1 | 04-04-2025 10:15 | DR Time Synchronization issue at SOMANAHALLI - 220KV | KPTCL to resolve the time synchronization issue | KPTCL | Puspha:KPTCL: 06/07/2025 23:12:51: GPS time sync issue at Somanahally is attended on 03.07.2025 | Complied | Complied
130/VI/27 | 400KV-KAIGA-GUTTUR-2 | 19-04-2025 23:55 | DR time synchronization issue at GUTTUR - 400KV | KPTCL to resolve the time synchronization issue | KPTCL | Puspha:KPTCL: 09/07/2025 22:54:10: GPS time synchronization is healthy at Guttur, Only few old version relays have problem Puspha:KPTCL: 07/08/2025 21:38:09: GPS time synchronisation for protection relays is in healthy condition at Guttur except few old version relays | Complied | Complied
131/I/1 | Complete Outage 2220kV/66kV Kanabargi SS, 220kV/66kV Belagavi SS, 220kV/66kV Indal SS, 220kV/66kV Aques SS, 220kV/66kV Kanagala SS, 220kV/110kV Chikodi SS, 220kV/66kV Mugalkod SS, 220kV/66kV Ghataprabha SS, 220kV/66kV Kudachi SS, 220kV/66kV Athani SS of KPTCL | 15-04-2025 14:42 | During antecedent conditions, 2220kV/66kV Kanabargi SS, 220kV/66kV Belagavi SS, 220kV/66kV Indal SS, 220kV/66kV Aques SS, 220kV/66kV Kanagala SS, 220kV/66kV Chikodi SS, 220kV/66kV Mugalkod SS, 220kV/66kV Ghataprabha SS, 220kV/66kV Kudachi SS, 220kV/66kV Athani SS are being radially fed from 220kV Narendra Kanabargi Line-1&2, 220kV Narendra Ghataprabha Line-1&2, 220kV Mahalingapura Kudachi, 220kV Mahalingapura Athani. The triggering incident was RY-N fault in 220kV Narendra Kanabargi Line-2. After this, 220kV Narendra Kanabargi Line-1, 220kV Narendra Ghataprabha Line-2, 220kV Mahalingapura Kudachi, 220kV Mahalingapura Athani tripped on over loading and 220kV Narendra Ghataprabha Line-1 tripped on R-N fault. Tripping of lines led to cimplete outage of 2220kV/66kV Kanabargi SS, 220kV/66kV Belagavi SS, 220kV/66kV Indal SS, 220kV/66kV Aques SS, 220kV/66kV Kanagala SS, 220kV/66kV Chikodi SS, 220kV/66kV Mugalkod SS, 220kV/66kV Ghataprabha SS, | 1. KPTCL to replace all the 600/1CTs with 1200/1 CTs | KPTCL | Puspha:KPTCL: 06/07/2025 23:03:34: At Narendra replacement of Main-1 relay work has been taken up. Along with relay replacement CT ratio is being enhanced to 800/1 or 1200/1. Work completed for Hubli 1 &2 lines. Waiting for y of shut down opportunity Puspha:KPTCL: 02/09/2025 22:13:11: Attended. At Narendra Substation, Kanabargi D/c line CT ratio has been enchancced from 600/1 to 1200/1 Puspha:KPTCL: 15/09/2025 22:56:11: Attended and complied CT ratio changed at Narendra end | Complied | Complied
131/I/1 | Complete Outage 2220kV/66kV Kanabargi SS, 220kV/66kV Belagavi SS, 220kV/66kV Indal SS, 220kV/66kV Aques SS, 220kV/66kV Kanagala SS, 220kV/110kV Chikodi SS, 220kV/66kV Mugalkod SS, 220kV/66kV Ghataprabha SS, 220kV/66kV Kudachi SS, 220kV/66kV Athani SS of KPTCL | 15-04-2025 14:42 | During antecedent conditions, 2220kV/66kV Kanabargi SS, 220kV/66kV Belagavi SS, 220kV/66kV Indal SS, 220kV/66kV Aques SS, 220kV/66kV Kanagala SS, 220kV/66kV Chikodi SS, 220kV/66kV Mugalkod SS, 220kV/66kV Ghataprabha SS, 220kV/66kV Kudachi SS, 220kV/66kV Athani SS are being radially fed from 220kV Narendra Kanabargi Line-1&2, 220kV Narendra Ghataprabha Line-1&2, 220kV Mahalingapura Kudachi, 220kV Mahalingapura Athani. The triggering incident was RY-N fault in 220kV Narendra Kanabargi Line-2. After this, 220kV Narendra Kanabargi Line-1, 220kV Narendra Ghataprabha Line-2, 220kV Mahalingapura Kudachi, 220kV Mahalingapura Athani tripped on over loading and 220kV Narendra Ghataprabha Line-1 tripped on R-N fault. Tripping of lines led to cimplete outage of 2220kV/66kV Kanabargi SS, 220kV/66kV Belagavi SS, 220kV/66kV Indal SS, 220kV/66kV Aques SS, 220kV/66kV Kanagala SS, 220kV/66kV Chikodi SS, 220kV/66kV Mugalkod SS, 220kV/66kV Ghataprabha SS, | 2. KPTCL to replace old Main 1 relays with new relays having A/R enable function. | KPTCL | Puspha:KPTCL: 07/07/2025 07:31:25: Replacement of old version main-1 relays are in progress, work completed for Hubli lines. Puspha:KPTCL: 02/09/2025 22:13:11: Attended. At Narendra end M1 relays of Kanabargi lines have been replaced by ZIV make numerical distance relays Puspha:KPTCL: 15/09/2025 22:56:11: Attended and compiled | Complied | Complied
131/I/1 | Complete Outage 2220kV/66kV Kanabargi SS, 220kV/66kV Belagavi SS, 220kV/66kV Indal SS, 220kV/66kV Aques SS, 220kV/66kV Kanagala SS, 220kV/110kV Chikodi SS, 220kV/66kV Mugalkod SS, 220kV/66kV Ghataprabha SS, 220kV/66kV Kudachi SS, 220kV/66kV Athani SS of KPTCL | 15-04-2025 14:42 | During antecedent conditions, 2220kV/66kV Kanabargi SS, 220kV/66kV Belagavi SS, 220kV/66kV Indal SS, 220kV/66kV Aques SS, 220kV/66kV Kanagala SS, 220kV/66kV Chikodi SS, 220kV/66kV Mugalkod SS, 220kV/66kV Ghataprabha SS, 220kV/66kV Kudachi SS, 220kV/66kV Athani SS are being radially fed from 220kV Narendra Kanabargi Line-1&2, 220kV Narendra Ghataprabha Line-1&2, 220kV Mahalingapura Kudachi, 220kV Mahalingapura Athani. The triggering incident was RY-N fault in 220kV Narendra Kanabargi Line-2. After this, 220kV Narendra Kanabargi Line-1, 220kV Narendra Ghataprabha Line-2, 220kV Mahalingapura Kudachi, 220kV Mahalingapura Athani tripped on over loading and 220kV Narendra Ghataprabha Line-1 tripped on R-N fault. Tripping of lines led to cimplete outage of 2220kV/66kV Kanabargi SS, 220kV/66kV Belagavi SS, 220kV/66kV Indal SS, 220kV/66kV Aques SS, 220kV/66kV Kanagala SS, 220kV/66kV Chikodi SS, 220kV/66kV Mugalkod SS, 220kV/66kV Ghataprabha SS, | 3. KPTCL/KAR SLDC to implement SPS with in a month. Remove all O/C settings for lines. | KPTCL | Puspha:KPTCL: 06/07/2025 23:10:01: Directions have been given to disable SPS for 220kV lines by implementing SPS based on operation study results Puspha:KPTCL: 07/08/2025 21:44:14: SPS required for load reduction at Kudachi, Athani and other connected substations are implemented and OCR for 220kV lines has been disabled Puspha:KPTCL: 15/09/2025 22:56:11: Disabling OCR for 220kV lines is in progress, few SPS are proposed for this purpose. The details will be submitted to OCC for approval Puspha:KPTCL: 04/10/2025 20:03:42: Under progress Puspha:KPTCL: 06/01/2026 22:02:57: OC settings for all 220kV lines have disabled in this area Puspha:KPTCL: 06/01/2026 22:09:21: Attended, SPS required for disabling OCR for connected 220kV lines have been implemented | Complied | Complied
131/I/1 | Complete Outage 2220kV/66kV Kanabargi SS, 220kV/66kV Belagavi SS, 220kV/66kV Indal SS, 220kV/66kV Aques SS, 220kV/66kV Kanagala SS, 220kV/110kV Chikodi SS, 220kV/66kV Mugalkod SS, 220kV/66kV Ghataprabha SS, 220kV/66kV Kudachi SS, 220kV/66kV Athani SS of KPTCL | 15-04-2025 14:42 | During antecedent conditions, 2220kV/66kV Kanabargi SS, 220kV/66kV Belagavi SS, 220kV/66kV Indal SS, 220kV/66kV Aques SS, 220kV/66kV Kanagala SS, 220kV/66kV Chikodi SS, 220kV/66kV Mugalkod SS, 220kV/66kV Ghataprabha SS, 220kV/66kV Kudachi SS, 220kV/66kV Athani SS are being radially fed from 220kV Narendra Kanabargi Line-1&2, 220kV Narendra Ghataprabha Line-1&2, 220kV Mahalingapura Kudachi, 220kV Mahalingapura Athani. The triggering incident was RY-N fault in 220kV Narendra Kanabargi Line-2. After this, 220kV Narendra Kanabargi Line-1, 220kV Narendra Ghataprabha Line-2, 220kV Mahalingapura Kudachi, 220kV Mahalingapura Athani tripped on over loading and 220kV Narendra Ghataprabha Line-1 tripped on R-N fault. Tripping of lines led to cimplete outage of 2220kV/66kV Kanabargi SS, 220kV/66kV Belagavi SS, 220kV/66kV Indal SS, 220kV/66kV Aques SS, 220kV/66kV Kanagala SS, 220kV/66kV Chikodi SS, 220kV/66kV Mugalkod SS, 220kV/66kV Ghataprabha SS, | 4. KPTCL to rectify the DR Time synch issues 5. KPTCL to implement A/R functionality in all the lines. | KPTCL | Puspha:KPTCL: 09/07/2025 22:46:53: For enabling AR, action has been taken for replacing old version Main-1 relay wherever necessary. 2). AR issue of Bagewadi-Nandihal and Narendra PG -Gataprabha has been rectified and AR is put back to service | Complied | Complied
131/I/2 | North Karnataka Complete Outage | 16-04-2025 13:36 | The triggering incident is at 13:36:43.120 with the tripping of the 220kV BagewadiNandihal2 line due to a fault. | Karnataka SLDC to give instructions to all the Substation Operators to avoid hand tripping of the 220kV and above lines | KPTCL | Puspha:KPTCL: 06/07/2025 23:04:59: Directions are given to connected substations to identify 110kV loads to be tripped during contingency instead of tripping of 220kV grid lines | Complied | Pending
131/I/2 | North Karnataka Complete Outage | 16-04-2025 13:36 | The triggering incident is at 13:36:43.120 with the tripping of the 220kV BagewadiNandihal2 line due to a fault. | Karnataka SLDC to identify suitable 110kV lines for load shedding during overloading conditions | KPTCL | Puspha:KPTCL: 09/07/2025 22:42:34: Action has been taken to identify 110kV loads to be tripped in case of contingency. A letter is issued to CEE,TZ, Bagalkot in this regard Puspha:KPTCL: 07/08/2025 21:57:41: For over loading of 220kV lines, SPS has been implemented . Directions given to follow SOP to trip 110kV loads in case of contingencies | Complied | Pending
131/I/2 | North Karnataka Complete Outage | 16-04-2025 13:36 | The triggering incident is at 13:36:43.120 with the tripping of the 220kV BagewadiNandihal2 line due to a fault. | KPTCL to furnish Compliance report on relay replacement | KPTCL |  | Pending | Pending
131/I/2 | North Karnataka Complete Outage | 16-04-2025 13:36 | The triggering incident is at 13:36:43.120 with the tripping of the 220kV BagewadiNandihal2 line due to a fault. | KPTCL to furnish report on A/R enabling report to be furnished | KPTCL | Puspha:KPTCL: 07/07/2025 07:35:06: 1. AR is put back to service at Gataprabha for Narendra powergrid lines. 2. AR put back to service for nandihal-Bagewadi lines 3. For enabling AR for Bagalkot connected lines Main-1 relay replacement has been taken up | Complied | Pending
131/I/2 | North Karnataka Complete Outage | 16-04-2025 13:36 | The triggering incident is at 13:36:43.120 with the tripping of the 220kV BagewadiNandihal2 line due to a fault. | KPTCL to rectify DR Time synch issues at Vajramatti SS and Ghataprabha SS | KPTCL | Puspha:KPTCL: 03/09/2025 22:49:48: Yet to be attended | Pending | Pending
131/I/10 | Complete Outage of 220kV/66kV/11kV Chitradurga SS | 27-04-2025 18:08 | Due to LBB operation of 100MVA 220kV/66kV Chitradurga PTR2, all the 220kV elements connected to Bus1 and Bus2 got tripped resulting in the complete outage of 220kV/66kV/11kV Chitradurga SS. | 1. KPTCL to ensure the proper working of the all the breakers at 220kV Chitradurga and submit a report. | KPTCL | Puspha:KPTCL: 06/07/2025 23:06:20: Action is being taken by EEE, Operations Chitradurga and EEE,RT Chitradurga. Directions are given | Complied | Pending
131/I/10 | Complete Outage of 220kV/66kV/11kV Chitradurga SS | 27-04-2025 18:08 | Due to LBB operation of 100MVA 220kV/66kV Chitradurga PTR2, all the 220kV elements connected to Bus1 and Bus2 got tripped resulting in the complete outage of 220kV/66kV/11kV Chitradurga SS. | 2. KPTCL to implement the zone segregation for the LBB scheme. | KPTCL | Puspha:KPTCL: 07/08/2025 21:53:11: Necessary switches and other materials required is being arranged by EEE, Operations Chitradurga Puspha:KPTCL: 02/09/2025 22:15:10: Attended , necessary modifications in the LBB Tscheme for rip bus zone segregation based on isolator status has been implemented and taken in to service on 20.08.2025 | Complied | Pending
131/I/10 | Complete Outage of 220kV/66kV/11kV Chitradurga SS | 27-04-2025 18:08 | Due to LBB operation of 100MVA 220kV/66kV Chitradurga PTR2, all the 220kV elements connected to Bus1 and Bus2 got tripped resulting in the complete outage of 220kV/66kV/11kV Chitradurga SS. | 3. KPTCL to expediate the Transformer-2 replacement. | KPTCL | Puspha:KPTCL: 07/07/2025 07:47:21: Action taken, power transformer to be allotted from Corporate office Puspha:KPTCL: 03/09/2025 22:46:55: For replacement of failed transformer, power transformer is yet to be allotted | Pending | Pending
131/I/10 | Complete Outage of 220kV/66kV/11kV Chitradurga SS | 27-04-2025 18:08 | Due to LBB operation of 100MVA 220kV/66kV Chitradurga PTR2, all the 220kV elements connected to Bus1 and Bus2 got tripped resulting in the complete outage of 220kV/66kV/11kV Chitradurga SS. | 4. KPTCL to check the functionality of all the breakers at 220kV Chitradurga substation | KPTCL | Puspha:KPTCL: 06/07/2025 23:11:55: Action has been taken for overhauling of the Circuit Breakers at Chitradurga | Complied | Pending
131/I/10 | Complete Outage of 220kV/66kV/11kV Chitradurga SS | 27-04-2025 18:08 | Due to LBB operation of 100MVA 220kV/66kV Chitradurga PTR2, all the 220kV elements connected to Bus1 and Bus2 got tripped resulting in the complete outage of 220kV/66kV/11kV Chitradurga SS. | 5. KPTCL to expediate the Busbar replacement | KPTCL | Puspha:KPTCL: 07/07/2025 07:30:24: Bus bar replacement wok is in tendering state in Corporate office | Pending | Pending
131/I/12 | Complete outage of 220kV/66kV Bidadi_KA SS, 220kV/66kV Kothipura SS, 220kV Toyota of KPTCL | 30-04-2025 16:33 | During antecedent conditions, 220kV Tubinikere Kothipura and 220kV Kothipura Channapatna were under outage. As per the reports submitted, the triggering incident was B-N fault in 220kV Bidadi Kothipura Line-1. At Bidadi end, the fault was not cleared and the fault was cleared by remote ends of Bidadi connected lines. This led to complete outage of 220kV/66kV Bidadi_KA SS, 220kV/66kV Kothipura SS, 220kV Toyota of KPTCL. | 1. KPTCL to check all the control cable healthiness at Bidadi station. | KPTCL | Puspha:KPTCL: 06/07/2025 22:53:06: Attended, damaged 19Cx2.5sqmm control cable between CRP to line CB has been replaced | Complied | Pending
131/I/12 | Complete outage of 220kV/66kV Bidadi_KA SS, 220kV/66kV Kothipura SS, 220kV Toyota of KPTCL | 30-04-2025 16:33 | During antecedent conditions, 220kV Tubinikere Kothipura and 220kV Kothipura Channapatna were under outage. As per the reports submitted, the triggering incident was B-N fault in 220kV Bidadi Kothipura Line-1. At Bidadi end, the fault was not cleared and the fault was cleared by remote ends of Bidadi connected lines. This led to complete outage of 220kV/66kV Bidadi_KA SS, 220kV/66kV Kothipura SS, 220kV Toyota of KPTCL. | 2. KPTCL provide the back up protection immediately whenever main protection was out of service. | KPTCL | Puspha:KPTCL: 06/07/2025 22:54:25: Arrangements are made to provide external LBB protection. Necessary relays are procured, work to be taken up | Complied | Pending
131/I/12 | Complete outage of 220kV/66kV Bidadi_KA SS, 220kV/66kV Kothipura SS, 220kV Toyota of KPTCL | 30-04-2025 16:33 | During antecedent conditions, 220kV Tubinikere Kothipura and 220kV Kothipura Channapatna were under outage. As per the reports submitted, the triggering incident was B-N fault in 220kV Bidadi Kothipura Line-1. At Bidadi end, the fault was not cleared and the fault was cleared by remote ends of Bidadi connected lines. This led to complete outage of 220kV/66kV Bidadi_KA SS, 220kV/66kV Kothipura SS, 220kV Toyota of KPTCL. | 3. KPTCL to replace the Bus Bar protection scheme at Bidadi station, until the replacement works are completed, LBB protection to be enabled through trip relays. | KPTCL | Puspha:KPTCL: 06/07/2025 22:55:34: It is in tendering stage at Corporate office | Pending | Pending
131/I/12 | Complete outage of 220kV/66kV Bidadi_KA SS, 220kV/66kV Kothipura SS, 220kV Toyota of KPTCL | 30-04-2025 16:33 | During antecedent conditions, 220kV Tubinikere Kothipura and 220kV Kothipura Channapatna were under outage. As per the reports submitted, the triggering incident was B-N fault in 220kV Bidadi Kothipura Line-1. At Bidadi end, the fault was not cleared and the fault was cleared by remote ends of Bidadi connected lines. This led to complete outage of 220kV/66kV Bidadi_KA SS, 220kV/66kV Kothipura SS, 220kV Toyota of KPTCL. | 4. KPTCL to implement the line differential protection in all short lines. | KPTCL | Puspha:KPTCL: 07/07/2025 07:36:01: Action will be taken | Pending | Pending
131/I/12 | Complete outage of 220kV/66kV Bidadi_KA SS, 220kV/66kV Kothipura SS, 220kV Toyota of KPTCL | 30-04-2025 16:33 | During antecedent conditions, 220kV Tubinikere Kothipura and 220kV Kothipura Channapatna were under outage. As per the reports submitted, the triggering incident was B-N fault in 220kV Bidadi Kothipura Line-1. At Bidadi end, the fault was not cleared and the fault was cleared by remote ends of Bidadi connected lines. This led to complete outage of 220kV/66kV Bidadi_KA SS, 220kV/66kV Kothipura SS, 220kV Toyota of KPTCL. | 5. KPTCL to rectify the time synchronization issue. | KPTCL | Puspha:KPTCL: 06/07/2025 22:56:22: Attended. GPS time sync unit is put back to service after repairs | Complied | Pending
131/I/12 | Complete outage of 220kV/66kV Bidadi_KA SS, 220kV/66kV Kothipura SS, 220kV Toyota of KPTCL | 30-04-2025 16:33 | During antecedent conditions, 220kV Tubinikere Kothipura and 220kV Kothipura Channapatna were under outage. As per the reports submitted, the triggering incident was B-N fault in 220kV Bidadi Kothipura Line-1. At Bidadi end, the fault was not cleared and the fault was cleared by remote ends of Bidadi connected lines. This led to complete outage of 220kV/66kV Bidadi_KA SS, 220kV/66kV Kothipura SS, 220kV Toyota of KPTCL. | 6. PGCIL SR-II / KPTCL to check the relay settings of the PGCIL Bidadi- Bidadi line. | KPTCL | rtamcsr2:PGCIL (SR-II): 04/07/2025 13:00:48: Relay Setting has been verified for the PGCIL Bidadi - Bidadi line. | Complied | Pending
131/I/13 | Complete Outage of 220kV Manyatha and 220kV HBR Layout. Multiple Tripping in 220kV Sahkarinagar SS of KPTCL | 30-04-2025 17:10 | During antecedent 220kV Manyatha ITI and 220kV Hoody HBR Layout lines were under outage and hence 220kV Manyatha SS and 220kV HBR Layout were radially fed from 220kV Sahkarinagar SS. | 1. KPTCL to implement the line Differential protection scheme in all the short lines (length less than 10kM). | KPTCL | Puspha:KPTCL: 07/07/2025 07:32:47: Action will be taken for replacement of existing distance schemes by Line Differential scheme for lines having length less than 10km Puspha:KPTCL: 07/11/2025 22:27:12: Yet to be attended | Pending | Pending
131/I/13 | Complete Outage of 220kV Manyatha and 220kV HBR Layout. Multiple Tripping in 220kV Sahkarinagar SS of KPTCL | 30-04-2025 17:10 | During antecedent 220kV Manyatha ITI and 220kV Hoody HBR Layout lines were under outage and hence 220kV Manyatha SS and 220kV HBR Layout were radially fed from 220kV Sahkarinagar SS. | 2. KPTCL to intimate changes in the SPS settings in OCC forum. | KPTCL | Puspha:KPTCL: 06/07/2025 23:07:39: Will be attended. in future Puspha:KPTCL: 03/09/2025 22:59:16: Will be followed Puspha:KPTCL: 15/09/2025 22:45:58: Disabling of OCR provided for 220kV lines is in progress in KPTCL. Few new SPSs are being implemented for this purpose. All the SPS implemented along with adopted settings will be submitted to OCC for approval by SRPC Puspha:KPTCL: 07/11/2025 22:27:12: Will be updated to OCC forum | Complied | Pending
131/I/13 | Complete Outage of 220kV Manyatha and 220kV HBR Layout. Multiple Tripping in 220kV Sahkarinagar SS of KPTCL | 30-04-2025 17:10 | During antecedent 220kV Manyatha ITI and 220kV Hoody HBR Layout lines were under outage and hence 220kV Manyatha SS and 220kV HBR Layout were radially fed from 220kV Sahkarinagar SS. | 3. KPTCL to check the healthiness of the line differential protection in 220KV Puttenahalli Yelahanka (YCCP) lines. | KPTCL | Puspha:KPTCL: 09/07/2025 22:44:06: Detail report will be furnished after checking the relays Puspha:KPTCL: 15/09/2025 22:56:11: The recommendation will be complied, satisfactory operation of the relays will be tested by availing line outages. | Pending | Pending
131/I/13 | Complete Outage of 220kV Manyatha and 220kV HBR Layout. Multiple Tripping in 220kV Sahkarinagar SS of KPTCL | 30-04-2025 17:10 | During antecedent 220kV Manyatha ITI and 220kV Hoody HBR Layout lines were under outage and hence 220kV Manyatha SS and 220kV HBR Layout were radially fed from 220kV Sahkarinagar SS. | 4. KPTCL to modify the SPS logic to trigger the DR whenever there is a SPS operation. | KPTCL | Puspha:KPTCL: 15/09/2025 22:56:11: Will be complied | Pending | Pending
131/I/14 | Complete outage of 220kV/110kV Kavoor SS, 220kV/110kV MSEZ(Bajpe) SS, and 400kV/220kV UPCL of Adani and Tripping of 220kV Bus-1 of 220kV/110kV Kemar SS of KPTCL on 02-05-2025 at 16:11hrs | 02-05-2025 16:11 | The triggering incident was BN fault in 400kV UPCL Hebbanahalli line1 and 2. Due to tripping of these lines, running U2 at UPCL got tripped on operation of SPS at 16:11.48 hrs. Since there was split bus operation at 220kV Kemar SS during antecedent condition, an island was formed consisting of 220kV Kemar Bus1 connected loads and U1 generation at UPCL. Due to variation in the load generation balance in the island, U1 UPCL got tripped at 16:12:02hrs (island operation for 14 sec) on operation of UF protection resulting in the complete outage of 400kV/220kV UPCL, 220kV/110kV Kavoor SS, 220kV/110kV MSEZ(Bajpe) SS and de-energization of 220kV Bus1 of 220kV/110kV Kemar SS. | 1. KPTCL to submit the report on the Tower footing resistance for UPCLHebbanahalli Lines. | KPTCL | Puspha:KPTCL: 09/07/2025 22:40:38: The matter is referred to concerned operation wing for rectification | Complied | Pending
131/I/14 | Complete outage of 220kV/110kV Kavoor SS, 220kV/110kV MSEZ(Bajpe) SS, and 400kV/220kV UPCL of Adani and Tripping of 220kV Bus-1 of 220kV/110kV Kemar SS of KPTCL on 02-05-2025 at 16:11hrs | 02-05-2025 16:11 | The triggering incident was BN fault in 400kV UPCL Hebbanahalli line1 and 2. Due to tripping of these lines, running U2 at UPCL got tripped on operation of SPS at 16:11.48 hrs. Since there was split bus operation at 220kV Kemar SS during antecedent condition, an island was formed consisting of 220kV Kemar Bus1 connected loads and U1 generation at UPCL. Due to variation in the load generation balance in the island, U1 UPCL got tripped at 16:12:02hrs (island operation for 14 sec) on operation of UF protection resulting in the complete outage of 400kV/220kV UPCL, 220kV/110kV Kavoor SS, 220kV/110kV MSEZ(Bajpe) SS and de-energization of 220kV Bus1 of 220kV/110kV Kemar SS. | 2. KPTCL and UPCL to explore mothds to reduce the tower footing resistance. | KPTCL | Puspha:KPTCL: 07/08/2025 21:55:36: SRPC Recommendations communicated to CEE, Operations Hassan and the matter is being perused | Pending | Pending
131/I/14 | Complete outage of 220kV/110kV Kavoor SS, 220kV/110kV MSEZ(Bajpe) SS, and 400kV/220kV UPCL of Adani and Tripping of 220kV Bus-1 of 220kV/110kV Kemar SS of KPTCL on 02-05-2025 at 16:11hrs | 02-05-2025 16:11 | The triggering incident was BN fault in 400kV UPCL Hebbanahalli line1 and 2. Due to tripping of these lines, running U2 at UPCL got tripped on operation of SPS at 16:11.48 hrs. Since there was split bus operation at 220kV Kemar SS during antecedent condition, an island was formed consisting of 220kV Kemar Bus1 connected loads and U1 generation at UPCL. Due to variation in the load generation balance in the island, U1 UPCL got tripped at 16:12:02hrs (island operation for 14 sec) on operation of UF protection resulting in the complete outage of 400kV/220kV UPCL, 220kV/110kV Kavoor SS, 220kV/110kV MSEZ(Bajpe) SS and de-energization of 220kV Bus1 of 220kV/110kV Kemar SS. | 3. Forum recommended to implement the OPGW cable for UPCLHebbanahalli Lines. | KPTCL |  | Pending | Pending
131/I/14 | Complete outage of 220kV/110kV Kavoor SS, 220kV/110kV MSEZ(Bajpe) SS, and 400kV/220kV UPCL of Adani and Tripping of 220kV Bus-1 of 220kV/110kV Kemar SS of KPTCL on 02-05-2025 at 16:11hrs | 02-05-2025 16:11 | The triggering incident was BN fault in 400kV UPCL Hebbanahalli line1 and 2. Due to tripping of these lines, running U2 at UPCL got tripped on operation of SPS at 16:11.48 hrs. Since there was split bus operation at 220kV Kemar SS during antecedent condition, an island was formed consisting of 220kV Kemar Bus1 connected loads and U1 generation at UPCL. Due to variation in the load generation balance in the island, U1 UPCL got tripped at 16:12:02hrs (island operation for 14 sec) on operation of UF protection resulting in the complete outage of 400kV/220kV UPCL, 220kV/110kV Kavoor SS, 220kV/110kV MSEZ(Bajpe) SS and de-energization of 220kV Bus1 of 220kV/110kV Kemar SS. | 4. KPTCL and UPCL to ensure the Bus Coupler to be in closed condition as SPS is being implemented. | KPTCL | Puspha:KPTCL: 06/07/2025 23:00:02: Attended. Bus Coupler at Kemar is kept in closed condition after incorporating necessary modifications in theUPCL SPS | Complied | Pending
131/I/19 | Complete outage of 220kV/66kV HBR Layout SS of KPTCL | 14-05-2025 12:11 | During antecedent conditions, 220kV Manyata HBR layout was under outage. As per the reports submitted, the triggering incident was R-N fault in the UG cable of 220kV Hoody HBR Layout line and the line tripped.Tripping of the only connected line led to complete outage of 220kV HBR Layout SS. | KPTCL to resolve the DR time sych issue at Hoody SS. | KPTCL | Puspha:KPTCL: 06/07/2025 22:58:36: PO placed for replacement of faulty GPS unit, supply of new GPS device is awaited Puspha:KPTCL: 04/12/2025 16:13:14: As verified by the OEM earlier the PO was placed and new antenna was procured. While commissioning the same by OEM it was found that it is not compatible for the GPS unit. Hence action has been taken to purchase the compatible GPS unit from the OEM. Puspha:KPTCL: 04/12/2025 17:13:15: As verified by the OEM earlier the PO was placed and new antenna was procured. While commissioning the same by OEM it was found that it is not compatible for the GPS unit. Hence action has been taken to purchase the compatible GPS unit from the OEM. | Pending | Pending
131/VI/7 | NARENDRA_KP - 220KV | 01-05-2025 17:59 | DR TIME SYNC ISSUE | KPTCL to furnish the reasons for DR Time sync issues | KPTCL | Puspha:KPTCL: 09/07/2025 22:47:39: Action will be taken for rectification of GPS time sync equipment at Narendra substation | Pending | Pending
131/VI/14 | 220KV-KADAKOLA-KANIYAMPETTA | 19-05-2025 00:50 | KADAKOLA - 220KV | KPTCL to furnish the reasons for DR Time sync issues | KPTCL | Puspha:KPTCL: 06/07/2025 22:57:36: At Kadakola, except Siemens make Main-2 relays other relays are time synchronized with GPS clock.. | Complied | Complied
132/I/3 | Complete outage of 220kV/66kV Neelagunda SS, 220kV/66kV Kudligi SS, 220kV/66kV Tallak SS, 220kV BARC SS, 220kV Sagitur SS and 220kV Bus-2 of 220kV/66kV Ittagi SS | 22-05-2025 11:22 | During antecedent conditions, 220kV Neelagunda Guttur and 220kV Jagalur Tallak Line-&2 were under outage. 220kV Itagi SS was operating with Bus split condition with 220kV Itagi Neelagunda and 220kV Itagi Kudlagi Line-1&2 on 220kV Bus-1. As per the reports submitted, multiple lines tripped on over loading. Subsquently, 400kV/220kV Jagalur ICT-1&2 tripped on over loading. Tripping of all these elements led to complete outage of 220kV/66kV Neelagunda SS, 220kV/66kV Kudligi SS, 220kV/66kV Tallak SS, 220kV BARC SS, 220kV Sagitur SS and 220kV Bus-2 of 220kV/66kV Ittagi SS | KPTCL & KAR SLDC to finalise SPS to avoid such instances. The SPS may include generation and load as per the contigencies | KPTCL | Puspha:KPTCL: 06/08/2025 20:57:53: SPS for generation back down during over loading of ICTs at Jagalur is in service. SPS for overloading of 220kV lines in the downstream of Jagalur ICTs have been provided by CEE,RT Office. SPS is implemented at Chitradurga line OCR for 220kV lines are disabled. SPS under implementation at Thalak substation. Puspha:KPTCL: 03/09/2025 22:56:05: SPS implementation and disabling OCR for 220kV lines is under progress Puspha:KPTCL: 15/09/2025 22:56:11: SPS implemented for various contingency conditions in this corridor Puspha:KPTCL: 07/11/2025 22:27:12: SPSs have been implemented for various contingency conditions Puspha:KPTCL: 06/01/2026 22:18:21: The recommendation will be complied by SLDC in future | Complied | Complied
132/I/7 | Complete Outage of 220kV/110kV Ambewadi SS and Tripping of 220kV South West Bus of 220kV Naghjeri PH | 18-06-2025 16:50 | During antecedent conditions, 220kV Ambewadi Narendra line-1 and 2 were under outage for power regulation and 220kV Ambewadi Naghjeri line-1 was out due to fault. Hence 220kV/110kV Ambewadi SS was radially fed through 220kV Ambewadi Naghjeri line-2. The triggering incident was LBB maloperation of 220kV Naghjeri Hubli line-1 at Naghjeri end resulting in the de-energisation of 220kV Naghjeri PH South West Bus. Since 220kV Ambewadi Naghjeri line-2 was connected to 220kV South West Bus of 220kV Naghjeri PH. Tripping of the only connected line resulted in the complete outage of 220kV/110kV Ambewadi SS | KPCL to implement the double BUSBAR operation | KPCL | EE (E )/CEED:KPCL: 04/08/2025 10:31:39: Double busbar operation will be made operational after conditioning of the ODY equipments. EE (E )/CEED:KPCL: 30/08/2025 14:55:02: Double bus operation is in service. It is requested to close the point. EE (E )/CEED:KPCL: 04/10/2025 11:44:44: Double bus operation is in service. It is requested to close the point. EE (E )/CEED:KPCL: 04/11/2025 10:04:03: Double bus operation is in service. It is requested to close the point. EE (E )/CEED:KPCL: 04/12/2025 16:42:28: Double bus operation is in service. It is requested to drop the point. | Complied | Complied
132/II/4 | Tripping of 400kV Bus-1 and Bus-2 of 400kV/220kV Talaguppa SS of KPTCL | 06-06-2025 12:13 | As per the reports submited, the triggering incident was changing of DC source of 400kV Bus panel and 400kV Bus-1 and Bus-2 BBP maloperated tripping all main breakers connected to both buses. 220kV was intact during the event | KPTCL to consult the OEM to understand the reason for CU reboot and to submit the same along with a detailed report regarding the Busbar protection operation and Tie breaker operation to SRPC and SRLDC | KPTCL | Puspha:KPTCL: 06/08/2025 20:52:22: Details sought by OEM are furnished, reply from OEM M/s GE is awaited. DC grounding issue has been resolved. Due to full hydro generation bus bar/lbb scheme testing is not taken upat talaguppa SS | Pending | Pending
132/VI/7 | Chitradurga - 220KV | 22-05-2025 11:22 | Station at which DR time synchronisation was not observed - Chitradurga - 220KV | KPTCL to furnish the reasons for DR Time sync Issues | KPTCL | Puspha:KPTCL: 07/08/2025 15:17:49: M/s SANDS make GPS equipment provided is healthy and in working condition. Sifang make Main-1 relays of few lines and some old version relays are not time synchronized with GPS GPS clock due to relay limitations. | Pending | Pending
132/VI/9 | 400KV-NELAMANGALA-TALGUPPA-1 | 23-05-2025 12:42 | Station at which DR time synchronisation was not observed - NELAMANGALA - 400KV | KPTCL to furnish the reasons for DR Time sync Issues | KPTCL | Puspha:KPTCL: 06/08/2025 20:44:33: At Nelamanagala GPS time synchronisation system is healthy. Only M1 relay of Talaguppa having issue .M2 is time synchronised with GPS clock | Complied | Complied
132/VI/15 | 220KV-SEDAM-TANDUR-1 | 29-05-2025 11:41 | Station at which DR time synchronisation was not observed - SEDAM - 220KV | KPTCL to furnish the reasons for DR Time sync Issues | KPTCL | Puspha:KPTCL: 07/08/2025 15:15:56: SANDS make GPS time sync equipment is in working condition at Sedam. On verification it was observed that due to station level network issue relays are not time synchronized with GPS clock. Action has been taken to rectify the issue by taking online support of M/s Kalkitech Ltd Puspha:KPTCL: 03/09/2025 22:55:03: Sedam GPS time sync issue of relays was rectified on 29.08.2025 Puspha:KPTCL: 15/09/2025 22:56:11: Attended and complied Puspha:KPTCL: 15/09/2025 23:10:11: Attended on 29.08.2025 and complied | Complied | Complied
132/VI/20 | 220KV-BIJAPUR-NANDHIHAL-1 | 15-06-2025 13:07 | Station at which DR time synchronisation was not observed - BIJAPUR - 220KV | KPTCL to furnish the reasons for DR Time sync Issues | KPTCL | Puspha:KPTCL: 07/08/2025 17:39:18: At Bijapur GPS time synchronising equipment provided along with SAS at the time of Substation commissioning i not functional. The matter is reffered to concerned Operatiuon Division for rectification of the same Puspha:KPTCL: 03/09/2025 22:54:00: At Bijapur provision for replacement of failed GPS equipment was not made along with SAS upgradation work. Now action is being taken Puspha:KPTCL: 15/09/2025 22:56:11: At Bijapur GPS time sync issue provided along with SAS is faulty, It is recommended to replace the same for restoring GOS time synchronization of protection relays in Bijapur | Complied | Complied
133/I/1 | Complete Outage of 220kV TUBINAKERE, CHANNAPATNA, KOTHIPURA of KPTCL | 05-07-2025 07:03 | The triggering incident is the R-Y fault in 220KV-TUBINAKERE-CHANNAPATNA-1 line during which 220KV-BIDADI-KOTHIPURA-1 &2 tripped on distance protection (suspected overreach) and at the same time LBB operated at TUBINAKERE Bus-1. After tripping of 220KV-BIDADI-KOTHIPURA-1&2 lines, the only source to these stations was Bus-1 at TUBINAKERE (Connected to Mysore and Gopalpura). Due to the LBB operation and tripping of Bus-1 at TUBINAKERE led to the Complete Outage of 220kV TUBINAKERE, CHANNAPATNA, KOTHIPURA of KPTCL | KPTCL to ensure strict adherence to SOP during testing activities. | KPTCL | Puspha:KPTCL: 02/09/2025 22:11:08: Clear Instructions have been given to concerned field officers in this regard | Complied | Complied
133/I/1 | Complete Outage of 220kV TUBINAKERE, CHANNAPATNA, KOTHIPURA of KPTCL | 05-07-2025 07:03 | The triggering incident is the R-Y fault in 220KV-TUBINAKERE-CHANNAPATNA-1 line during which 220KV-BIDADI-KOTHIPURA-1 &2 tripped on distance protection (suspected overreach) and at the same time LBB operated at TUBINAKERE Bus-1. After tripping of 220KV-BIDADI-KOTHIPURA-1&2 lines, the only source to these stations was Bus-1 at TUBINAKERE (Connected to Mysore and Gopalpura). Due to the LBB operation and tripping of Bus-1 at TUBINAKERE led to the Complete Outage of 220kV TUBINAKERE, CHANNAPATNA, KOTHIPURA of KPTCL | KPTCL to map the DR channels are per FOLD recommendations at 220kV Bidadi SS. | KPTCL | Puspha:KPTCL: 02/09/2025 22:11:08: Directions have been given to attend DR channel mapping issues at Bidadi substation | Complied | Complied
133/I/1 | Complete Outage of 220kV TUBINAKERE, CHANNAPATNA, KOTHIPURA of KPTCL | 05-07-2025 07:03 | The triggering incident is the R-Y fault in 220KV-TUBINAKERE-CHANNAPATNA-1 line during which 220KV-BIDADI-KOTHIPURA-1 &2 tripped on distance protection (suspected overreach) and at the same time LBB operated at TUBINAKERE Bus-1. After tripping of 220KV-BIDADI-KOTHIPURA-1&2 lines, the only source to these stations was Bus-1 at TUBINAKERE (Connected to Mysore and Gopalpura). Due to the LBB operation and tripping of Bus-1 at TUBINAKERE led to the Complete Outage of 220kV TUBINAKERE, CHANNAPATNA, KOTHIPURA of KPTCL | KPTCL to rectify DR time sync issue at 220kV Kothipura & Bidadi SS. | KPTCL | Puspha:KPTCL: 03/09/2025 22:44:56: At Bidadi GPS unit is put back to service. At Kothipura time sync of protection relays is healthy | Complied | Complied
133/I/1 | Complete Outage of 220kV TUBINAKERE, CHANNAPATNA, KOTHIPURA of KPTCL | 05-07-2025 07:03 | The triggering incident is the R-Y fault in 220KV-TUBINAKERE-CHANNAPATNA-1 line during which 220KV-BIDADI-KOTHIPURA-1 &2 tripped on distance protection (suspected overreach) and at the same time LBB operated at TUBINAKERE Bus-1. After tripping of 220KV-BIDADI-KOTHIPURA-1&2 lines, the only source to these stations was Bus-1 at TUBINAKERE (Connected to Mysore and Gopalpura). Due to the LBB operation and tripping of Bus-1 at TUBINAKERE led to the Complete Outage of 220kV TUBINAKERE, CHANNAPATNA, KOTHIPURA of KPTCL | KPTCL to rectify the PSL logic issue at Bidadi & Bastipura SS. | KPTCL | Puspha:KPTCL: 02/09/2025 22:11:08: PSL logic issues have been resolved in Bidadi Substation (Kothipura D/c line M2 relays) and aT Tubinakere (Bastipura line M1 REL670 relay) | Complied | Complied
133/II/5 | Tripping of 400kV Bus-1 at RTPS of KPCL | 08-07-2025 02:39 | The triggering incident is the suspected input contact in the B90 Numerical relay of GT-7 main breaker triggering of External LBB initiation of Bus-1 Main Breaker and leading to Bus-1 BBP operation tripping of all the breakers connected to 400kV Bus-1 at RTPS. Since tie breakers connected to 400KV/220KV RTPS-ICT-2, 400KV/220KV RTPS-ICT-3 were unavailable during the event to the tripping of 400KV/220KV RTPS-ICT-2, 400KV/220KV RTPS-ICT-3. This led to the tripping of 400kV Bus-1 at RTPS. | KPCL to rectify the contact issues in the B90 relay in consultation with OEM. | KPCL | EE (E )/CEED:KPCL: 30/08/2025 14:50:04: OEM visited site and requested DC supply and other details to analyse and identify the failure. Reply from OEM is awaited. EE (E )/CEED:KPCL: 04/11/2025 10:04:03: OEM visited site and requested DC supply and other details to analyse and identify the failure. Reply from OEM is awaited. EE (E )/CEED:KPCL: 04/12/2025 16:42:28: OEM visited site and requested DC supply and other details to analyse and identify the failure. Reply from OEM is awaited. EE (E )/CEED:KPCL: 01/01/2026 10:09:46: OEM Opined the issue of station 220V DC earth fault as probable reason for mal-operation of the relay and suggested to rectify DC earth fault. Identification of DC earth fault is in proces and will be attended. EE (E )/CEED:KPCL: 03/02/2026 12:02:39: OEM Opined the issue of station 220V DC earth fault as probable reason for mal-operation of the relay and suggested to rectify DC earth fault. Identification of DC earth fault is in proces and will be attended | Complied | Complied
134/I/3 | Complete outage of 220kV Chitradurga SS of KPTCL | 10-08-2025 09:58 | As per the reports submitted, the triggering incident was the tripping of the B-pole of the 220 kV Hiriyur_PG Chitradurga line, caused by the failure of the DC supervision coil and its contacts, which were found burnt. This resulted in a short circuit in the DCS coil and extension of positive DC to the B-phase tripping coil. Subsequently, DEF picked up due to unbalanced current and DEF trip was issued. However, the CB failed to open as the DC supply fuses in the C&R panel had blown. As a result, the Main-2 relay initiated LBB protection, following which all elements connected to the 220 kV Bus-1 and Bus-2 tripped, causing a complete outage of the 220 kV Chitradurga substation. | KPTCL to extend dual DC supply to all the circuit breakers | KPTCL | Puspha:KPTCL: 04/10/2025 19:57:19: Actiona has been taken for extending second DC source to Hiriyur line CB. Procurement of necessary materials being done by EEE,Operations Chitradurga. Once the necessary materials are procured modifications will be done to extend second DC source tpo line CB Puspha:KPTCL: 04/10/2025 19:58:48: GPS device is in healthy condition at chitradurga. But majority of the relays are old and having limitations with respect to GPS time synchronisation. Procurement of new relays is under progress. PO will be placed shortly | Complied | Complied
134/I/3 | Complete outage of 220kV Chitradurga SS of KPTCL | 10-08-2025 09:58 | As per the reports submitted, the triggering incident was the tripping of the B-pole of the 220 kV Hiriyur_PG Chitradurga line, caused by the failure of the DC supervision coil and its contacts, which were found burnt. This resulted in a short circuit in the DCS coil and extension of positive DC to the B-phase tripping coil. Subsequently, DEF picked up due to unbalanced current and DEF trip was issued. However, the CB failed to open as the DC supply fuses in the C&R panel had blown. As a result, the Main-2 relay initiated LBB protection, following which all elements connected to the 220 kV Bus-1 and Bus-2 tripped, causing a complete outage of the 220 kV Chitradurga substation. | KPTCL to rectify the DR timesync issue at 220kV Chitradurga SS | KPTCL | Puspha:KPTCL: 04/10/2025 20:02:47: GPS time sync equipment is in working condition at Chitradurga. Some old version relays having limitations w.r.t GPS time synchronisation. Action has been taken for replacement of old version relays at chitradurga | Complied | Complied
134/I/3 | Complete outage of 220kV Chitradurga SS of KPTCL | 10-08-2025 09:58 | As per the reports submitted, the triggering incident was the tripping of the B-pole of the 220 kV Hiriyur_PG Chitradurga line, caused by the failure of the DC supervision coil and its contacts, which were found burnt. This resulted in a short circuit in the DCS coil and extension of positive DC to the B-phase tripping coil. Subsequently, DEF picked up due to unbalanced current and DEF trip was issued. However, the CB failed to open as the DC supply fuses in the C&R panel had blown. As a result, the Main-2 relay initiated LBB protection, following which all elements connected to the 220 kV Bus-1 and Bus-2 tripped, causing a complete outage of the 220 kV Chitradurga substation. | KPTCL to verify the LBB Scheme at Chitradurga and furnish the report | KPTCL | Puspha:KPTCL: 04/10/2025 19:54:48: Healthiness of LBB scheme has been verified at Chitradurga Substation and found to be working satisfactory. | Complied | Complied
134/I/5 | Complete Outage of 220kV Nagjheri PH of KPCL, 220kV Ambewadi SS, 220kV Hubli SS, and 220kV Sirsi SS of KPTCL | 12-08-2025 15:30 | During antecedent conditions, multiple 220 kV lines were already under outage or idle charged condition, leaving 220kV HubliBidnal line1 &2 as the only evacuation path for 220kV Nagjheri PH. At 15:30 hrs, 220kV HubliBidnal line2 was hand-tripped at Bidnal end due to arcing in Bus2 isolator. Subsequently, the entire load was shifted to 220kV HubliBidnal line1, and the line tripped at Hubli end on over loading. This led to islanding of 220kV Nagjheri PH, tripping of its running units on over-frequency, and resulted in complete outage of 220kV Ambewadi, 220kV Hubli, and 220kV Sirsi substations. | KPCL to explain the action of hand-tripping HubliBidnal line2 at Bidnal end without reducing the generation | KPCL | EE (E )/CEED:KPCL: 04/10/2025 11:40:07: Hand tripping of Hubli Bidnal -2 Line is from KPTCL side.Hence this point to be closed. | Complied | Complied
134/I/5 | Complete Outage of 220kV Nagjheri PH of KPCL, 220kV Ambewadi SS, 220kV Hubli SS, and 220kV Sirsi SS of KPTCL | 12-08-2025 15:30 | During antecedent conditions, multiple 220 kV lines were already under outage or idle charged condition, leaving 220kV HubliBidnal line1 &2 as the only evacuation path for 220kV Nagjheri PH. At 15:30 hrs, 220kV HubliBidnal line2 was hand-tripped at Bidnal end due to arcing in Bus2 isolator. Subsequently, the entire load was shifted to 220kV HubliBidnal line1, and the line tripped at Hubli end on over loading. This led to islanding of 220kV Nagjheri PH, tripping of its running units on over-frequency, and resulted in complete outage of 220kV Ambewadi, 220kV Hubli, and 220kV Sirsi substations. | KPTCL to furnish the restoration schedule of HubliNarendra D/c, which is under tripped condition since 17.05.2025 for attending to the tower collapse in the line | KPTCL | Puspha:KPTCL: 04/10/2025 19:53:35: Tender has been called by CEE,Operations Bagalkot for restoration of collapsed towers | Complied | Complied
134/I/5 | Complete Outage of 220kV Nagjheri PH of KPCL, 220kV Ambewadi SS, 220kV Hubli SS, and 220kV Sirsi SS of KPTCL | 12-08-2025 15:30 | During antecedent conditions, multiple 220 kV lines were already under outage or idle charged condition, leaving 220kV HubliBidnal line1 &2 as the only evacuation path for 220kV Nagjheri PH. At 15:30 hrs, 220kV HubliBidnal line2 was hand-tripped at Bidnal end due to arcing in Bus2 isolator. Subsequently, the entire load was shifted to 220kV HubliBidnal line1, and the line tripped at Hubli end on over loading. This led to islanding of 220kV Nagjheri PH, tripping of its running units on over-frequency, and resulted in complete outage of 220kV Ambewadi, 220kV Hubli, and 220kV Sirsi substations. | KPTCL to rectify the DR time sync issue at 220kV Hubli SS. | KPTCL | Puspha:KPTCL: 04/10/2025 19:51:59: At Hubli GPS Device is working. But due to faulty patch cords some of the relays are having time sync issue. Action has been taken by EEE,Operations Hubli for replacement of fauty patch cords, PO will be placed. Once the relays are restored back in SAS, GPS time synchronisation will be ensured | Complied | Complied
134/I/5 | Complete Outage of 220kV Nagjheri PH of KPCL, 220kV Ambewadi SS, 220kV Hubli SS, and 220kV Sirsi SS of KPTCL | 12-08-2025 15:30 | During antecedent conditions, multiple 220 kV lines were already under outage or idle charged condition, leaving 220kV HubliBidnal line1 &2 as the only evacuation path for 220kV Nagjheri PH. At 15:30 hrs, 220kV HubliBidnal line2 was hand-tripped at Bidnal end due to arcing in Bus2 isolator. Subsequently, the entire load was shifted to 220kV HubliBidnal line1, and the line tripped at Hubli end on over loading. This led to islanding of 220kV Nagjheri PH, tripping of its running units on over-frequency, and resulted in complete outage of 220kV Ambewadi, 220kV Hubli, and 220kV Sirsi substations. | Multiple shutdowns availed simultaneously were not in line with the outage guidelines. KAR SLDC to furnish a report on how such outages were permitted at the same time | KPTCL | Puspha:KPTCL: 04/10/2025 20:00:03: The matter has been taken up with SLDC to comply in future | Complied | Complied
134/I/8 | Complete Outage of 220kV MK Hubli SS of KPTCL | 14-08-2025 13:48 | 220kV MK Hubli is being radially fed through 220kV Narendra MK Hubli Line-1&2. As per the reports submitted, the triggering incident was R-N fault in 110kV MK Hubli Bidi line and was not cleared at MK Hubli end. Subsequently, DEF protection operated at Narendra end in 220kV Narendra MK Hubli Line-1&2 and the lines tripped clearing the fault. Tripping of only source led to complete outage of 220kV MK Hubli SS. | KPTCL to examine the relay coordination between MKHUBLI and Narendra SS | KPTCL | Puspha:KPTCL: 04/10/2025 07:13:27: Relay coordination between Narendra PGCIL and MK Hubli SS is found to be satisfactory. Since there is no busbar protection for 110kV buses at MK Hubli, the bus fault to be cleared by tripping of both the PTRs, Due to faulty back up protection relay one of the PTR did not trip. Hence fault is cleared by tripping of incoming lines. Tripping is in order Puspha:KPTCL: 07/11/2025 22:27:12: Attended and complied Puspha:KPTCL: 06/01/2026 22:18:21: Relay coordination is reviwed and found to be OK | Complied | Complied
134/I/8 | Complete Outage of 220kV MK Hubli SS of KPTCL | 14-08-2025 13:48 | 220kV MK Hubli is being radially fed through 220kV Narendra MK Hubli Line-1&2. As per the reports submitted, the triggering incident was R-N fault in 110kV MK Hubli Bidi line and was not cleared at MK Hubli end. Subsequently, DEF protection operated at Narendra end in 220kV Narendra MK Hubli Line-1&2 and the lines tripped clearing the fault. Tripping of only source led to complete outage of 220kV MK Hubli SS. | KPTCL to rectify the DR time sync issue at MK Hubli SS | KPTCL | Puspha:KPTCL: 04/10/2025 07:10:50: Action has been taken by EEE,Operations Belgaum for replacement of faulty GPS unit. PO to be placed after observing tender formalities Puspha:KPTCL: 07/11/2025 22:27:12: GPS replacement / restoration of SAS is Under process Puspha:KPTCL: 06/01/2026 22:18:21: Procuremnt of new GPS is under progress, PO will be placed shortly | Complied | Complied
134/I/8 | Complete Outage of 220kV MK Hubli SS of KPTCL | 14-08-2025 13:48 | 220kV MK Hubli is being radially fed through 220kV Narendra MK Hubli Line-1&2. As per the reports submitted, the triggering incident was R-N fault in 110kV MK Hubli Bidi line and was not cleared at MK Hubli end. Subsequently, DEF protection operated at Narendra end in 220kV Narendra MK Hubli Line-1&2 and the lines tripped clearing the fault. Tripping of only source led to complete outage of 220kV MK Hubli SS. | PGCIL SR-2 to transplay the event and furnish the results | KPTCL | Puspha:KPTCL: 07/11/2025 22:27:12: PGCIL to comply | Complied | Complied
135/I/1 | Complete outage of 220kV Davanagere SS, 220kV Benkikere SS, 220kV Hosadurga SS, 220kV Neelagunda SS, 220kV Guttur SAS SS , 220kV Bus outage at 400kV/220kV Guttur SS, 220kV Bus-2 of Itagi SS and 220kV Bus-2 Honnali SS of KPTCL | 23-08-2025 10:33 | During antecedent conditions, 220kV Davanagere SS, 220kV Benkikere SS, 220kV Hosadurga SS, 220kV Neelagunda SS, 220kV Guttur SAS SS,220kV Honnali Bus-2, 220kV Itagi Bus-2, 220kV Wish Wind were being radially fed from 220kV Guttur SS. As per the reports submitted, the triggering incident was failure of R-phase isolator in 220kV Chitradurga line bay at 220kV Guttur SS and fell on 220kV Guttur Bus-1 & 220kV Bus-2 causing and R-B fault. Immedeately, 220kV Bus-1 and Bus-2 BBP operated and all the elements tripped leading to 220kV bus shut down at Guttur 400/220kV substation and main suppply failure occurred to 220kV Davanagere SS, 220kV Benkikere SS, 220kV Hosadurga SS, 220kV Neelagunda SS, 220kV Guttur SAS SS,220kV Honnali Bus-2, 220kV Itagi Bus-2 and 220kV Wish Wind during the incident. | 1.KPTCL to verify the settings at Neelagunda & Chitradurga end. 2.KPTCL to rectify the DR Timesync issue at Guttur SS. 3.KPTCL to furnish the DR at chitradurga end during the event to SRPC & SRLDC. 4.KPTCL to give Feedback to Planning department on requirement of system strengthening | KPTCL | Puspha:KPTCL: 07/11/2025 22:27:12: 1. Neelagunda line revised settings are issued. 2) Chitradurga linelength to be ascertained once again using offline fault locator. 3) For attending GPS issue visit of GE engineers are awaited Puspha:KPTCL: 03/02/2026 15:07:08: Attended | Complied | Complied
135/I/2 | Complete Outage of 220kV Hoody Bus-2, 220kV EDC, 220kV ITPL, 220kV Sobha dreams and 220kV EPIP SS of KPTCL | 24-08-2025 13:41 | During antecedent conditons, 220kV HSR EPIP and 220kV EDC HAL, 220kV Electronic city Shobha dreams lines were under open condition. As per the reports submitted, the triggering incident was R Phase breaker limb failure in 220kV Hoody Sobha dreams line causing an R-N fault. The fault was sensed in zone-1, Y and B-poles opened but R-pole failed to open. Subsequently, B-N fault was observed in 220kV Hoody HAL Line-1. The fault was sensed in zone-1 and the line tripped. At the same time, 220kV EDC HAL line tripped at HAL end on SPS operation. At the same time, 400kV/220kV Hoody ICT-1 and 220kV Hoody Bus coupler tripped on EFR and OC protection and 220kV Hoody EPIP tripped on IN>1 trip at Hoody end. This led to loss of power suply to 220kV Hoody Bus-2 and 220kV EDC, 220kV ITPL, 220kV Sobha dreams and 220kV EPIP SS. | 1.KPTCL to disable the weak infeed logic. 2.KPTCL to rectify the DR time sync issue at Hoody SS. 3.KPTCL to ensure strict adherence to SOP during testing and maintainance activities. 4.KPTCL to review all other breaker healthiness of other breaker at 400/220kV Hoody SS. 5.KPTCL to review the SPS logic and settings at Hoody 6.KPTCL to give Feedback to Planning department on requirement of system strengthening | KPTCL | Puspha:KPTCL: 07/11/2025 22:21:04: 1. Weak end infeed disabled at Hoody for all lines 2. Yet to be rectified Puspha:KPTCL: 03/02/2026 15:07:08: Attended and complied | Complied | Complied
135/I/3 | Complete Outage of 220kV Kudligi SS, Tripping of 220kV Bus-1 & Bus-2 of Jagalur SS, 220kV Bus-1 of Itagi SS and 220kV Bus-2 of Thalak SS of KPTCL | 26-08-2025 12:15 | As per the reports submitted, the triggering incident was arcing in 220kV Jagalur Kudligi Line-2 line during change over from 220 kV Bus-2 to 220 kV Bus-1 for availing shutdown in 220kV Bus-2 at Jagalur. Consequently, 220kV Bus coupler tripped on O/C and E/F protection and 400kV/220kV Jagalur ICT-2 was handtripped which led to overloading of 400kV/220kV Jagalur ICT-1. The ICT-1 tripped on over loading eventually. Tripping of both ICTs led to Complete Outage of 220kV Kudligi SS, Tripping of 220kV Bus-1 & Bus-2 of Jagalur SS, 220kV Bus-1 of Itagi SS and 220kV Bus-2 of Thalak SS | 1.KPTCL to review and ensure the SPS trip extension at 220kV Kudligi Substation. 2.KPTCL to follow the SOP while carrying out operations in switchyard live condition. 3.KPTCL to rectify the DR timesync at Jagalur 400/220kV. 4.KPTCL to give Feedback to planners on huge loss of RE and Load | KPTCL | Puspha:KPTCL: 07/11/2025 22:21:04: 1) Mock test has been conducted, at Kudlagi some issues noticed have to be rectified 2).Heathy 3) Attended , feedback [has been provided to the planning wing Puspha:KPTCL: 06/01/2026 22:18:21: Attended. Mock test was conducted. During the mock test problem observed in contactors extending PLCC signal to respective IPP bays in Badeladuku was identifed and the same has been attended | Complied | Complied
135/I/5 | Complete outage of 220 kV Aheri, Nimbarga, Vaishali, Shahbad, Kapnoor, Humnabad, Gulbarga, and Santhapur and tripping of 220 kV Bijapur Bus-2, Shahpur Bus-2, Sedam Bus-2, and Bus-1 & Bus-2 at Kalburgi of KPTCL | 08-09-2025 14:35 | In the antecedent conditions, multiple bus splits were carried out in the vicinity of 400/220 kV Kalburgi substation to facilitate evacuation of RE power. The triggering incident was the tripping of all elements at the 220 kV Kalburgi substation due to a suspected control cable issue, which resulted in the tripping of both 220 kV Bus-1 and Bus-2 at Kalburgi and all elements associated to it. Since multiple substations evacuate power through Kalburgi, the tripping of the evacuation path led to the complete outage of 220 kV Aheri, Nimbarga, Vaishali, Shahbad, Kapnoor, Humnabad, Gulbarga, and Santhapur and tripping of 220 kV Bijapur Bus-2, Shahpur Bus-2, Sedam Bus-2, and Bus-1 & Bus-2 at Ferozabad(Kalburgi) of KPTCL | 1.KPTCL to rectify the time synchronization issue at Kalaburgi SS. 2.KPTCL to check the healthiness of all the control cables at 400/220 kV Kalaburgi Substation. 3.KPTCL to give Feedback to planner on huge RE/load loss. | KPTCL | Puspha:KPTCL: 07/11/2025 22:21:04: GPS time synchronisatiof of relays at Kalaburgi is ascertained | Complied | Complied
135/I/6 | Complete outage of 220kV Vaishali, Shahbad, Kapnoor, Humnabad, Gulbarga, and Santhapur and tripping of 220 kV Sedam Bus-2, and 220kV Bus-1 & Bus-2 at Kalburgi of KPTCL. | 08-09-2025 15:15 | In the antecedent conditions, due to bus split operations at Sedam, the generation in the pocket (yellow highlighted region) is evacuating through 400kV Kalaburgi station through 400/220kV Kalaburgi ICT-1&2.The triggering incident is the tripping of all the 220kV elements due to 96 operated indication on suspected DC earth fault at Kalburgi (Ferozabad) station. Due to the tripping of the evacuation path of the generation led to complete outage of 220kV Vaishali, Shahbad, Kapnoor, Humnabad, Gulbarga, and Santhapur and tripping of 220 kV Sedam Bus-2, and 220kV Bus-1 & Bus-2 at Kalburgi of KPTCL. | 1.KPTCL to rectify the DR time sync issue at Kalaburgi SS 2.KPTCL to verify the healthiness of all the control cables at Kalaburgi SS | KPTCL | Puspha:KPTCL: 07/11/2025 19:43:11: Attended . GPS time synchronization of relays have been ascertained at Kalaburgi Substation | Complied | Complied
135/II/5 | Tripping of 400kV Bus-2 of 400kV Yelahanka of PGCIL SR-2 | 08-09-2025 23:04 | The triggering incident is the R-ph failure of 402CB compartment (400kV-Yelahanka-Nelamangala) leading to 400kV Bus-2 fault, BBP protection operated and led to tripping of all the elements connected to 400kV Bus-2 at Yelahanka end and DT was sent to remote end. This led to the tripping of 400kV Bus-2 of 400kV Yelahanka | 1.KPTCL to check the healthiness of the CT and CVT at Nelmangala 2.KPTCL to review the Distance zone settings at Nelamangala SS | KPTCL | Puspha:KPTCL: 07/11/2025 22:21:04: Will be attended by taking line shut down | Pending | Pending
135/II/8 | Tripping of 220kV Bus-2 of 220kV Yerrandahalli SS of KPTCL | 13-09-2025 12:43 | During antecedent condition, 220kV Yerrandahalli SS was operating with bus split condition with 220kV Yerrandahalli Hosur line radially feeding 220kV Yerrandahalli Bus-2. As per the reports submitted, the triggering incident was-N fault in 220kV Yerrandahalli Hosur Line-1. Tripping of only connected line led to loss of power supply to 220kV Yerrandahalli Bus-2. | KPTCL to resolve the Right of Way (ROW) issues in the Yerrandahalli Hosur line | KPTCL | Puspha:KPTCL: 07/11/2025 19:42:16: Line maintenance activities have been carried out by availing the line outage Puspha:KPTCL: 06/01/2026 22:05:53: Attended by TLM SOmanahally sub division | Complied | Complied
135/V/4 | 400KV-KAIGA-GUTTUR-2 | 15-09-2025 13:14 | As per the reports submitted, the triggering incident is the spurious DT signal being sent from Guttur end. DT was received at Kaiga end and 3ph tripped. The line was holding at Guttur end. | KPTCL to review the Tie CB connections at Guttur | KPTCL | Puspha:KPTCL: 07/11/2025 03:23:09: Attended, Additional wiring done from Tie CB to Kaiga 2DT send Channel 1 and 2 both removed Puspha:KPTCL: 06/01/2026 22:04:08: Attended | Complied | Complied
135/VI/1 | 220KV-HOODY-HAL-1 | 24-08-2025 13:41 | On 24.08.2025, 220kV hoody Shobha dreams acres line tripped at 13:41hrs at 400kV R/s, Hoody on main II distance relay with very huge sound : Fault location: 3.814kM, Ia:19.33kA, Ib: 512A, Ic:935A, Zone-1 operated. On inspection of the yard, observed that, Rph limb of 220kV shobha dreams line breaker (SIEMENS make, 3Ap1F1 type, DOC:31.08.2008) had flashed over. Due to this, Rph breaker isolator (289C) male arm along with rigid bus collapsed. Also, the dropper jump connected to Rph CT has been disconnected and damaged the Post Insulators of the isolators of the same bay. At the same time, Bph rigid bus pipe connected between the circuit breaker & the line isolator of adjacent 220kV HAL line-1 has been collapsed and tripped on Main II relay at 13:41hrs:Fault location: -91.64mtr, IA:221A, IB:871A, IC:10.20kA. Zone-4 operated. Also, the supporting structure of the breaker isolator (289C) has been chipped out. For re-connection of Bph rigid bus pipe along with supporting insulator, HAL line-1 LC availed on 24.08.2025 at 15:00hrs. Hired heavy duty crane with man lifter reconnected the rigid bus pipe. Also replaced the damaged R& Y ph post insulators of 289C breaker isolator and the line charged at 06:21hrs (25.08.2025). Loads normalized. | KPTCL to rectify the DR time synchronization issue at HOODY - 220KV | KPTCL | Puspha:KPTCL: 07/11/2025 03:22:01: GPS equipment provided recently under R&M works is not working. Issue reffered to OEM Masibus . OEM has o visit the site and rectify the issue. Puspha:KPTCL: 07/11/2025 22:16:26: GPS device issue is yet to be rectified by the OEM Puspha:KPTCL: 06/01/2026 22:07:05: M/s SANDs make newGPS equipment is procured, for commissioning deputation of service personnel by OEM is awaited Puspha:KPTCL: 06/01/2026 22:08:12: M/s SANDs make GPS equipment is procured the same will be put in to service wiith OEM support | Complied | Complied
135/VI/3 | JAGALUR - 220KV | 26-08-2025 12:15 | 220kV BUS Coupler breaker tripped on OC/EF relay due to persistant arcover in 89A isolator of 220kV Kudligi-2 line | KPTCL to rectify the DR time synchronization issue at JAGALUR - 220KV | KPTCL | Puspha:KPTCL: 07/11/2025 19:40:36: GPS time synchronization of individual relays verified on 07.11.2025 and found to be healthy at Jagalur substation | Complied | Complied
135/VI/7 | 220KV-AMBEWADI-PONDA-2 | 08-09-2025 12:27 | Distance protection relay operated, Auto reclose lockout | KPTCL to rectify the DR time synchronization issue at AMBEWADI - 220KV | KPTCL | Puspha:KPTCL: 07/11/2025 19:39:22: GPS device and time synchronization of relays is in heathy condition at Ambewadi SS Puspha:KPTCL: 06/01/2026 22:04:59: GPS time synchronisation for protection relays are in healthy working condition at Ambewadi SS | Complied | Complied
135/VI/12 | KALABURAGI - 400KV | 08-09-2025 15:15 | KALABURAGI - 400KV | KPTCL to rectify the DR time synchronization issue at KALABURAGI - 400KV | KPTCL | Puspha:KPTCL: 07/11/2025 19:37:12: At Kalaburgi, GPS time sync equipment is in heathy condition. Time synchronization of all numerical relays verified and found to working satisfactory Puspha:KPTCL: 06/01/2026 22:03:46: GPS time synchronisation for protection relays is in healthy working condition at Kalaburgi 400kV SS | Complied | Complied
135/VI/16 | 220KV-YERRAANDAHALLI-HOSUR-1 | 10-09-2025 01:37 | 220KV-YERRAANDAHALLI-HOSUR-1 | KPTCL to rectify the DR time synchronization issue at YERRAANDAHALLI - 220KV | KPTCL | Puspha:KPTCL: 07/11/2025 22:21:04: Yet to be attended | Pending | Pending
136/I/2 | Complete Outage of 220kV ITI SS of KPTCL | 25-09-2025 14:11 | During antecedent conditions, 220kV Manyata ITI was open. 220kV ITI SS was being radially fed through 220kV Hoody ITI line. As per the reports submitted, the triggering incident was R-N fault in 220kV Hoody ITI line and the line tripped. Tripping of the only connected line led to complete outage of 220kV ITI SS | 1.KPTCL to provide LDP for 220kV Hoody ITI line. 2.KPTCL to rectify the DR time sync issue at Hoody SS. | KPTCL | Puspha:KPTCL: 03/12/2025 22:37:21: For Hoody-ITI line LDP is available due to communication failure it is working in distance mode. Action will be taken to rectifythe communication issue Puspha:KPTCL: 04/12/2025 17:13:15: Line Differential protection is provided at both the ends, communication between both end relays is to be restored. GPS issue of Hoody SS will be rectified | Pending | Pending
136/I/4 | Complete Outage of 220kV Bagewadi SS, 220kV Atria and 220kV Fortune generating stations of KPTCL | 28-09-2025 10:23 | As per the reports submitted, the triggering incident was overloading of the 220 kV RTPS Lingsugur 1, 220 kV Lingsugur Malat, and 220 kV Lingsugur Shahpur lines. These lines subsequently tripped due to overloading, forcing the generation in the pocket to be evacuated through BB Wadi. Due to arcing, the operator at 220kV BB Wadi manually tripped all lines, leading to a complete outage of BB Wadi and the radially connected generating stations 220kV Atria and 220kV Fortune | 1.KPTCL to disable the OC for 220kV lines. 2.SRLDC to furnish the learnings for the event and in particular the Siemens relay PSL logics related to over current. 3.SPS may be worked by Karnataka SLDC. 4.Feedback to Planning Division for system strengthening. | KPTCL | Puspha:KPTCL: 03/12/2025 22:37:21: 1. Attended Puspha:KPTCL: 04/12/2025 17:17:54: OCR disabled for all 220kV lines in this corridor | Complied | Complied
136/I/5 | Complete outage of 220kV Tataguni, KIADB-Harohalli and Kankapura and Tripping of Bus-A1 of Somanahalli station. | 03-10-2025 15:55 | The triggering incident is the Y G bus fault occurred in Somanahally Harohally line bay due to failure of Y phase cross bus insulator string before the CT of the line (can be confirmed from the DR of Somanahally-Harohally line at Somanahally). Since the BBP is in disabled condition and BBP protection in not available, multiple lines tripped on Z4 and 500MVA Somanahally ICT 1 tripped on OC protection operation and led to the Complete outage of KIADB Harohalli and Kankapura station. The event led to the Complete outage of 220kV Tataguni, KIADB Harohalli and Kankapura and Tripping of Bus A1 of Somanahalli station. | 1.KPTCL to furnish a detailed report after consulation with OEM regarding the ZONE-1 trip at Keonics end. 2.All the distance protection settings may be verified. | KPTCL | Puspha:KPTCL: 03/12/2025 22:37:21: Setting files and DR files are furnished to OEM M/s SIFANG, reply awaited. The matter is being ersued with OEM M/s SIFANG Puspha:KPTCL: 04/12/2025 17:17:54: The setting files /DR files of SIfang make main 1 relay is referred to OEM. Reply awaited from the OEM M/s SIFANG. The matter is being perused with OEM. After receipt of OEM recommendations testing of the relay will be taken up. Puspha:KPTCL: 05/04/2026 19:07:11: Rectified . AR issue attended by configuring tie CB status to the relays since the line is charged through Tie CB | Complied | Pending
136/I/13 | Complete Outage of 220kv Ranebennur SS of KPTCL | 12-10-2025 13:13 | During antecedent conditions, 220kV Ranebennur Shiralkoppa line was under open condition and 220kV Ranebenur SS was being radially fed from 220kV Guttur SS. As per the reports submitted, the triggering incident was BN fault in 220kV Guttur Ranebennur line and the line tripped. Tripping of the only connected line led to complete outage of 220kV Ranebennur SS. | KPTCL may rectify Time sync issue at Ranebennur. | KPTCL | Puspha:KPTCL: 03/12/2025 22:37:21: Attended Puspha:KPTCL: 04/12/2025 17:17:54: Attended and complied during the meeting | Complied | Complied
136/III/5 | 400KV/220KV NELAMANGALA-ICT-2 | 06-10-2025 06:42 | As per the reports submitted, due to an accidental trip extension from the 220kV single-pole isolator auxiliary switch, which belongs to the R-phase autotransformer that is currently out of service. The ICT-2 was in a SYB combination, where the spare autotransformer is considered as the R-phase | KPTCL to check the healthiness of all the isolator auxiliary switches at 400KV/220KV Nelamangala. | KPTCL | Puspha:KPTCL: 03/12/2025 22:37:21: Attended Puspha:KPTCL: 04/12/2025 17:17:54: Attended | Complied | Complied
136/IV/8 | 400KV-GUTTUR-BTPS-1 | 08-10-2025 16:35 | As per the reports submitted, the triggering incident was B-G fault in the line due to B PH insulator found failed at location no 659 as B-phase insulator flashover. The fault distance from Guttur end was 46.98kms and from BTPS end was 110kms. At Guttur end, the line tripped on operation of Z1 distance protection, at the same time DC fuses blown out resulting in no DC supply and hence AR did not operate. At BTPS end, the line tripped due to operation of Z1 distance protection. Since the line was in charged condition through Tie breaker 410-52 where in AR was disabled in Tie breaker, AR did not get operated and 3ph tripped. | KPTCL to rectify the non-operation of A/R at Guttur. | KPTCL | Puspha:KPTCL: 03/12/2025 22:37:21: Visit of firm engineers expected during next week to rectify the issue Puspha:KPTCL: 04/12/2025 17:17:54: Scheduled outage of the line will be taken for testing of AR scheme at Guttur end | Pending | Pending
136/VI/1 | 220KV-HOODY-ITI-1 | 25-09-2025 14:11 | 220KV-HOODY-ITI-1 | KPTCL to rectify the DR Time Synchronization Issue at HOODY - 220KV. | KPTCL | Puspha:KPTCL: 03/12/2025 22:37:21: Earlier due to problem with GPS antenna POwas placed and new attena was provided. However due to compatibilty issue GPS time sync issue was not resolved. Now action has been taken by EEE, Operation Division Hoody to replace the GPS unit by placing the PO on OEM M/s Masibus Puspha:KPTCL: 05/04/2026 19:05:52: Attended , New GPS equipment is provided at Hoody 220 | Complied | Pending
136/VI/10 | 400KV/220KV GUTTUR-ICT-1 | 27-09-2025 09:30 | GUTTUR - 400KV | KPTCL to rectify the DR Time Synchronization Issue at GUTTUR - 400KV. | KPTCL | Puspha:KPTCL: 03/12/2025 22:37:21: M/s Maverik Facility Management Private Limited (Authorised Channel Partner for GE T&D India Limited) Bengaluru to visit the site with the service person and they have assured to visit the site in the next week to verify the relays parameters & network. After the site visit by the firm service engineer . Puspha:KPTCL: 05/04/2026 19:03:36: GPS time sync network issue at Guttur has been rectified. Except few old version relays GPS time synchronisation is established for the protection relays at Guttur | Complied | Pending
136/VI/15 | 220KV-SOMANAHALLI-ELECTRONIC_CITY-1 | 03-10-2025 15:55 | SOMANAHALLI - 220KV | KPTCL to rectify the DR Time Synchronization issue at SOMANAHALLI - 220KV. | KPTCL | Puspha:KPTCL: 03/12/2025 22:37:21: GPSis provided under R&U works. Integration of M2 relays to SAS and time synchronisation of relays will be carried out as part of R&M works Puspha:KPTCL: 05/04/2026 19:05:11: GPS device is provided. M1 relays of 220kV lines are time synchronized. M2 relay SAS integration and GPS time synchronization will be taken up | Complied | Pending
136/VI/19 | 220KV-AMBEWADI-XELDEM-1 | 05-10-2025 12:51 | AMBEWADI - 220KV | KPTCL to rectify the DR Time Synchronization Issue at AMBEWADI - 220KV. | KPTCL | Puspha:KPTCL: 03/12/2025 22:37:21: GPS, time synchronisation for individual relays is in healthy working condition at Ambewadi substation | Complied | Complied
136/VI/35 | 220KV-GUTTUR-RANEBENNUR-1 | 12-10-2025 13:13 | RANEBENNUR - 220KV | KPTCL to rectify the DR Time Synchronization issue at RANEBENNUR - 220KV. | KPTCL | Puspha:KPTCL: 03/12/2025 22:37:21: Rectified. GPS time synchronisation of relays at Ranebennur is working fine. | Complied | Complied
137/I/6 | Complete Outage 400kV UPCL Generating Station of Adani, 220kV Kavoor SS, 220kV Kemar SS, 220kV Puttur SS and 220kV MSEZ SS of KPTCL. | 18-10-2025 17:12 | As per the reports submitted, 400kV UPCL Hebbanahalli Line-1&2 tripped on B-N fault at 16:27hrs. Subsequently, 220kV Kemar Varahi Line-1&2 tripped on YB-N fault at 17:09hrs and 220kV Kemar Heggunje line tripped on RYB-N fault at 17:13hrs. Tripping of all these lines led to complete outage of 400kV UPCL Generating Station, 220kV Kavoor SS, 220kV Kemar SS, 220kV Puttur SS and 220kV MSEZ SS | 1.KPTCL to rectify the DR time sync issue at Kemar end. 2.KPTCL to verify the tower footing resistance for 400kV UPCL-Hebbanahally lines and submit a detailed report. 3.KPTCL to furnish the relay settings at Hebbanlalli end for analysis by PSSG | KPTCL | Puspha:KPTCL: 06/01/2026 22:13:57: Measurement of tower footing resistance is communicated to field and the same is under progress. | Pending | Pending
137/I/13 | Complete Outage of 220kV Exora SS, 220kV Vikas Tech and 220kV Bus-1 Outage at 220kV Malur SS of KPTCL | 20-11-2025 11:32 | 220kV Malur SS was operating with split bus condition with 220kV Hoody Malur line feeding 220kV Malur Bus-1. 220kV/66kV Exora and 220kV/66kV Vikas Tech Park were being radially fed from 220kV Malur Bus-1. As per the reports submitted, the triggering incident was R-G fault in 220kV Hoody Malur line. Tripping of this line led to loss of power supply to 220kV Malur Bus-1 which intrun led to complete outage of 220kV Exora SS and 220kV Vikas Tech Park. | 1.KPTCL to rectify the DR time sync issue at Malur and Hoody end. 2.KPTCL to configure DR at Malur as per FOLD committee recommendation. | KPTCL | Puspha:KPTCL: 06/01/2026 22:12:44: At Hoody new GPS equipment has been procured the same will be put in to service. At Malur , recently revised settings have been issued for Hoody and Kolar lines. WHile implementing the revised settings and during testing DR configuration will be updated and also time drift in relays w.r.t GPSclock will be rectified | Complied | Complied
137/VI/1 | 220KV-KADAKOLA-KANIYAMPETTA | 23-10-2025 11:01 | 220KV-KADAKOLA-KANIYAMPETTA | KPTCL to rectify the DR time synchronization issue at KADAKOLA - 220KV. | KPTCL | Puspha:KPTCL: 06/01/2026 22:10:11: Will be rectified with OEM support Puspha:KPTCL: 03/02/2026 15:29:08: Except Siemens relays GPS time synchronisation is ensured for all other numerical relays in Kadakola | Pending | Pending
137/VI/4 | 220KV-AMBEWADI-PONDA-2 | 24-10-2025 13:36 | 220KV-AMBEWADI-PONDA-2 | KPTCL to rectify the DR time synchronization issue at AMBEWADI - 220KV. | KPTCL | Puspha:KPTCL: 06/01/2026 22:01:29: GPS time sync equipment is in healthy working condition at Ambewadi | Complied | Complied
138/I/1 | Complete Outage of 220kV Davanagere, Benkikere, Hosadurga, Neelagunda, Ranebennur, Haveri, Guttur SAS and Tripping of Bus-1 and 2 at Guttur and Bus-2 at Honnali of KPTCL | 25-11-2025 11:12 | In the antecedent conditions, 220kV Neelagunda-Ittagi, 220kV Ranebennur-Shiralkoppa was under outage condition and Honnali was under bus split condition where in Bus-2 is connected to Davanagere and Benkikere. The triggering incident is the failure of Y-ph LV side LA of 400KV/220KV GUTTUR-ICT-2 leading to the tripping of the ICT-2 on differential protection, during the same time 400KV/220KV GUTTUR-ICT-1 also tripped on OLTC Y Ph OSR operation. With the tripping of both the 400KV/220KV GUTTUR-ICT-1&2 led to the overloading of 220KV-HAVERI-SHIGGAON-1&2 and 220KV-GUTTUR-Chitradurga-1 and subsequently led to the tripping of these lines and leading to the Complete Outage of 220kV Davanagere, Benkikere, Hosadurga, Neelagunda, Ranebennur, Haveri and Tripping of Bus-1 and 2 at Guttur and Bus-2 at Honnali of KPTCL | 1.KPTCL to rectify the DR time sync at Guttur & Haveri SS. 2.DR heathiness to be ensured for all stations. 3.KPTCL to disable Overcurrent protection for 220kV lines . 4.KPTCL to furish the relay settings details in DMNS portal for Haveri Shiggon line. | KPTCL | Puspha:KPTCL: 03/02/2026 15:24:35: 1. For Guttur GPS issue , visit of GE engineers is awaited. 2. GPS equipment was faulty , it is sent to OEM M/s SANDS factory at chennai Puspha:KPTCL: 04/02/2026 08:24:32: 4. Repplacement of SEL make Main1 relay by new relay(ZIV)) is pplanned for Shiggaon 1 &2 lines at Haveri end. Settings are issued for new relays. Shortly the relays are going to be replaced. Along with relay replacement new settings and network configuration changes will be updated to PMS by raising ticket through DMNS | Pending | Pending
138/VI/5 | 400KV/220KV GUTTUR-ICT-1 | 25-11-2025 11:12 | DR time synchronization issue at GUTTUR - 220KV and 400kV | KPTCL to rectify the DR time synchronization issue at GUTTUR - 220KV and 400kV | KPTCL | Puspha:KPTCL: 03/02/2026 15:22:43: Visit of GE engineers to Guttur substation is awaited | Pending | Pending
138/VI/6 | 220KV-GUTTUR-Chitradurga-1 | 25-11-2025 11:16 | DR time synchronization issue at Chitradurga - 220KV | KPTCL to rectify the DR time synchronization issue at Chitradurga - 220KV | KPTCL | Puspha:KPTCL: 03/02/2026 15:26:03: 3. OCR disabling for 220kV lines is in progress.Presently OCR is diabled for more than 300 lines | Pending | Pending
139/I/4 | Complete outage of 220kV Chikkodi SS of KTPCL | 05-01-2026 02:50 | As per the reports submitted, the triggering incident is the failure of R-ph PT of 220kV Bus-1 at Chikkodi end, during which all the elements connected to Chikkodi tripped leading to complete outage of 220kV Chikkodi SS | 1. KPTCL to rectify the DR time sync issue at Chikkodi. 2.KPTCL to submit equipment failure report to CEA. 3.KPTCL to conduct Earthmat integrity test of Chikkodi SS. | KPTCL | Puspha:KPTCL: 05/03/2026 12:50:36: 1. GPS Puspha:KPTCL: 05/03/2026 13:06:25: 1. The faulty GPS device is to be sent to OEM factory at Chennai, directions have been given to concerned substation. 2. PT failure report will be sent to CEA by concerned substation, being pursued with the site 3. Deputation of engineers for conducting earthmat integrity check of Chikkodi Substation is delayed due to commissioning works. During April 2026, the testing team will vist Chikkodi substation and conduct earthmat integrity test Puspha:KPTCL: 05/04/2026 18:54:35: 1,2 &3 yet to be implemented | Pending | Pending
139/I/6 | Complete Outage of 220kV Adakanahalli, Chamarajanagar RS, Begur RS, Madhuvanahalli RS, Hebbani RS and Bus outage of 220kV TK Halli RS and Vajamangala RS | 15-01-2026 09:03 | In the antecedent condition, 220 kV Hootagalli-Vajamangala was under outage and bus split operation at 220kV TKHalli leading to the entire load of the vicinity was through 220kV Kadakola-Adakanahalli-1&2. The triggering incident is the BBP operation at Adakanahalli SS leading to the tripping of 220kV Adakanahalli Bus-2. After which due to subsequent over loading led to tripping of the lines and led to the Complete Outage of 220kV Adakanahalli RS, 220kV Chamarajanagar RS, 220kV Begur RS, 220kV Madhuvanahalli RS, 220kV Hebbani RS and partial outage of 220kV TK Halli RS and 220kV Vajamangala RS | 1. KPTCL to disable Over current logic for 220kV lines. 2. KPTCL to rectify the BBP issue at Adakanahally SS. | KPTCL | Puspha:KPTCL: 05/03/2026 12:50:36: 1. OCR disabled for all 220kV lines in Mysore Operation Zone. 2. For Busbar scheme testing OEM support has been requested, Visit of GE Engineers to the site is awaited Puspha:KPTCL: 05/04/2026 18:56:06: 1. Attended. OCR is disabled for all 220kV lines in Mysore Zone. 2. BBP has been put back to service after rectifying the issue | Complied | Complied
139/III/1 | 400KV/220KV GUTTUR-ICT-2 | 22-12-2025 09:23 | As per the reports submitted, at Guttur end 315MVA ICT-2 Tripped on Differential protection due to differential fault created by monkey which was within the 33kV induction zone (FIR) & 3-ph tripped in HV and LV side. As per the information from KPTCL, arching over 33kV side cleaned other than that no abnormalities found. | KPTCL has been advised to take the necessary actions to control the monkeys near the substation. | KPTCL | Puspha:KPTCL: 05/03/2026 12:50:36: Directions have been given to Guttur Substation regarding switchyard maintenance issues | Complied | Complied
139/III/11 | 400KV-GUTTUR-HIRIYUR-1 | 19-01-2026 16:19 | As per the reports submitted, the 400 kV Guttur- Hiriyur -1 Line tripped at Guttur end only due to momentary DC earthing (as per FIR) and no protection operated or DR was triggered for the event. At Hiriyur end, the line was in service. | KPTCL to check the healthiness of the all the cables at Guttur SS. | KPTCL | Puspha:KPTCL: 05/03/2026 12:50:36: The scheduled outage of the line will be obtained by the substation by raising request for OCC approval Puspha:KPTCL: 05/04/2026 18:58:16: Control cables between CRP-CB are checked and found OK. Also, DC sources grounding issue is rectified after the incident | Complied | Pending
139/VI/1 | 400KV/220KV GUTTUR-ICT-2 | 22-12-2025 09:23 | 400KV/220KV GUTTUR-ICT-2 | KPTCL to rectify the DR time synchronization issue at 400kV Guttur | KPTCL | Puspha:KPTCL: 05/03/2026 12:50:36: At Guttur GPS is in working condition, Except few old version relays GPS time synchronisation was healthy. Due to issue with substation level relay network presently relay clocks are not time synchronised. To resolve the issue following action has been taken 1). Station level relay network issue will be attended by the agency M/s Kalkitech scheduled during 3rd week of March. For resolving issue with some of the relays of GE make, deputation of GE engineers have been requested. However due to commissioing activities vist of GE engineers is yet to be finalised | Pending | Pending
139/VI/6 | 220KV-RAICHUR_KA-UPPER_JURALA-2 | 29-12-2025 01:07 | 220KV-RAICHUR_KA-UPPER_JURALA-2 | KPTCL to rectify the DR time synchronization issue at RAICHUR_KA - 220KV | KPTCL | Puspha:KPTCL: 05/03/2026 13:12:09: Attended. new GPS equipment is provided at Raichur 220kV SS and time synchronisation of relays have been attended | Complied | Complied
139/VI/6 | 220KV-AMBEWADI-XELDEM-1 | 31-12-2025 13:22 | 220KV-AMBEWADI-XELDEM-1 | KPTCL to rectify the DR time synchronization issue at AMBEWADI - 220KV | KPTCL | Puspha:KPTCL: 05/03/2026 12:50:36: GPS is in working condition at Amewadi Substation. Relays are time synchronised with GPS clock, minor time drift observed is reffered to GPS OEM SANDS Ltd for rectification | Pending | Pending
139/VI/15 | 220KV-KADAKOLA-KANIYAMPETTA | 18-01-2026 12:39 | 220KV-KADAKOLA-KANIYAMPETTA | KPTCL to rectify the DR time synchronization issue at KADAKOLA - 220KV | KPTCL | Puspha:KPTCL: 05/03/2026 12:50:36: GPS clock is working only Siemens relays have time sync issue at Kadakola. Issue with Siemens make relays will be rectified in consultation with relay OEM. | Pending | Pending
140/I/5 | Complete outage of 220kV Guttur SAS, Neelagunda and Tripping of 220kV Bus-1 of Guttur SS of KPTCL | 02-02-2026 01:31 | In the antecedent conditions, 220kV Neelagunda-Ittagi was under idle charged condition from Neelagunda end and hence 220kV Neelagunda is radially connected to 220kV Guttur SS. 220kV Guttur SAS is connected to Bus-1 at Guttur SS. The triggering incident is the failure of B-ph CT in 220KV-GUTTUR-DAVANGERE-2 at GUTTUR end leading to Bus bar protection operation and tripping of all the elements connected to Bus-1 at Guttur SS. Since 220kV Neelagunda and Guttur SAS are only connected Bus-1, with the tripping of Bus-1 led to the complete outage of 220kV Neelagunda and Guttur SAS station. | 1. KPTCL to rectify the DR time sync issue at Guttur SS. 2. KPTCL to verify the Carrier wiring of all lines in Guttur SS. 3. KPTCL to furnish CT failure report to CEA. | KPTCL | Puspha:KPTCL: 05/04/2026 18:53:35: 1. Attended 2,Carrier issue attended and ascertained through end to end test 3.r Failure report is sent to CEA | Complied | Complied
140/I/8 | Complete Outage of 220kV Orient Cement and Tripping of 220kV Bus-1 of 220kV Sedam SS of KPTCL | 10-02-2026 15:15 | 220kV Orient cement is radially fed from 220kV Bus-1 of Sedam SS. As per the reports submitted, at 220kV Sedam SS, while attending to the issue on Line CB of 220kV Sedam Ramasamudra Line-1, the breaker was hand-tripped. During hand tripping, the Y and B poles opened, however, the R pole did not open. Subsequently, 86 A & B operated due to the operation of IN>2 only in the M1 (P442 relay) with a definite time delay of 2s but still the breaker did not open and LBB was initiated. Due to the non-opening of the R phase limb, LBB operated and tripped all the elements connected to 220 kV Bus-1. The bus coupler was already in the open condition. Tripping of 220kv Sedam Bus-1 led to complete outage of 220kV Orient Cement. | 1. KPTCL to configure DR as per FOLD Committee recommendations at Sedam SS. 2. KPTCL to rectify the DT issue for LBB operation at Sedam SS. 3. KPTCL to verify the VT fuse fail logic for all feeders at Sedam SS. | KPTCL | Puspha:KPTCL: 05/04/2026 19:02:17: 1. DR configuration will be verified and impement as per the standard signal list given by SRPC earlier. 2. For DT configuration for LBB, OPGW link is to be established 3. Attended. VTF logic reviewed in other lines in Sedam | Pending | Pending
140/II/4 | Tripping of 400kV Bus-2 of 400kV Talaguppa SS of KPTCL | 07-02-2026 06:28 | As per the reports submitted, while hand-tripping the 125 MVAR Bus Reactor-2, the Bus Reactor-2 circuit breaker (CB-410R.52) experienced a flashover on the R-phase limb, and the R-phase lightning arrester also flashed over. Immediately, it was suspected that the LBB protection of the bus reactor operated, resulting in the tripping of all main breakers connected to the 400 kV Talaguppa Bus-2. However, a DT was sent to the remote ends of the 400 kV Talaguppa Hassan line and 400 kV Talaguppa Nelamangala lines. At the remote ends, the lines tripped, and due to a rise in voltage, the overvoltage protection operated after 8 seconds. Subsequently, a DT was sent to the Talaguppa end, causing the tripping of the tie breakers of these lines, and the lines tripped. | KPTCL to review the relay settings at 400kV Tallagupp SS. | KPTCL | Puspha:KPTCL: 05/04/2026 18:51:40: Relay settings at Talaguppa are verified and it is in order | Complied | Pending
140/III/15 | Multiple trippings at 400/220kV Guttur SS | 13-02-2026 15:00 | As per the reports submitted, the triggering incident is the R-G fault in Guttur-Haveri-1 line. At Guttur end, the fault was sensed in Main-1 in Z2 only as the Main-2 was out of service during the event. However even after sensing the fault in Z2 and 86A/B operated after around 350 ms (Z2 time trip), trip was not extended to the breakers (as per DR) and also LBB did not operate and hence the fault continued to be fed, after which ICT-1 and ICT-2 tripped at Guttur end on EF protection operated where in 400/220kV ICT-1, IN>1 operated around 100 ms prior to that of 400/220kV ICT-2 at around 15:01:22:840 Hrs. With the tripping of the ICTs, the fault continues to be fed through 220kV side and eventually fault developed into R-Y-G fault in Z1 and 3 ph tripped to clear the fault. In the antecedent condition, 220kV Guttur-Haveri lines were under idle charged condition from Guttur end. | 1. KPTCL to rectify the time synchronization issue at Guttur SS. 2. KPTCL was advised to ensure the availability of the Main2 relay for the 220 kV Guttur Haveri Line2 at the earliest. | KPTCL | Puspha:KPTCL: 05/04/2026 18:50:53: 1. Attended. 2, Main-2 relay power supply card is used to 400kV line. Action is taken to procure power supply cards from the OEM on proprietary basis. | Pending | Pending
140/VI/6 | 220KV-CHIKKODI-TALANGADE | 29-01-2026 11:23 | 220KV-CHIKKODI-TALANGADE | KPTCL to rectify the DR time synchronization issue at CHIKKODI - 220KV | KPTCL |  | Pending | Pending
140/VI/10 | 220KV-AMBEWADI-PONDA-2 | 05-02-2026 14:09 | 220KV-AMBEWADI-PONDA-2 | KPTCL to rectify the DR time synchronization issue at AMBEWADI - 220KV | KPTCL | Puspha:KPTCL: 05/04/2026 18:48:36: GPS is in working condition. relays are time synchronized. Few msec difference only | Complied | Complied
140/VI/12 | TALGUPPA - 400KV | 07-02-2026 06:28 | TALGUPPA - 400KV | KPTCL to rectify the DR time synchronization issue at TALGUPPA - 400KV | KPTCL | Puspha:KPTCL: 05/04/2026 18:48:36: GPS is in working condition at Talaguppa 400kV SS | Complied | Complied
140/VI/16 | 400KV/220KV GUTTUR-ICT-2 | 13-02-2026 15:09 | 400KV/220KV GUTTUR-ICT-2 | KPTCL advised to rectify the DR time synchronization issue at GUTTUR - 400KV at the earliest | KPTCL | Puspha:KPTCL: 05/04/2026 18:46:25: Attended. GPS time synchronization of relays restored except few old version relays having limitations | Pending | Pending
141/I/2 | Complete outage 220kV GM Navar SS and Tripping of 220kV Bus-2 at 220kV Nandhihal of KPTCL | 28-02-2026 15:03 | 220kV GMNavar is radially connected to 220kV Nandhihal through 220kV GMNavar- Nandhihal-1&2. In the antecedent conditions, 220kV GMNavar- Nandhihal-1&2 was connected to 220kV Bus-2 at Nandhihal. The triggering incident is the Y-ph isolator contact failure in 220kV Nandhihal-Kudgi line-5 which came into vicinity of 220kV Nandhihal-Kudgi line-3 creating a Y-B phase bus fault in 220kV Bus-2 at Nandhihal. This led to the BBP operation and tripping of all the elements connected to 220kV Bus-2 at 220kV Nandhihal and led to the Complete outage 220kV GM Navar SS | KPTCL to review the protection settings at Nandihal SS and submit a report in this regard. | KPTCL |  | Pending | Pending
141/I/3 | Complete outage of 220 kV Aheri, Nimbarga, Vaishali, Shahbad, Kapnoor, Humnabad, Gulbarga, and Santhapur and tripping of 220 kV Bijapur Bus-2, Shahpur Bus-2, Sedam Bus-2, and Bus-1 & Bus-2 at Kalburgi of KPTCL | 03-03-2026 11:00 | In the antecedent conditions, multiple bus splits were carried out in the vicinity of 400/220 kV Kalburgi substation to facilitate evacuation of RE power. The triggering incident was the tripping of 400/220kV ICT-1 and 2 at Kalburgi substation. Since multiple substations evacuate power through Kalburgi, the tripping of the evacuation path led to the complete outage of 220 kV Aheri, Nimbarga, Vaishali, Shahbad, Kapnoor, Humnabad, Gulbarga, and Santhapur and tripping of 220 kV Bijapur Bus-2, Shahpur Bus-2, Sedam Bus-2, and Bus-1 & Bus-2 at Ferozabad (Kalburgi) of KPTCL. | 1.KPTCL to submit the report on LVRT compliance during the event. 2.KPTCL to review ICT over current settings at Kalaburgi SS. 3.KPTCL to install PMU at Kalaburgi SS. | KPTCL |  | Pending | Pending
141/I/4 | Complete Outage of 220kV Nagamangala, Anchepalya and Magadi SS of KPTCL | 05-03-2026 13:48 | 220kV Nagamangala SS, 220kV Anchepalya SS, and 220kV Magadi SS are being radially fed from the 220kV Nelamangala Anchepalya line and the 220kV Nelamangala Magadi line. The triggering incident was a B-G fault in the 220kV Nelamangala Anchepalya line and the line tripped and after which 220kV Nelamangala Magadi line tripped on over current protection. WIth the tripping of 220kV Nelamangala Anchepalya and 220kV Nelamangala Magadi line led to the Complete Outage of 220kV Nagamangala, Anchepalya and Magadi SS of KPTCL | 1.KPTCL to disable Over current logic for 220kV lines at Neelamangala , Anchenpalya SS. 2.KPTCL to verify the Over current relay rest settings at Neelamangala , Anchenpalya SS. | KPTCL |  | Pending | Pending
141/II/3 | Tripping of 400kV Bus-2 at RTPS of KPCL | 24-02-2026 04:27 | The triggering incident is the B-G bus fault in 400kV Bus-2 at RTPS. All the main breakers connected to Bus-2 got tripped and led to the tripping of 400kV Bus-2 at RTPS. 400kV RTPS-Munirabad was only in service with the main breaker connected to Bus-2 and due to the tripping of the Bus-2 led to the tripping of 400kV RTPS-Munirabad line. All other elements were in service through 400kV Bus-1. | KPCL to measure IR testing of BPI periodically. | KPCL |  | Pending | Pending
141/III/5 | 400KV-DONI-GUTTUR-1 | 01-03-2026 14:50 | The triggering incident is the tripping of the line only at GUTTUR end due to suspected DC earth fault. The line was holding at DONI end. | KPTCL to review the Healthiness of control cables at both 400kV Doni and Guttur SS. | KPTCL |  | Pending | Pending
141/VI/4 | 400KV-KAIGA-GUTTUR-2 | 24-02-2026 15:45 | Station at which DR time synchronisation was not observed : GUTTUR - 400KV | KPTCL to rectify the DR time synchronization issue at GUTTUR 400 KV | KPTCL |  | Pending | Pending
KERALA
109/II/1 | Tripping of 400/220 kV ICT-1 AT TRICHUR and 220kV TRICHUR CHALAKUDY LINE | 09-06-2023 1.33.00 PM | The triggering incident was Rphase insulator failure in 230kV Trichur Chalakudi line. At Trichur end, fault was sensed in Z1 and line tripped. At Chalakudi end, zone-2 protection operated and the line tripped with a delay of 420ms.At the same time, | KSEBL to expedite the communication link between Trichur Chalakudy stations for and implementation of the LDP for MDCH feeder at the earliest. KSEBL to update on the same to SRPC and SRLDC | KSEBL | aeldkseb:KSEB: 20/10/2023 14:21:56: Now communication link has been established and tele-protection with distance function enabled. Also enabled the AR function. LDP relay will be put in service after the refurbishment of C&R panels at Madakkathara end. aeldkseb:KSEB: 04/12/2023 16:28:12: communication link is now in service aeldkseb:KSEB: 03/02/2024 11:49:18: Communication link is now in service aeldkseb:KSEB: 07/05/2024 10:32:39: Complied aeldkseb:KSEB: 07/05/2024 11:01:07: Complied aeldkseb:KSEB: 04/07/2024 13:41:14: The issue was that the 220 kV Chalakudy - Madakkathara feeder was not having communication link at the time of that tripping on 09.06.2023 which led to delayed tripping (Zone2) at Chalakudy end. The communication link and tele-protection of the line with distance trip have been implemented about 6 months back and that issue was resolved. Also the AR put in service. LDP protection for the line will be implemented during the rennovation works at Madakkathara SS by doing the retrofitting of panels with LDP relays and this work is now not relevant as far as the issue led to that tripping is concerned. So this point may be closed. aeldkseb:KSEB: 05/08/2024 12:01:24: The same has been rectified. | Complied | Complied
108/I/22 | Complete Outage of 220kV/110kV Mylatty SS, 220kV/110kV Ambalathara SS and 220kV/110kV/33kV Taliparamba SS of KSEBL | 23-05-2023 7.03.00 PM | Supply failure occurred at 220 kV Mylathy & Ambalathara and Thaliparamba due to tripping of 220kV Kanhirode-Taliparamba & 220kV Kanhirode-Ambalthara feeders at 19:03Hrs. | KSEBL to analyse the event in detail and furnish a report in this regard. | KSEBL | aeldkseb:KSEB: 03/05/2024 11:20:59: Details of Event is missing aeldkseb:KSEB: 07/05/2024 10:32:39: Complied aeldkseb:KSEB: 30/05/2024 09:41:41: Complied aeldkseb:KSEB: 04/07/2024 15:58:02: 220kV Kanhiroded- Taliparamba autoreclosing function made available on Main2(Siemens 7SA611) also with effect from 18.05.2024. Autoreclose function in both Main 1 and Main2 relays tested and found satisfactory. aeldkseb:KSEB: 05/08/2024 12:29:26: 220kV Kanhirode- Taliparamba auto reclosing function made available on Main 2 (Siemens 7SA611) also with effect from 18.05.2024. Autoreclose function in both Main 1 and Main 2 relays tested and found satisfactory. | Complied | Complied
115/III/11 | Multiple trippings at 220kV Kochi SS | 08-01-2024 18:48 | 220kV Kochi- Bramhapuram-1 line tripped due to Line Diff trip at the same time 220 kV Kochi-Kalamassery Line 1 tripped on R-Y-G Flt. | KSEBL to expedite the replacement of the damaged cable. | KSEBL | aeldkseb:KSEB: 22/03/2024 10:42:30: The damaged connecting cable from IRIG-B GPS receiver to the relays (for 2COKL1 feeder) at 220 KV Substation has been replaced. Hence the time synchronization issue rectified. aeldkseb:KSEB: 07/05/2024 10:32:39: Complied aeldkseb:KSEB: 07/05/2024 10:59:22: Complied aeldkseb:KSEB: 07/05/2024 11:02:50: Complied | Complied | Complied
117/III/10 | Multiple trippings at 220kV/110kV Palakkad SS | 18-03-2024 10:21 | 110kV Bus coupler tripped on Earth fault protection. Subsequently, 220kV/110kV Palakkada ICT-1,2&3 tripped. | KSEBL to ensure all the substation operators to follow the SOP. | KSEBL | aeldkseb:KSEB: 03/05/2024 12:54:32: Strict instructions was given to operation wing to follow SOP and the same was discussed in the internal OCC meeting of KSEBL. | Complied | Complied
119/I/6 | Complete Outage of 220kV Kanniyampeta of KSEB | 03-05-2024 17:55 | 220kV Kanniyampeta is connected with two 220kV feeders (220kV Kadakola-Kanniyampeta and 220kV Kaniyampeta-Kunnamangalam). In the antecedent condition 220kV Kadakola-Kanniyampeta was idle charged from Kanniyampeta end. Hence the 220kV Kanniyampeta was connected to the grid only through 220kV Kunnamangalam single feeder | KSEBL to review SOTF setting at Kanniyampeta | KSEBL | aeldkseb:KSEB: 04/07/2024 15:58:02: SOTF settings reviewed.In Main 1& Main2 relays The SOTF function enabled with ZONE 2 pickup. The Zone 2 Ground fault Resistive reach setting has been revised from 66 % of load impedance to 80% of load impedance on 16-06-2024. During tne energisation the relay picked up with zone3 Ground fault. The resistive reach of Zone 3 was 80% of load impedance. | Complied | Complied
120/II/4 | Tripping of 220kV Bus-2 of 220kV/110kV Pothencode SS of KSEB | 25-05-2024 02:47 | As per the reports submitted, the triggering incident was Y-phase bus side insulator failure in 220kV Trivandrum Pothencode Line-4 at 220kV/110kV Pothencode SS causing a bus fault in 220kV Bus-2. Immediately BBP operated and all elements connected to bus-2 tripped. At Pothencode end Y-N fault was sensed and Bus Bar protection operated and DT was sent to remote ends | KSEBL to take up with Higher Management on renovation and modernisation of Protection systems. | KSEBL | aeldkseb:KSEB: 05/08/2024 11:20:23: KSEBL to take up with Higher Management on renovation & modernisation of Protection systems. aeldkseb:KSEB: 05/08/2024 11:32:53: KSEBL has given direction to resolve the related issues. | Complied | Complied
120/II/5 | Tripping of 220kV Bus-1 of 220kV Sabarigiri PH of KSEB | 25-05-2024 06:39 | As per the reports submitted, the triggering incident was R-N fault in 220kV Sabarigiri-Theni line. At Theni end the fault was sensed in Zone-1 with a fault current of 2.181kA and at a distance of 55.023km. A/R got operated and the line was holding. At Sabarigiri end the fault was sensed in Zone-1 with a fault current of 2.44kA and at a distance of 51.3km. However, breaker failed to open at Sabarigiri end leading to the LBB operation and tripping of all elements connected to Lower and Upper Bus-2 | KSEBL to carry out regular maintenance activities on SS auxiliary systems. | KSEBL | aeldkseb:KSEB: 05/08/2024 11:53:49: Now regular maintenance activites are being carried out on SS auxiliary systems aeldkseb:KSEB: 05/08/2024 12:21:19: The same has been rectified. Now regular maintenance activites are carried out on SS auxiliary sytems aeldkseb:KSEB: 05/08/2024 12:22:34: The same has been rectified. Now regular maintenance activites are carried out on SS auxiliary sytems | Complied | Complied
122/III/3 | Tripping of 400kV Tirunelveli-Kottayam-1 and 2 | 03-08-2024 16:50 | 400 KV TIRUNELVELI- KOTTYAM LINE 1 tripped at Tirunelveli end only on Zone-2 during the fault in Line-2. | KSBEL to verify the DR for the Toshiba relay for 400kV Kottayam-Tirunelveli lines | KSEBL | aeldkseb:KSEB: 03/10/2024 15:18:02: Revised the setting of DEF (200A/0.365 TMS). Revised the reach settings (resistive reach setting only) of both the Main 1&2 relays of 400kV feeders. aeldkseb:KSEB: 06/12/2024 16:27:16: Verified and found ok | Complied | Complied
122/III/3 | Tripping of 400kV Tirunelveli-Kottayam-1 and 2 | 03-08-2024 16:50 | 400 KV TIRUNELVELI- KOTTYAM LINE 1 tripped at Tirunelveli end only on Zone-2 during the fault in Line-2. | KSEBL to ensure that DEF settings need to drop once the distance relay picks up. | KSEBL | aeldkseb:KSEB: 03/10/2024 15:17:43: Thoroughly verified the DR of the Toshiba relay and remedial measures taken including revision in the DEF and resistive reach settings. aeldkseb:KSEB: 06/12/2024 16:24:28: The DEF Setting and the resistive reach settings updated as per the approved settings from SRPC PSSG. DEF definite time corrected as IDMT. DEF disabling during zone pick up unavailable with MICOM and Toshiba relays. Siemens relay updated. | Complied | Complied
122/III/3 | Tripping of 400kV Tirunelveli-Kottayam-1 and 2 | 03-08-2024 16:50 | 400 KV TIRUNELVELI- KOTTYAM LINE 1 tripped at Tirunelveli end only on Zone-2 during the fault in Line-2. | KSEBL to review CT and VT failures signal high in DR for 400kV Kottayam-Tirunelveli lines. | KSEBL | aeldkseb:KSEB: 04/10/2024 12:33:44: Corresponding revision is done in the DR of Toshiba relay of 4TNKO -2 feeder. The same will be done in the Toshiba relay of other 400kV feeders during the next shutdown itself. aeldkseb:KSEB: 06/12/2024 16:27:16: CT and VT failure signal high disabled on DR | Complied | Complied
123/II/6 | Tripping of 220kV Bus-2 of 400kV/220kV Madakathara SS of KSEB | 04-09-2024 20:17 | As per the reports submitted, Y-phase insulator on the 220 kV side in Bus Section 2B of the 220/110 Madakathara Transformer-2 experienced a flashover resulting in a bus fault. Immediately, Both Main-1 and Main-2 BBP of Bus -2 operated tripping all elements connected to 220kV Bus section 2-A and 2-B as both bus sections are connected through an isolator. | KSEBL to rectify the Main-2 BBP relay logic at their 400/220 kV Madakkathara station | KSEBL | aeldkseb:KSEB: 04/11/2024 13:09:00: Low Impedence numerical BBP Commissioning works by M/s GE is progressing at 400kV S/s Madakkathara. We have entrusted M/s GE to look into the maloperation of Main 2 GE B90 BBP relay of 220kV in between. aeldkseb:KSEB: 06/12/2024 14:58:24: The settings of the B90 GE relay downloaded and verified. It is found that present firmware is not equipped with current reversal guarding. Taken up with M/s GE for firmware upgradation. aeldkseb:KSEB: 03/01/2025 17:23:52: Taken it up with M/s GE, Not resolved aeldkseb:KSEB: 07/04/2025 12:27:34: Sir, Problem not resolved yet. Waiting for M/S GE Support. aeldkseb:KSEB: 20/08/2025 10:36:55: Sir problem not resolved yet, still waiting for M/s. GE support aeldkseb:KSEB: 03/11/2025 16:38:58: Sir, Status update waiting from the field. aeldkseb:KSEB: 03/02/2026 11:40:16: Sir, The GE Multilin B90 (Main-2 relay) mal-operated on two occasions. Hence, Main-2 has been disabled, and OEM support is awaited. | Pending | Pending
123/VI/9 | 400KV-TIRUNELVELI-KOTTAYAM-2 | 30-08-2024 21:59 | DR TIME SYNC ISSUE | KSEBL to rectify the DR Time synchronization issue at Kottayam Station | KSEBL | aeldkseb:KSEB: 04/11/2024 13:09:00: Taken up with M/s Thoshiba. Firmware / Software modification required. aeldkseb:KSEB: 06/12/2024 16:24:28: Toshiba relay is time synchronized. but the DR is on GMT. Taken up with M/s TOSHIBA. aeldkseb:KSEB: 03/01/2025 17:23:52: Taken it up with M/s Thoshiba, Not resolved aeldkseb:KSEB: 11/03/2025 14:37:36: Thoshiba relay is time synchronised. DR is time synchronised in GMT, adjusted the DR time synchronisation by 330 Minutes (5.30 Hrs), issue resolved. DR is synchronised in IST now. | Complied | Complied
125/III/3 | 400KV/220KV MADAKKATHARA-ICT-2 | 18-10-2024 08:28 | As per the reports submitted, the triggering incident was failure of Y-phase insulator of spare transformer which is charged through Madakathara ICT-2. immediately, ICT-2 differential protection operated ICT-2 tripped. The spare transformer connectivity is shown below. | KSEBL to furnish the reason for the insulator failure | KSEBL | aeldkseb:KSEB: 03/01/2025 17:23:52: It was an issue with that lot. Hence, the same was replaced with a new one | Complied | Complied
126/I/4 | Complete Outage of 220kV/110kV/33kV Punnapura SS of KSEB | 02-12-2024 08:43 | The triggering incident was failure of HV side Y-phase CT of 200MVA 220kV/110kV Transformer2 at Punnapura SS resulting in 220kV Bus-2 fault. Due to non-operation of BBP protection, fault was cleared by tripping of both 220kV lines at remote end. This resulted in complete outage of 220kV/110kV/33kV Punnapura SS of KSEB | 1.KSEBL to furnish the reason for the tripping of New Pallom to Pallom line during this event. 2.KSEBL to adhere to the CERC Regulatory Provisions and the Timelines. | KSEBL | aeldkseb:KSEB: 06/02/2025 10:22:25: 1. LBB timings are corrected to total of 200 milli seconds . Pallom tripping was due to the delay of LBB tripping 2. Given data | Complied | Complied
126/III/10 | 400KV/220KV KOTTAYAM-ICT-2 | 11-12-2024 12:53 | During antecedent conditions, 315MVA ICT 2 Tertiary winding feeds 315kVA 33kV/440V auxiliary transformer. As per the reports submitted, 400kV/220kV Kottayam ICT-2 tripped as Over Voltage to Ground occurred on 33kV Side while PET testing was in progress on 33kV/433V Auxiliary transformer and terminal equipment. 125MVAR Reactor and 33kV/433V Auxiliary transformer 2 was under permit work at Kottayam station. | KSEBL to follow SOP and furnish revised SOP to SRPC and SRLDC. | KSEBL | aeldkseb:KSEB: 06/02/2025 10:22:25: SOP Revised | Complied | Complied
128/I/3 | Complete Outage of 220kV/110kV Thlassery SS, 220kV/110kV Kanhirode SS, 220kV/110kV Ambalathara SS, 220kV/110kV Mylatti SS, 220kV/110kV Taliparamba SS and 220kV/110kV Orkattery SS of KSEB. | 27-01-2025 15:38 | 220kV/110kV Thlassery SS, 220kV/110kV Kanhirode SS, 220kV/110kV Ambalathara SS, 220kV/110kV Mylatti SS, 220kV/110kV Taliparamba SS and 220kV/110kV Orkattery SS are being radially connected through 220kV Areakode Orkattery and 220kV Areakode Kanhirode at 220kV level. During antecedent conditions, 220kV Areakode Kanhirode was under outage. The triggering incident was B-N fault in 220kV Areakode-Orakattery Line and the line tripped. Tripping of the only connected line led to the over loading of 110kV lines in the downstream and subsequently due to the tripping of 110kV lines on over loading, led to the Complete Outage of 220kV/110kV Thlassery SS, 220kV/110kV Kanhirode SS, 220kV/110kV Ambalathara SS, 220kV/110kV Mylatti SS, 220kV/110kV Taliparamba SS and 220kV/110kV Orkattery SS of KSEB. | 1.Standardization of DR settings (Sample Rate, Channels) to be implemented at both Areakode and Orkattery Substations 2.Correction of Auto-Reclose (A/R) logic for both Main-1 and Main-2 relays for all lines to ensure proper operation at Orkattery SS 3.Right of Way (ROW) maintenance to be ensured for all lines emanating from Areakode and Orkattery Substations to minimize faults due to sagging conductors or external interferences 4.KSEBL to review the reason for non-sensing of fault 220kV Orkattery-Areakode at Orkattery end by Main-1 relay 5.KSEBL to rectify the Pantograph isolator issue at Areakode | KSEBL | aeldkseb:KSEB: 07/04/2025 12:27:34: Sir, Direction given to field officers . The settings of 220KV Areacode Orkkattery will change along with the next shutdown of 2AROR. aeldkseb:KSEB: 02/09/2025 14:26:46: Sir, The pending recommendations have been addressed. Request you to please close this entry. | Complied | Complied
128/VI/15 | 220KV-THENI-SABARIGIRI-1 | 18-02-2025 11:05 | As per the reports submitted, the triggering incident was BN fault in the line. At Theni end, the linet ripped on operation of Zone-1 distance protection. At Sabarigiti end the line tripped on oepration of Zone-2, carrier-aided, distance protection. A/R operated but again the line tripped due to fault within the reclaim time. Tripping is in order. | 1.KSEBL to furnish a detailed analysis of the event. | KSEBL | aeldkseb:KSEB: 07/04/2025 12:27:34: Sir, Tripping is in order , aeldkseb:KSEB: 02/07/2025 11:52:21: Sir Tripping is in order you may please close this entry. | Complied | Complied
129/VI/24 | 220KV-KADAKOLA-KANIYAMPETTA | 12-03-2025 17:45 | As per the reports submitted, the triggering incident is the Y-N fault in the line. At both ends, the fault was sensed in Z1, and AR operated and tripped on persistent fault. There is a difference in dead time and needs review. | KSEBL to furnish the action taken report. | KSEBL | aeldkseb:KSEB: 05/06/2025 10:53:19: Sir, Awaiting for compliance report from the field. aeldkseb:KSEB: 28/06/2025 15:32:24: Sir, The dead time @ Kaniyampetta substation end revised to 1 sec, hence this may be closed. | Complied | Complied
30/III/9 | 220KV-THENI- SABARIGIRI-1 | 04-04-2025 17:13 | As per the reports furnished, the triggering incident was RB fault in the line. At Theni end, line tripped on operation of Zone-1 distance protection. At Sabarigiri end, fault was sensed in Zone-2 but carrier wasn't received. Failure of carrier aided protection at Sabarigiri end need review. | KSEBL to adjust the CB operating time at Sabarigiri station | KSEBL | aeldkseb:KSEB: 05/06/2025 10:47:03: Directions already given to Sabarigiri PH to correct their CB operating time. Awaiting the compliance report. aeldkseb:KSEB: 28/06/2025 16:36:52: Sir The rectified the problem you may please close this entry. | Complied | Complied
130/III/20 | 220KV-Kadakola- Kaniyambetta | 13-04-2025 13:56 | As per the reports submitted, the triggering incident is the R-N fault in the line. Data is not furnished from Kadakola end | 1.KSEBL to confirm AR operation at the Kaniyambetta SS. 2.KSEBL to increase the DR sample rate at Kaniyambetta. | KSEBL | aeldkseb:KSEB: 05/06/2025 10:40:48: AR operation confirmed. The PD time was below the single phase AR time delay, Corrected the settings. DR Sample rate is corrected, this may be closed. aeldkseb:KSEB: 20/08/2025 10:36:55: Sir, Rectified the problem , already reported to close this entry, hence please close . aeldkseb:KSEB: 03/11/2025 16:38:58: Sir, Rectified the problem , please close this entry. | Complied | Complied
130/VI/1 | PALAKKAD(KL) - 220KV | 21-03-2025 20:08 | DR time synchronization was not observed at PALAKKAD(KL) - 220KV | KSEBL to resolve the time synchronization issue | KSEBL | aeldkseb:KSEB: 05/06/2025 10:49:15: Sir The time synchronization issues resolved, you may please remove this entry. aeldkseb:KSEB: 28/06/2025 15:34:06: Sir The issue resolved you may please remove this entry | Complied | Complied
135/III/18 | 220KV-UDUMALPET-Pallivasal-1 | 18-09-2025 15:23 | As per the reports submitted, the triggering incident was RN fault in the line. The fault distance from Udumalpet was 19.6kms and from Pallivasal end it was 66.4kms. At Udumalpet end, the fault was sensed in Zone1 and AR operated and was successful and the line was holding. At Pallivasal end, the 220kV Pallivasal Udumalpet feeder tripped in Zone 1 trip but AR did not get operated and 3ph tripped as AR operated in Rph but Y and B phases got tripped. | KSEBL to check the PD time delay setting in all lines connected at Pallivasal SS. | KSEBL | aeldkseb:KSEB: 03/11/2025 16:38:58: Sir, PD timings of all lines connected to Pallivasal substation are corrected. Please close this entry. | Complied | Complied
137/I/3 | Complete Outage of 220kV Orkattery SS, 220kV Kanhirode SS, 220kV Thalaserry SS, 220kV Taliparamba SS, 220kV Ambalathara SS and 220kV Mylatty SS of KSEB | 16-10-2025 14:18 | 220kV Orkattery SS, 220kV Kanhirode SS, 220kV Thalaserry SS, 220kV Taliparamba SS, 220kV Ambalathara SS, 220kV Mylatty SS are being radially fed from 220kV Areakode Orkattery line and 220kV Areakode Kanhirode lines. As per the reports submitted, the triggering incident was YN fault in 220kV Areakode Orkattery line . A/R operated and the line was holding. Subsequently, YB-N fault was observed in 220kV Areakode Orkattery line and 220kV Areakode Kanhirode lines tripped. Tripping of both connected lines led to complete outage of radial connected stations. | 1.KSEBL to configure DR as per FOLD recommendations at Areacode and Khanirode SS. 2.KSEBL to ensure AR reclaim time of 25 Sec for all the lines in the network. | KSEBL | aeldkseb:KSEB: 07/01/2026 10:25:05: Sir, 1. The DR standardiation at Areacode and Kanhirode SS are done as per FOLD recommendations. 2. The AR reclim time is corrected to 25 seconds for all the lines. Requested to close this entry. | Complied | Complied
137/I/8 | Complete Outage of 220kV Kaniyampetta SS of KSEB | 19-10-2025 19:31 | During antecedent conditions, 220kV Kaniyampetta Kadakola was under outage. 220kV Kaniyampetta SS was being radially fed from 220kV Kunnamangalam Kaniyampetta line. As per the reports submitted, the triggering incident was YB-G fault in 220kV Kunnamangalam Kaniyampetta line and the line tripped. Tripping of the only connected line led to complete outage of 220kV Kaniyampetta SS | 1.KSEBL to update the Main-1 relay details in DMNS portal. 2.KSEBL to rectify the DR time sync issue at Kaniyampeta. 3.KSEBL to rectify SAS issues and enable Auto reclosure at Kunnamangalam end. | KSEBL | aeldkseb:KSEB: 07/01/2026 10:20:39: Sir, The item no 2 DR time sync issue rectified, item no 3 AR issues rectified. Only the item no 1 updation of relay settings in the DMNS portal is pending , directions are given to the field people . | Complied | Complied
138/I/5 | Complete Outage of 220kV Pallom, New Pallom, Punnapra, Kayamkulam, Edappon, Pathanamthitta and Kundara SS of KSEB | 17-12-2025 13:35 | During antecedent conditions, 220kV Edamon dappon and 220kV Edamon Kundara were under shutdown. 220kV Pallom, New Pallom, Punnapra, Kayamkulam, Edappon, Pathanamthitta and Kundara SS were being radially fed through 220kv Sabarigiri Pallom, 220kv Kottayam Pallom and 220kV Idukki New Pallom. At 13:35hrs, 220kV Sabarigiri Pallom tripped on B-G fault. Subsequently other two lines tripped on SLG faults within 7 minutes of first fault . Tripping of all source feeders led to complete outage of 220kV Pallom, New Pallom, Punnapra, Kayamkulam, Edappon, Pathanamthitta and Kundara SS | KSEBL to upload the relay settings in DMNS portal. KSEBL the configure the DR as per FOLD committee recommendations at Pallom end. KSEBL to transpaly the event and furnish the findings. KSEBL to refer the incident to SLDC for planning of any SPS | KSEBL | aeldkseb:KSEB: 03/02/2026 11:51:22: Sir, Directions have already been issued to the field officers for uploading the relay settings in the DMNS portal, configuring the DR at Pallom end as per FOLD Committee recommendations, and for downloading, analyzing, and furnishing the event data with findings. The incident has been examined, and it is observed that the tripping occurred due to four contingencies happening simultaneously. Hence, no requirement for planning or implementation of an SPS is envisaged in this case. | Complied | Complied
139/II/1 | Tripping of 220kV Bus-1 at Madakathara of KSEB | 07-01-2026 18:58 | In the antecedent condition 220KV-MADAKATHARA-CHALAKUDY-1 line and 220kV Bus Section 2A were under planned shutdown due to retrofitting works. As per the reports submitted, during the returning of the shutdown, 220 kV bus isolator (227) connected to 220KV-MADAKATHARA-CHALAKUDY-1 line to Bus Section 1A where in the bus dropper accidentally came into contact with an earth rod leading to B-G bus fault in the Bus Section 1A. BBP protection operated and tripped both the Bus Section 1A and Bus Section 1B. This led to the Tripping of 220kV Bus-1 at Madakathara of KSEB. | KSEBL to follow SOP during maintainance activities. | KSEBL | aeldkseb:KSEB: 06/03/2026 10:46:38: Sir, The maloperated GE Multilin B90 relay is disabled , th main 1 Busbar protection relay is healthy. Please remove this entry. | Complied | Complied
139/VI/14 | 220KV-KADAKOLA-KANIYAMPETTA | 18-01-2026 12:39 | 220KV-KADAKOLA-KANIYAMPETTA | KSEBL to rectify the DR time synchronization issue at KANIYAMPETTA - 220KV | KSEBL | aeldkseb:KSEB: 06/03/2026 10:43:16: Sir, The DR time synchronisation issue rectified, please remove the entry | Complied | Complied
140/III/4 | 220KV-THENI-SABARIGIRI-1 | 23-01-2026 13:40 | As per the reports submitted, the triggering incident was Y-G fault in the line. The Fault distance from Theni end was 26.9 kms and from Sabarigiri end was 86.1 kms. At Theni end, the fault was sensed in Z1, AR operated and tripped due to persistent fault. At Sabarigiri end, the fault was sensed in Z2, carrier aided trip and Y pole opened and AR operated after around 1.2 sec and tripped due to persistent fault (the issue is delayed fault clearance due to Z2 time trip instead of Z2 carrier aided trip), before which carrier was received for AR operation and Z1 sensing at remote ends. | 1. KSEBL to review the TOR operation at Sabarigiri end. 2. KSEBL to review the Dead time at Sabarigiri end. | KSEBL |  | Pending | Pending
140/VI/18 | 220KV-THENI-SABARIGIRI-1 | 15-02-2026 13:17 | 220KV-THENI-SABARIGIRI-1 | KSEBL to rectify the DR time synchronization issue at SABARIGIRI - 220KV | KSEBL |  | Pending | Pending
TAMIL NADU
109/I/1 | Complete Outage of 230kV/110kV/11kV Kadaperi SS of TANTRANSCO | 10-06-2023 17:22:00 | As per the reports submitted, the triggering incident was B-N fault in 230kV Kadaperi-Porur line feeder and the fault was not cleared at Kadaperi end (suspected high resistance fault). Subsequently, remote ends of all 230kV lines connected to 230kV/110kV/ | TANTRANSCO to check & correct the time sync issue at 110kV side & 230kV side. DEF settings coordination for the feeders connected to Kadaperi SS needs to be verified. Different make Main 1& Main 2 relays to be installed at Kadaperi end. | TANTRANSCO | cepc:TANTRANSCO: 05/10/2023 11:17:15: will be complied cepc:TANTRANSCO: 01/12/2023 16:26:57: 1.R&M proposal approved in PSDF & will be complied 2.Complied 3..R&M proposal approved in PSDF & will be complied cepc:TANTRANSCO: 02/01/2024 14:58:26: 1. will be complied 2.complied 3.will be complied cepc:TANTRANSCO: 01/02/2024 17:26:22: 1.will be complied 2.Complied 3.Will be complied cepc:TANTRANSCO: 04/03/2024 10:42:59: 1.WILL BE COMPLIED 2.COMPLIED 3.WILL BE COMPLIED cepc:TANTRANSCO: 30/03/2024 13:49:07: 1.WILL BE COMPLIED 2.COMPLIED 3.WILL BE COMPLIED cepc:TANTRANSCO: 03/05/2024 16:56:36: 1.WILL BE COMPLIED 2.COMPLIED 3.WILL BE COMPLIED cepc:TANTRANSCO: 02/07/2024 13:11:38: 1. will be complied 2.complied 3.will be complied cepc:TANTRANSCO: 06/01/2025 16:17:12: 1.will be complied 2.complied 3.will be complied cepc:TANTRANSCO: 03/02/2025 16:40:08: 1.Time Sync ensured at 230kV side At 110kV side _Relay has to be replaced 2.complied 3.Distance relay has to be procured cepc:TANTRANSCO: 04/03/2025 12:12:05: 1.Time sync ensured at 230kV side 2.Complied 3. Relay has to be procured cepc:TANTRANSCO: 05/04/2025 15:15:10: 1. Time Sync ensured at 230kV side 2. complied 3. Numerical relay has to be procured cepc:TANTRANSCO: 04/06/2025 13:41:56: 1. Time Sync ensured at 230kV side 2. Complied 3.Distance relay has to be procured cepc:TANTRANSCO: 03/07/2025 14:42:44: 1. complied 2.complied 3. Distance relay has to be procured cepc:TANTRANSCO: 06/08/2025 16:21:19: Distance relay has to be procured cepc:TANTRANSCO: 02/09/2025 13:40:46: Distance relay has to be procured cepc:TANTRANSCO: 03/10/2025 17:02:45: Distance relay has to be procured cepc:TANTRANSCO: 06/11/2025 10:42:00: Distance relay has to be procured cepc:TANTRANSCO: 04/12/2025 13:14:47: Distance relay has to be procured cepc:TANTRANSCO: 29/12/2025 10:52:09: Distance relay has to be procured cepc:TANTRANSCO: 02/02/2026 14:40:41: distance relay has to be procured cepc:TANTRANSCO: 04/03/2026 16:03:55: Distance relay has to be procured cepc:TANTRANSCO: 30/03/2026 16:34:30: Distance relay has to be procured | Pending | Pending
50/I/3 | . | 21-12-2015 at 6:28 hrs | Busbar protection got operated for a fault in 230kV Mywadi-Anaikadavu line | TANTRANSCO to examine the feasibility of providing two main-zone operation for bus bar protection by exploring various alternatives like replacing existing bus-coupler CB with a hybrid bus-coupler CB that comes with inbuilt CT, replacing existing BBP relay with another suitable relay that supports two main-zone operation, and implement the same. | TANTRANSCO | cepc:TANTRANSCO: 01/12/2023 16:26:57: Bus coupler Breaker & CT commissioned. In Relay two zone feature enabled. Bus Strengthening & Bus Isolator replacement to be completed. Replacement of Isolator work under progress cepc:TANTRANSCO: 02/01/2024 14:58:26: Time line requested upto 30.06.2024 cepc:TANTRANSCO: 01/02/2024 17:26:22: Time Line requested upto 30.06.2024 cepc:TANTRANSCO: 04/03/2024 10:42:59: TIME LINE REQUESTED UPTO 30.06.2024 cepc:TANTRANSCO: 30/03/2024 13:49:07: TIME LINE REQUESTED UPTO 30.06.2024 cepc:TANTRANSCO: 03/05/2024 16:56:36: TIME LINE REQUESTED UPTO 30.06.2024 cepc:TANTRANSCO: 02/07/2024 13:11:38: will be complied cepc:TANTRANSCO: 06/01/2025 16:17:12: pending for want replacemet of bus isolator cepc:TANTRANSCO: 03/02/2025 16:41:01: Replacement of Isolator work under progress.LV-I Bus-I and BUS-II Isolator Replaced on 11.01.2025,LV-II Bus-I Isolator Replaced On 24.1.2023 cepc:TANTRANSCO: 04/03/2025 12:11:00: Pending for want of Disconnector & bus strengthening work cepc:TANTRANSCO: 05/04/2025 15:15:10: Pending for want of replacement of disconnector and bus strengthening cepc:TANTRANSCO: 04/06/2025 13:43:02: Pending for want of replacement of disconnector & bus strengthening cepc:TANTRANSCO: 03/07/2025 14:41:45: Pending for want of replacement of disconnector & bus strengthening cepc:TANTRANSCO: 06/08/2025 16:21:19: Pending for want of replacement of disconnector & bus strengthening cepc:TANTRANSCO: 02/09/2025 13:40:46: Pending for want of replacement of disconnector & bus strengthening cepc:TANTRANSCO: 04/10/2025 12:34:02: Bus strengthening & replacement of disconnectors works are to be taken up by System operation wing cepc:TANTRANSCO: 06/11/2025 10:42:00: Bus strengthening & replacement of disconnectors works to be taken up by System Operation wing cepc:TANTRANSCO: 04/12/2025 13:14:47: Strengthening & Replacement of disconnectors work to be taken up by System operation wing cepc:TANTRANSCO: 29/12/2025 10:52:09: 14 Nos of 1250 A Disconnector replaced with 2000A in Bus.1 & 2 Another 14 disconnector has to be replaced after that Bus strengthening work will be taken up cepc:TANTRANSCO: 02/02/2026 14:40:41: pending 1250A Disconnector has to be replaced & Strengthening of Bus cepc:TANTRANSCO: 04/03/2026 16:03:55: Disconnector replacement work under progress cepc:TANTRANSCO: 30/03/2026 16:34:30: Disconnector replacement work under progress | Pending | Pending
58/II/17 | . | 14-09-16 11:13 15-09-16 22:14 | Bus Bar Protection (Zone-2) of 230 kV Bus-B got operated at Alamathy Station during fault in 230 kV Alamathy-Korattur feeder. | 1. TANTRANSCO to check the healthiness of BBP relay by conducting stability test, and take appropriate remedial action like increasing voltage settings, ensuring the healthiness of CTwith similar characteristics (equal saturation effects & equal winding resistances) etc. at their 230 kV Alamathy SS. 2. TANTRANSCO to replace the existing high-impedance BBP relay with its low-impedance/ numerical variant so as to accommodate variation in CT characteristics at their 230 kV Alamathy SS. | TANTRANSCO | srpcadmin:SRPC: 08/11/2023 13:02:27: TANTRANSCO Mail dated 03-08-2022/ 06-10-2022_&_06-12-2022_and _01-02-2023_and_13-04-2023 Purchase order placed vide PO.No. 1028 Dated 21.06.2022 for procurement of Numerical BBP. Discussed in Bilateral meeting held on 29.05.2023: TANTRANSCO Mail dated 19-06-2023 informed that BBP relay allotted & Time lIne requested upto 31.12.2023 for commissioning. TANTRANSCO Mail dated 01-08-2023_and_24-08-2023_AND_03-10-2023 BBP relay allotted & Time lIne requested upto 31.12.2023 for commissioning. cepc:TANTRANSCO: 01/12/2023 16:26:57: Low Impedence BBP relay configuration completed & will be commissioned based on availability of Line Clear cepc:TANTRANSCO: 02/01/2024 14:58:26: BBP allotted & will be complied cepc:TANTRANSCO: 01/02/2024 17:26:22: will be complied cepc:TANTRANSCO: 04/03/2024 10:42:59: BBP RELAY ALLOTTED & WILL BE COMPILED cepc:TANTRANSCO: 30/03/2024 13:49:07: BBP RELAY ALLOTTED & WILL BE COMPLIED cepc:TANTRANSCO: 03/05/2024 16:56:36: NUMERICAL BBP RELAY ALLOTED & WILL BE COMPLIED cepc:TANTRANSCO: 02/07/2024 13:11:38: will be complied cepc:TANTRANSCO: 06/01/2025 16:17:12: BBP relay allotted & will be complied cepc:TANTRANSCO: 03/02/2025 16:41:41: BBP relay configuration testing done Cable has to be laid cepc:TANTRANSCO: 04/03/2025 12:11:00: Line clear awaited cepc:TANTRANSCO: 05/04/2025 15:19:23: Numerical Low Imp BBP relay configuration done and awaited line clear . Time line requested upto 30.06.2025 cepc:TANTRANSCO: 04/06/2025 13:30:57: Complied. NUmerical BBP relay commisioned on 09.05.2025 cepc:TANTRANSCO: 03/07/2025 14:55:34: Complied. Numerical BBP relay commissioned on 09.05.2025 | Complied | Complied
64/1/4 | . | 26-03-2017 at 23:14hrs | Tripping of evacuating lines due to fault led to tripping of running Unit at NCTPS Stg-1 | 1. TANTRANSCO to take steps to complete insulator replacement works on the 230 kV lines owned by them in NCTPS area within 6 months. 2. TANTRANSCO to take steps to implement A/R on all 230 kV lines emanating from NCTPS-I at the earliest. | TNPGCL | srpcadmin:SRPC: 08/11/2023 13:04:09: TANTRANSCO Mail dated 11.04.2022; and 23-05-2022. 1. Completed 2.TANGEDCO has to procure the C & R panels Discussed in Bilateral meeting held on 29.05.2023: TANTRANSCO Mail dated 19-06-2023 2.TANGEDCO has to procure the C & R panels TANTRANSCO Mail dated 01-08-2023_and_24-08-2023_AND_03-10-2023 TANGEDCO has to procure the C&R panels. cepc:TANTRANSCO: 01/12/2023 16:26:57: pending with TANGEDCO cepc:TANTRANSCO: 02/01/2024 14:58:26: C&R panels has to be procured by TANGEDCO. . cepc:TANTRANSCO: 01/02/2024 17:26:22: pending with TANGEDCO cepc:TANTRANSCO: 04/03/2024 10:42:59: TANGEDCO HAS TO PROCURE THE C&R PANEL,PENDING WITH TANGEDCO cepc:TANTRANSCO: 30/03/2024 13:49:07: PENDING WITH TANGEDCO cepc:TANTRANSCO: 03/05/2024 16:56:36: PENDING WITH TANGEDCO cepc:TANTRANSCO: 02/07/2024 13:11:38: pending with TANGEDCO cepc:TANTRANSCO: 06/01/2025 16:17:12: pending with TANGEDCO cepc:TANTRANSCO: 03/02/2025 16:42:05: pending with TNPGCL | Pending | Pending
91/I/5 | . | 19-04-2020 at 04:14Hrs | Triggering incident was YN fault in 230kV Karaikudi-Karambyam line. the same time, bus fault occurred at 230kV Thiruvarur SS due to snapping of B phase dropper conductor of 230 kV Thanjavur-Thiruvarur line near Bus-1 side isolator and Bus-1 BBP operated resulting in the tripping of all the elements connected to 230kV Thiruvarur SS. Since 230kV Thiruvarur SS was under single bus operation, this resulted in de-energization of 230kV bus at Thiruvarur SS. Tripping of 230kV Karaikudi-Karambyam line and 230kV Thiruvarur-Karambyam line resulted in complete loss of supply at 230kV Karambyam SS. | i. TANTRANSCO to avoid single bus operation at their Substations where atleast 2 buses are available. ii. To share the reasons for SLDC instruction for single bus operation at Tiruvarur. | TANTRANSCO | srpcadmin:SRPC: 08/11/2023 13:05:38: TANTRANSCO Mail dated 13-04-2023 In Karambayam & Thiruvarur 230kVSS is having double bus configuration with 3 Nos of 230/110kV 100MVA Auto Tr. While implementing the zone segregation, out of 3 Auto Tr, 2 Tr comes in one bus & remaining 1 no Transformer comes in another bus. Due to that the over loding was observed. The same was addressed to System studies wing for further study & Time line requested upto 30.06.2023 Discussed in Bilateral meeting held on 29.05.2023: TANTRANSCO Mail dated 19-06-2023: Time Line requested upto 31.07.2023 TANTRANSCO Mail dated 01-08-2023 Time Line requested upto 31.08.2023 TANTRANSCO Mail dated 24-08-2023 Time Line requested upto 31.09.2023 TANTRANSCO Mail dated 03-10-2023 400 kV Vellalalviduthi SS - Pre commissioning works under progress, hencce could not be implemented. Proposed commissioning in first week October 23. Will be implemented in this month. cepc:TANTRANSCO: 01/12/2023 16:26:57: will be complied. Time Line requested upto 31.12.2023 cepc:TANTRANSCO: 02/01/2024 14:58:26: will be complied time line requested upto 31.03.2024 cepc:TANTRANSCO: 01/02/2024 17:26:22: will be complied time line requested upto 31.03.2024 cepc:TANTRANSCO: 04/03/2024 10:42:59: NEW BBP PANELS ALLOTED & TIME LINE REQUESTED TO UPTO 30.06.2024 cepc:TANTRANSCO: 30/03/2024 13:49:07: NUMERICAL BBP RELAY ALLOTTED & TIME LINE REQUESTED UPTO 30.06.2024 cepc:TANTRANSCO: 03/05/2024 16:56:36: NUMERICAL BBP RELAY ALLOTED & TIME LINE REQUESTED UPTO 30.06.2024 cepc:TANTRANSCO: 02/07/2024 13:11:38: will be complied cepc:TANTRANSCO: 06/01/2025 16:17:12: will be complied cepc:TANTRANSCO: 03/02/2025 16:42:50: Addressed to System Operation wing for ensuring two zone operation cepc:TANTRANSCO: 04/03/2025 12:11:00: Addressed to System operation wing for implementing double bus operation cepc:TANTRANSCO: 05/04/2025 15:19:23: Addressed to System operation wing to implement the double bus operation cepc:TANTRANSCO: 04/06/2025 13:36:19: Addressed to System operation wing for implementing double bus operation cepc:TANTRANSCO: 03/07/2025 14:50:48: Addressed to system operation wing for implementing double bus operation. cepc:TANTRANSCO: 06/08/2025 16:22:25: Addressed to System operation wing for implementing double bus operation | Complied | Complied
92/1/I | . | 22-06-2020 at 23:47 Hr. | 1.During antecedent conditions, 230kV Mwyadi SS was under single bus operation.2.Triggering incident was failure of B phase CT of 230kV Mywadi-Ponnapuram line-2 at 230kV Mywadi end. 3.230 kV Bus-1 bus bar protection operated resulting in the tripping of all the connected elements at 230kV Mywadi. 4.400kV/230kV Udumalpet ICT-1, 2 and 3 also tripped during the event. | i. TANTRANSCO to expedite the process of Bus strengthening at 230kV Mywadi SS, on priority , in order to restore double bus operation. Healthiness of other CTs in the SS shall also be ensured. ii. TANTRANSCO requested to submit equipment failure report to CEA with a copy to SRPC. | TANTRANSCO | srpcadmin:SRPC: 08/11/2023 13:07:26: TANTRANSCO Mail dated 01-02-2023_and 13-04-2023 Bus coupler Breaker & CT commissioned. In Relay two zone feature enabled. Bus Strengthening & Bus Isolator replacement to be completed in ICT.1 ( bus isolator) The Procurement of 230KV Isolators are now under progress After completion of Isolator replacement works and Bus II strengthening works , the Bus segregation works will be carry out at 230KV Myvadi Switching Station.Time Line requested upto 30.06.2023 Discussed in Bilateral meeting held on 29.05.2023: TANTRANSCO Mail dated 19-06-2023_and 01-08-2023_&_24-08-2023_and_03-10-2023 Time Line requested upto 31.12.2023 cepc:TANTRANSCO: 01/12/2023 16:26:57: Bus coupler Breaker & CT commissioned. In Relay two zone feature enabled. Bus Strengthening & Bus Isolator replacement to be completed. Replacement of Isolator work under progress cepc:TANTRANSCO: 02/01/2024 14:58:26: Time line requested upto 30.06.2024 cepc:TANTRANSCO: 01/02/2024 17:26:22: Time line requested upto 30.06.2024 cepc:TANTRANSCO: 04/03/2024 10:42:59: TIME LINE REQUESTED UPTO 30.06.2024 cepc:TANTRANSCO: 30/03/2024 13:49:07: TIME LINE REQUESTED UPTO 30.06.2024 cepc:TANTRANSCO: 03/05/2024 16:56:36: TIME LINE REQUESTED UPTO 30.06.2024 cepc:TANTRANSCO: 02/07/2024 13:11:38: will be complied cepc:TANTRANSCO: 06/01/2025 16:17:12: pending for want of replacement of bus isolator cepc:TANTRANSCO: 03/02/2025 16:43:12: Replacement of Isolator work under progress.LV-I Bus-I and BUS-II Isolator Replaced on 11.01.2025,LV-II Bus-I Isolator Replaced On 24.1.2023 cepc:TANTRANSCO: 04/03/2025 12:08:18: pending for want of replacement of disconnector & bus strengthening work cepc:TANTRANSCO: 05/04/2025 15:15:10: Pending for want of replacement of disconnector and bus strengthening cepc:TANTRANSCO: 04/06/2025 13:43:02: Pending for want of replacement of disconnector & bus strengthening cepc:TANTRANSCO: 03/07/2025 14:41:45: Pending for want of replacement of disconnector & bus strengthening cepc:TANTRANSCO: 06/08/2025 16:23:39: Pending for want of replacement of disconnector & bus strengthening cepc:TANTRANSCO: 02/09/2025 13:40:46: Pending for want of replacement of disconnector & bus strengthening cepc:TANTRANSCO: 04/10/2025 12:34:02: Bus strengthening & replacement of disconnectors works are to be taken up by System operation wing cepc:TANTRANSCO: 06/11/2025 10:42:00: Bus strengthening & replacement of disconnectors works to be taken up by System Operation wing cepc:TANTRANSCO: 04/12/2025 13:14:47: Strengthening & Replacement of disconnectors work to be taken up by System operation wing cepc:TANTRANSCO: 29/12/2025 10:52:09: 14 Nos of 1250 A Disconnector were replaced with 2000A in Bus.1 & 2 Another 14 disconnector has to be replaced after that Bus strengthening work will be taken up cepc:TANTRANSCO: 02/02/2026 14:40:41: pending 1250A Disconnector has to be replaced & Strengthening of Bus cepc:TANTRANSCO: 04/03/2026 16:03:55: Disconnector replacement work under progress cepc:TANTRANSCO: 30/03/2026 16:34:30: Disconnector replacement work under progress | Pending | Pending
95/II/20 | . | 19-02-21 23:49 hrs. | Triggering incident was Y-E fault in the 400kV Alamathy - NCTPS ST2 line-1. At Alamathy end, fault was sensed in Zone-1. At NCTPS ST2 end, carrier aided Zone-2 protection operated. A/R operated and line tripped on persistent fault at both the ends. At the same time, at Alamathy end, BBP Zone-1 protection operated at 400 kV Bus-1 and all the elements connected to 400 kV Bus-1 got tripped. 400/230 kV ICT 3 at Alamathy also got tripped during this event since Tie C.B was under LC for new reactor commissioning work during antecedent. | TANTRANSCO to expedite the process of providing numerical BBP at their 400/ 230kV Alamathy SS. | TANTRANSCO | srpcadmin:SRPC: 08/11/2023 13:09:08: TANTRANSCO Mail dated 03-08-2022_and_06-10-2022_&_06-12-2022_and_01-02-2023_and_13-04-2023 Purchase order placed vide PO.No. 1028 Dated 21.06.2022 for procurement of Numerical BBP. Discussed in Bilateral meeting held on 29.05.2023: TANTRANSCO Mail dated 19-06-2023 Purchase order placed vide PO.No. 1028 Dated 21.06.2022 TANTRANSCO Mail dated 01-08-2023 Purchase order placed vide PO.No. 1028 Dated 21.06.2022 for procurement of Numerical BBP. TANTRANSCO Mail dated 24-08-2023_and_03-10-2023 BBP panels allotted & Time Line requested cepc:TANTRANSCO: 01/12/2023 16:26:57: Low impedence BBP relay allotted & will be commissioned based on Line clear cepc:TANTRANSCO: 02/01/2024 14:58:26: BBP allotted & will be complied cepc:TANTRANSCO: 01/02/2024 17:26:22: will be complied cepc:TANTRANSCO: 04/03/2024 10:42:59: NUMERICLA BBP RELAY ALLOTTED & WILL BE COMPLIED cepc:TANTRANSCO: 30/03/2024 13:49:07: NUMERICAL BBP RELAY ALLOTTED & WILL BE COMPLIED cepc:TANTRANSCO: 03/05/2024 16:56:36: NUMERICAL BBP RELAY ALLOTED & WILL BE COMPLIED cepc:TANTRANSCO: 02/07/2024 13:11:38: will be complied cepc:TANTRANSCO: 06/01/2025 16:17:12: BBP panels allotted & will be complied cepc:TANTRANSCO: 03/02/2025 16:44:10: Numerical BBP procured vide .Purchase order .No. 1028 Dated 21.06.2022 BBP relay configuration testing done Cable has to be laid cepc:TANTRANSCO: 04/03/2025 12:08:18: Line clear awaited cepc:TANTRANSCO: 05/04/2025 15:19:23: Numerical Low Imp BBP relay configuration done and awaited line clear . Time line requested upto 30.06.2025 cepc:TANTRANSCO: 04/06/2025 13:38:14: Numerical BBP panel alloted . Now 110kV BBP & 230kV BBP commissioned 400kV BBP revamping work will be taken up cepc:TANTRANSCO: 03/07/2025 14:50:48: Numerical BBP Commissioned in 110kV & 230kV voltage level. 400kV side is pending for want of laying cable. Cable received. Laying of cable has to be taken up. Time line requested upto 31.12.2025 | Complied | Complied
107/II/1 | . | 01-02-2023 4.23.00 PM | . | TANTRANSCO to provide Line differential protection for these short lines (for line length <10kM) | TANTRANSCO | srpcadmin:SRPC: 08/11/2023 13:11:28: TANTRANSCO Mail dated 19-06-2023:_AND_01-08-2023_and_24-08-2023_and_03-10-2023 Line differential protection relay procurement under process. Time Line requested upto 31.12.2023 cepc:TANTRANSCO: 01/12/2023 16:26:57: LDP procurement under Progress. Time line requested upto 31.03.2024 cepc:TANTRANSCO: 02/01/2024 14:58:26: LDP procurement under progress. Time line requested upto 31.03.2024 cepc:TANTRANSCO: 01/02/2024 17:26:22: Time line requested upto 31.03.2024 cepc:TANTRANSCO: 04/03/2024 10:42:59: LDP PROCUREMENT UNDER PROGRESS. TIME LINE REQUESTED UPTO 31.12.2024 cepc:TANTRANSCO: 30/03/2024 13:49:07: LDP PROCUREMENT UNDER PROGRESS. TIME LINE REQUESTED UPTO 30.06.2024 cepc:TANTRANSCO: 03/05/2024 16:56:36: LDP PROCUREMENT UNDER PROGRESS cepc:TANTRANSCO: 02/07/2024 13:11:38: will be complied cepc:TANTRANSCO: 06/01/2025 16:17:12: will be complied cepc:TANTRANSCO: 03/02/2025 16:44:34: LDP has to be procured cepc:TANTRANSCO: 04/03/2025 12:08:18: LDP has to be procured cepc:TANTRANSCO: 05/04/2025 15:19:23: LDP has to be procured cepc:TANTRANSCO: 04/06/2025 13:38:44: LDP has to be procured cepc:TANTRANSCO: 03/07/2025 14:50:48: LDP has to be procured cepc:TANTRANSCO: 06/08/2025 16:21:19: LDP has to be procured cepc:TANTRANSCO: 02/09/2025 13:40:46: LDP has to be procured proposed under PSDF cepc:TANTRANSCO: 03/10/2025 17:02:45: LDP has to be procured cepc:TANTRANSCO: 06/11/2025 10:42:00: LDP has to be procured cepc:TANTRANSCO: 04/12/2025 13:14:47: LDP has to be procured cepc:TANTRANSCO: 05/01/2026 12:57:59: LDP has to be procured cepc:TANTRANSCO: 02/02/2026 14:26:41: LDP procured & will be commissioned cepc:TANTRANSCO: 04/03/2026 16:03:55: LDP procured. will be commissioned before 15.04.2026 cepc:TANTRANSCO: 30/03/2026 16:34:30: LDP procured. Will be commissioned before 15.04.2026 | Pending | Pending
107/II/8 | . | 13-02-2023 17:55 | . | TANTRANSCO to review the distance zone setting of both Main.1 & Main 2 relay at Gurubarapally. | TANTRANSCO | cepc:TANTRANSCO: 01/12/2023 16:26:57: Complied | Complied | Complied
108/I/5 | . | 22-04-2023 14:27 | . | TANTRANSCO: i. to replace the 230 kV Static BBP relay with a numerical BBP relay at Alamathy end ii. to rectify the Carrier failure at both ends for the line 230 kV Alamathy-Koyambedu feeder iii. to enable A/R at OPG end of 230 kV Alamathy-OPG feeders. | TANTRANSCO | srpcadmin:SRPC: 08/11/2023 13:13:16: TANTRANSCO Mail dated 01-08-2023_&_24-08-2023_and_03-10-2023 1. 230kv BBP panel allotted & time line requested upto 31.12.2023 2. Action is being taken to implement the CAT 3.Addressed to OPG for implementation of delayed AR Time Line requested upto 31.12.2023 cepc:TANTRANSCO: 01/12/2023 16:26:57: 1.Low Impedence BBP relay configuration completed & will be commissioned based on availability of Line Clear 2. will be complied 3.Addressed to OPG for implementation of delayed AR cepc:TANTRANSCO: 02/01/2024 14:58:26: 1.230kV BBP allotted & will be complied 2.Action is being taken to implement the CAT 3.Addressed to OPG for implementing delayed AR will be complied cepc:TANTRANSCO: 01/02/2024 17:26:22: 1.will be complied 2.will be complied 3.will be complied cepc:TANTRANSCO: 04/03/2024 10:42:59: 1.WILL BE COMPLIED 2.WILL BE COMPLIED 3.WILL BE COMPLIED cepc:TANTRANSCO: 30/03/2024 13:49:07: 1.WILL BE COMPLIED 2.WILL BE COMPLIED 3.WILL BE COMPLIED cepc:TANTRANSCO: 03/05/2024 16:56:36: 1.WILL BE COMPLIED 2.WILL BE COMPLIED 3.WILL BE COMPLIED cepc:TANTRANSCO: 02/07/2024 13:11:38: 1. will be complied 2.will be complied 3.will be complied cepc:TANTRANSCO: 06/01/2025 16:17:12: will be complied cepc:TANTRANSCO: 03/02/2025 16:45:09: 1.Numerical BBP procured vide .Purchase order .No. 1028 Dated 21.06.2022 Low Impedence BBP relay configuration completed & Cable has to be laid 2. awaiting Line cleafor testingr. 3.Delayed AR implemented at OPG end . Due to PD relay constriants, AR not successful. M/s. OPG has to procure the PD relay cepc:TANTRANSCO: 04/03/2025 12:05:47: 1 &2 Line clear awaited . OPG has to procure the PD relay cepc:TANTRANSCO: 05/04/2025 15:19:23: 1. Numerical BBP relay setting & configuration done. 2.Carrier fail attended 3.M/s. OPG has to procure PD relay cepc:TANTRANSCO: 04/06/2025 13:40:25: 1. Complied . 230kV BBP numerical relay has been commissioned on 13.05.2025 2.Carrier fail attended 3.M/s. OPG has to procure the PD relay cepc:TANTRANSCO: 03/07/2025 14:50:48: 1. complied 2.complied 3.OPG end has to be attended. | Complied | Complied
112/I/3 | Complete Outage of 230kV/110kV Taramani SS of TANTRANSCO | 05-10-2023 15:12 | At 14:13 hrs the triggering incident is the B-N fault in 230kV Tharamani-Kaluvinthapattu. This led to 230kV Tharamani-Sriperumpudur being the only feeder connected to 230kV Tharamani SS. At 14:50, 230kV Tharamani-Sriperumpudur also tripped due to Y-N fault and the tripping led in resulting complete outage at Tharamani 230KV SS. | 1.Dead time of Kalvinthapattu end and Tharamani end needs to be set at same. 2.TANTRANSCO to expedite the completion of new SS at Tharamani. | TANTRANSCO | cepc:TANTRANSCO: 01/12/2023 16:26:57: will be complied. Time Line requested upto 31.03.2024 cepc:TANTRANSCO: 02/01/2024 14:58:26: will be complied & time line requested upto 31.03.2024 cepc:TANTRANSCO: 01/02/2024 17:26:22: Time line requested upto 31.03.2024 cepc:TANTRANSCO: 04/03/2024 10:42:59: TIME LINE REQUESTED UPTO 30.06.2024 cepc:TANTRANSCO: 30/03/2024 13:49:07: TIME LINE REQUESTED UPTO 30.06.2024 cepc:TANTRANSCO: 03/05/2024 16:56:36: TIME LINE REQUESTED UPTO 30.06.2024 cepc:TANTRANSCO: 02/07/2024 13:11:38: will be complied cepc:TANTRANSCO: 06/01/2025 16:17:12: Complied Now Kalivanthupattu line shifted to Tharamani 400kVSS & dead time is revised cepc:TANTRANSCO: 25/01/2025 13:32:22: Complied | Complied | Complied
114/I/1 | Compete outage of 230kV Koyambedu, 230kV Mambalam and 230kV RA Puram | 03-11-2023 03:19 | As per the reports submitted the triggering incident was B-N fault in 230kV Koyambedu Guindy line. At Guindy end, the fault was sensed in zone-1 protection as fault current flowed through neutral in all 3 phases. At Koyambedu end, distance protection failed to clear the fault and DEF operated and the line tirpped after 767ms. By the time DEF operated at Koyambedu end, remote ends of other lines tripped on operation of zone-3 protection.. This resulted in a complete outage of 230kV/110kV Koyambedu SS, 230kV Guindy SS, 230kV/33kV Mambalam SS and 230kV/33kV RA Puram SS | 1. TANTRANSCO to implement both Main 1 Main 2 Relays as LDP with Backup inbuilt distance for 230kV Koyembedu Guidy Line and alternate fiber path for Main 2 LDP (Different from Main 1 LDP path) to be ensured 2. Earth mat Audit to be carried out by Third party agency at 230kV Koyembedu Substation | TANTRANSCO | cepc:TANTRANSCO: 01/02/2024 17:26:22: 1. will be complied 2.Will be complied cepc:TANTRANSCO: 04/03/2024 10:42:59: LDP PROCUREMENT UNDER PROGRESS TIME LINE REQUESTED UPTO 30.06.2024 2.WILL BE COMPLIED cepc:TANTRANSCO: 30/03/2024 13:49:07: 1.LDP PROCUREMENT UNDER PROGRESS 2.WILL BE COMPLIED cepc:TANTRANSCO: 03/05/2024 16:56:36: LDP PROCUREMENT UNDER PROGRESS cepc:TANTRANSCO: 02/07/2024 13:11:38: will be complied cepc:TANTRANSCO: 06/01/2025 16:20:59: will be complied cepc:TANTRANSCO: 03/02/2025 16:28:19: LDP has to be procured. Eartmat audit is to be carriedout cepc:TANTRANSCO: 04/03/2025 12:12:54: 1. LDP has to be procured 2. Addressed to system operation wing for earthmat audit cepc:TANTRANSCO: 05/04/2025 15:12:49: LDP relay has to be procured Addressed to System operation wing to conduct earthmat audit cepc:TANTRANSCO: 04/06/2025 13:44:34: LDP relay has to be procured Addressed to System Operation wing to conduct earthmat audit cepc:TANTRANSCO: 03/07/2025 14:40:21: LDP relay has to be procured. Addressed to System operation wing to carryout earthmat audit. cepc:TANTRANSCO: 06/08/2025 16:24:26: LDP relay has to be procured Addressed to system operation wing to carryout earthmat audit | Complied | Complied
115/II/4 | Tripping of 230kV Bus at 230kV/110kV Sembatty SS of TANTRANSCO | 10-01-2024 15:24 | 230kV/110kV Sembatty SS is operating with single bus configuration at 230kV level. As per the reports submitted, the triggering incident was a Y Phase jumper failure between the Breaker and 230 KV Bus isolator in the 230kV Checkanurani- Sembatty line causing a bus fault at 230kV Sembatty. Immediately, BBP operated and all the elements connected to the bus tripped. 110kV was intact during this event. | TANTRANSCO to check the healthiness of all Jumpers of feeders at Sembatty SS. | TANTRANSCO | cepc:TANTRANSCO: 04/03/2024 10:42:59: CHECKED | Complied | Complied
116/I/5 | Complete outage of 230kV Tondiarpet and Tripping of Bus-1 at Basin Bridge | 18-01-2024 18:08 | As per the reports submitted the triggering incident is the failure of R-phase CT of 230kV Basinbridge- Tondiarpet feeder at Basinbridge end which created a R-N fault and later developed to R-Y-B fault and at 230kV Basin Bridge end busbar protection operated in Bus- 1 and cleared the fault. However, at Tondiarpet end the fault was sensed in Z2 but the breaker did not open due to mechanical issue resulting in LBB initiation. It was observed that Z2 was not continuous and intermittent Z2 was observed from the DR (the same is transplayed in PSCT and is available in RLDC Analysis/Observations). It was informed that the LBB trip was not extended to all connected bays which resulted in tripping of all feeders connected to Tondiarpet at remote ends (230kV Tondiarpet-NCTPS-1 at NCTPS end on Z2 however only two poles opened after around 520ms and later 450ms B-pole opened, 230kV Tondiarpet-NCTPS-2 at NCTPS end tripped on Z3 protection and 230kV Tondiarpet-Pulianthope at Pulianthope end on Z3 operation). Due to tripping of all the feeders at remote end led to the Complete outage of 230kV Tondiarpet and the tripping of Bus-1 at Basin Bridge. | TANTRANSCO to check the LBB trip scheme. | TANTRANSCO | cepc:TANTRANSCO: 30/03/2024 13:49:07: WILL BE COMPLIED cepc:TANTRANSCO: 03/05/2024 16:56:36: WILL BE COMPLIED cepc:TANTRANSCO: 02/07/2024 13:11:38: will be complied cepc:TANTRANSCO: 06/01/2025 16:20:59: will be complied cepc:TANTRANSCO: 03/02/2025 15:59:05: Awaiting Line clear & Scheme will be checked cepc:TANTRANSCO: 04/03/2025 12:16:56: Awaiting Line clear cepc:TANTRANSCO: 05/04/2025 15:10:19: Line clear awaited. Time line requested upto 30.04.2025 cepc:TANTRANSCO: 04/06/2025 13:46:23: Line clear awaited cepc:TANTRANSCO: 01/07/2025 16:10:13: Line clear awaited cepc:TANTRANSCO: 01/07/2025 16:10:54: Line clear awaited cepc:TANTRANSCO: 06/08/2025 10:47:42: Since obsolete LBB scheme, New Numerical BBP has been allotted. Commissioning activities under progress cepc:TANTRANSCO: 02/09/2025 13:45:54: cable laying under progress cepc:TANTRANSCO: 03/10/2025 17:02:45: cable laying under progress cepc:TANTRANSCO: 06/11/2025 10:42:00: LBB tripping operated on 06-10-2025 11:02 during the event line fault in 230kV Tondiarpet_NCTPS line.2. Complied | Complied | Pending
116/I/5 | Complete outage of 230kV Tondiarpet and Tripping of Bus-1 at Basin Bridge | 18-01-2024 18:08 | As per the reports submitted the triggering incident is the failure of R-phase CT of 230kV Basinbridge- Tondiarpet feeder at Basinbridge end which created a R-N fault and later developed to R-Y-B fault and at 230kV Basin Bridge end busbar protection operated in Bus- 1 and cleared the fault. However, at Tondiarpet end the fault was sensed in Z2 but the breaker did not open due to mechanical issue resulting in LBB initiation. It was observed that Z2 was not continuous and intermittent Z2 was observed from the DR (the same is transplayed in PSCT and is available in RLDC Analysis/Observations). It was informed that the LBB trip was not extended to all connected bays which resulted in tripping of all feeders connected to Tondiarpet at remote ends (230kV Tondiarpet-NCTPS-1 at NCTPS end on Z2 however only two poles opened after around 520ms and later 450ms B-pole opened, 230kV Tondiarpet-NCTPS-2 at NCTPS end tripped on Z3 protection and 230kV Tondiarpet-Pulianthope at Pulianthope end on Z3 operation). Due to tripping of all the feeders at remote end led to the Complete outage of 230kV Tondiarpet and the tripping of Bus-1 at Basin Bridge. | TANTRANSCO to do the SF6 gas, dew point measurements testing of all breakers at Tondiarpet end. | TANTRANSCO | cepc:TANTRANSCO: 30/03/2024 13:49:07: WILL BE COMPLIED cepc:TANTRANSCO: 03/05/2024 16:56:36: WILL BE COMPLIED cepc:TANTRANSCO: 02/07/2024 13:11:38: will be complied cepc:TANTRANSCO: 06/01/2025 16:20:59: will be complied cepc:TANTRANSCO: 25/01/2025 13:31:07: Complied Dew point measurements testing of all breakers carried out by Sf6 wing during the month of September/2024. All the value are within limit | Complied | Pending
116/I/5 | Complete outage of 230kV Tondiarpet and Tripping of Bus-1 at Basin Bridge | 18-01-2024 18:08 | As per the reports submitted the triggering incident is the failure of R-phase CT of 230kV Basinbridge- Tondiarpet feeder at Basinbridge end which created a R-N fault and later developed to R-Y-B fault and at 230kV Basin Bridge end busbar protection operated in Bus- 1 and cleared the fault. However, at Tondiarpet end the fault was sensed in Z2 but the breaker did not open due to mechanical issue resulting in LBB initiation. It was observed that Z2 was not continuous and intermittent Z2 was observed from the DR (the same is transplayed in PSCT and is available in RLDC Analysis/Observations). It was informed that the LBB trip was not extended to all connected bays which resulted in tripping of all feeders connected to Tondiarpet at remote ends (230kV Tondiarpet-NCTPS-1 at NCTPS end on Z2 however only two poles opened after around 520ms and later 450ms B-pole opened, 230kV Tondiarpet-NCTPS-2 at NCTPS end tripped on Z3 protection and 230kV Tondiarpet-Pulianthope at Pulianthope end on Z3 operation). Due to tripping of all the feeders at remote end led to the Complete outage of 230kV Tondiarpet and the tripping of Bus-1 at Basin Bridge. | TANTRANSCO to revamp the C&R panels at Tondiarpet end. | TANTRANSCO | cepc:TANTRANSCO: 30/03/2024 13:49:07: WILL BE COMPLIED cepc:TANTRANSCO: 03/05/2024 16:56:36: WILL BE COMPLIED cepc:TANTRANSCO: 02/07/2024 13:11:38: will be complied cepc:TANTRANSCO: 06/01/2025 16:20:59: will be complied cepc:TANTRANSCO: 03/02/2025 15:59:05: Due to non availability of space in the existing control room propsal for new AIS SS inside the exisitng campus submitted. cepc:TANTRANSCO: 04/03/2025 12:16:56: Due to non availability of space in control room proposalfor new AIS SS proposed cepc:TANTRANSCO: 05/04/2025 15:10:19: Due to space constraint, new AIS SS is proposed cepc:TANTRANSCO: 04/06/2025 13:46:23: Due to space constraint, new AIS SS is proposed cepc:TANTRANSCO: 03/07/2025 14:38:26: Due to space constraint new AIS SS is proposed. cepc:TANTRANSCO: 05/08/2025 13:02:10: Estimate Under preparation for New control room with C&R panels cepc:TANTRANSCO: 06/08/2025 10:47:42: Since obsolete LBB scheme, New Numerical BBP has been allotted. Commissioning activities under progress cepc:TANTRANSCO: 02/09/2025 13:45:54: renovation of control room alongwith C&R panel revamping is proposed under estimate stage cepc:TANTRANSCO: 04/10/2025 12:34:02: Under estimate stage cepc:TANTRANSCO: 06/11/2025 10:42:00: Under estimate stage cepc:TANTRANSCO: 04/12/2025 13:14:47: Estimate Stage cepc:TANTRANSCO: 05/01/2026 12:57:59: Under estimate stage cepc:TANTRANSCO: 02/02/2026 14:40:41: Under estimate stage cepc:TANTRANSCO: 04/03/2026 16:03:55: Under estimate stage cepc:TANTRANSCO: 30/03/2026 16:34:30: Under estimate stage | Pending | Pending
116/I/10 | Complete outage of 765kV Ariyalur and 765kV NCPS of TANTRANSCO | 26-01-2024 19:52 | 765kV Ariyalur and 765kV NCPS are being radially fed from 765kV Ariyalur-Thiruvalam-2. The triggering incident is the tripping of 765kV Ariyalur-Thiruvalam-2 at Thiruvalam end on over-voltage (settings kept not in accordance with SRPC guidelines. During the instance set at 105% at Thiruvalam end) leading to a complete outage of 765kV Ariyalur and 765kV NCPS of TANTRANSCO. | TANTRANSCO to conduct a comprehensive verification of SOTF logic activation in all 765 kV feeders. | TANTRANSCO | cepc:TANTRANSCO: 30/03/2024 13:49:07: WILL BE COMPLIED cepc:TANTRANSCO: 03/05/2024 16:56:36: COMPLIED cepc:TANTRANSCO: 02/07/2024 13:11:38: complied cepc:TANTRANSCO: 06/01/2025 16:20:59: complied cepc:TANTRANSCO: 03/02/2025 16:36:53: SOTF logic verified in all feeders & complied | Complied | Complied
116/III/11 | 400/110kV KAMUTHI ICT- 3 | 16-02-2024 18:12 | At the 400/230/110KV Kamuthi SS, ICT-3 tripped on Buchholz Trip indication | TANTRANCO to expedite the trip Contact Replacement at the earliest. | TANTRANSCO | cepc:TANTRANSCO: 30/03/2024 13:49:07: COMPLIED | Complied | Complied
117/I/6 | Complete Outage of 230kV Karaikudi (TN) | 19-03-2024 11:27 | 230kV/110kV Karaikudi SS is operating with a double bus with bus coupler configuration but high impedance differential relay with no zone segregation is used for Bus bar protection. As per the reports submitted, the triggering incident was an R-phase jumper failure between the isolator and the breaker of 230kV Karaikudi_PG Karaikudi_TN line-1 at Karaikuidi_TN SS. Immediately, 230kV BBP operated and all the lines connected to be bus tripped except 230kV Karaikudi NT Kudi Line-1 due to non-operation of 96 relay due to suspected contact moisture. 230kV Karaikudi NT Kudi Line-1 tripped on suspected delayed operation of 96 protection at Karaikudi end while which Z1 was sensed at 230kV Karaikudi-NT Kudy-1 at Karaikudi end. After the tripping of 230kV Bus-1 &2, the load was fed radially majorly by 110kV Karaikudi-Valuthur and 110kV Karaikudi-Sivagangai line. | 1.TANTRANSCO to transplay the event and furnish the report. 2.TANTRANSCO to carry out sag check and hot spots on 110KV Valuthur Karaikudi feeder | TANTRANSCO | cepc:TANTRANSCO: 03/05/2024 16:56:36: WILL BE COMPLIED cepc:TANTRANSCO: 02/07/2024 13:11:38: 1. will be complied 2will be complied cepc:TANTRANSCO: 06/01/2025 16:20:59: will be complied cepc:TANTRANSCO: 25/01/2025 12:33:10: Complied. The 230kv NT kudi-1 feeder Distance relay transplay could not be done for the incident on 19-3-24 due to LC constraint Now, the existing conventional C&R panel was replaced with new CRP under PSDF scheme on 7-01-2025 & Scheme checked found Normal. 110kv Karaikudi-Valuthur feeder_ line patrol was conducted tower to tower and line healthiness was confirmed by System Operation wing cepc:TANTRANSCO: 03/02/2025 16:11:56: Old C&R panel was repalced with New SAS panel 110kV Karaikudi_Valuthur line tower to tower checked by System operation wing hence complied | Complied | Complied
117/II/3 | Tripping of 765kV Bus section-3 at 765kV/400kV NCPS GIS | 07-03-2024 13:59 | As per the reports submitted, the triggering incident was the maloperation of PCS915 redundant BBP relay in 765kV Bus section-3 at 765kV/400kV NCPS without any actual GD Zone trip initiation from the corresponding bays. Immediately, all the elements connected to the bus tripped. | All entities to ensure to disable the GD Monitor Trip, wherever it is available, and configure for only alarm. | TANTRANSCO | cepc:TANTRANSCO: 03/05/2024 16:56:36: WILL BE COMPLIED cepc:TANTRANSCO: 02/07/2024 13:11:38: will be complied | Complied | Complied
117/II/3 | Tripping of 765kV Bus section-3 at 765kV/400kV NCPS GIS | 07-03-2024 13:59 | As per the reports submitted, the triggering incident was the maloperation of PCS915 redundant BBP relay in 765kV Bus section-3 at 765kV/400kV NCPS without any actual GD Zone trip initiation from the corresponding bays. Immediately, all the elements connected to the bus tripped. | TANTRANSCO to disable the GD Monitor trip to avoid mal operations and recom-mended to monitor the alarm stages. | TANTRANSCO | cepc:TANTRANSCO: 03/05/2024 16:56:36: NOW TRIP IS ASSIGNED TO ALARM AND UNDER OBSERVATION cepc:TANTRANSCO: 02/07/2024 13:11:38: complied | Complied | Complied
118/III/5 | 400/110kV KAMUTHI ICT-4 | 06-04-2024 21:41 | Neutral IOC protection operated in 400kV/110kV Kamuthi ICT tripped for a fault in 110kV Kamuthi Kavanur line | TANTRANSCO to ensure SOP to be followed by the field officials. | TANTRANSCO | cepc:TANTRANSCO: 02/07/2024 13:11:38: Instruction issued to follow SOP. This may be dropped | Complied | Complied
118/I/7 | Complete Outage of 765kV/400kV NCPS of TANTRANSCO and 765kV/400kV NCTPS Stage-3 of TANGEDCO | 18-04-2024 04:31 | In the antecedent condition 765kV NCPS-Ariyalur-2 was under outage and 765kV NCPS with 765kV NCTPS ST3 was being radially fed from 765kV NCPS-Ariyalur-1. The triggering incident Y-N fault in the 765kV NCPS-Ariyalur-1 line. At Ariyalur end, the fault was sensed in Z2 carrier aided protection with a fault current of 2.8kA and at a distance of 222km and AR operated and tripped due to persistent fault. At NCPS end, the AR was disabled as the line is in radial condition, the fault was sensed in Z1 protection with a distance of 30km and fault current of 1kA 3ph tripped. With the tripping of the only line connected to 765kV NCPS and radially feeding 765kV NCTPS ST3 led to the complete outage of 765kV NCPS and 765kV NCTPSST3. | 1.TANTRANSCO to ensure ROW for 765KV ARIYALUR NCPS lines. 2.TANTRANSCO to check the AR accelerated mode operation in other D60 relays. 3.TANTRANSCO to rectify the DR time sync issue at Ariyalur end. | TANTRANSCO | cepc:TANTRANSCO: 02/07/2024 13:11:38: 1. complied 2.complied 3. NIC card issue. New card received from OEM. will be attended | Complied | Complied
119/I/2 | Complete Outage of 230kV NCTPS Generating station of TANGEDCO | 23-04-2024 04:40 | As per the reports submitted, 8no. of 230kV Feeders are connected to the 230kV NCTPS Generating station. During antecedent conditions, 230kV Gummidipoondi NCTPS was idle charged from Gummidipoondi end. At 04:03hrs, 230kV NCTPS Alamthy and 230kV NCTPS Sriperumbudur lines tripped on R-N fault and the same can be seen in the PMU. At the same time, 230kV NCTPS Athipattu line tripped and the same can be seen in SCADA SOE. For 230kV NCTPS Sriperumbudur line, the fault was sensed in Zone1 at both ends and the line tripped. For 230kV NCTPS Alamathy line, at NCTPS end, the fault was sensed in Zone1. At Alamathy end, the fault was sensed in carrier aided Zone2 and the line tripped. Subsequently, at 04:38hrs, Y B fault was observed in 230kV NCTPS Kilpauk line. At NCTPS end, the fault was sensed in Zone1. At Kilpauk end, the fault was sensed in Zone2 and the line tripped with a delay of 350ms. At 04:39hrs, YB fault was observed in 230kV NCTPS Tondiarpet 2 where the fault was sensed in Zone-1 at NCTPS end and the tripping at Tondiarpet couldt be verified due to non-submission of DR. At the same time NCTPS Tondiarpet Line1 tripped on IN1 at Tondiarpet end and later hand tripped at NCTPS end. After tripping of all these lines, NCTPS Unit 1,2 & 3 tripped on over frequency. Subsequently, 230kV NCTPS Athipattu, 230kV NCTPS ETP line was hand tripped at NCTPS end, this led to complete outage of 230kV NCTPS Generating station | TANTRANSCO to expedite the process of revamping the C&R panels at 230kV NCTPS Generating station | TNPGCL | cepc:TANTRANSCO: 02/07/2024 13:11:38: pending with TANGEDCO cepc:TANTRANSCO: 06/01/2025 16:20:59: pending with TANGEDCO cepc:TANTRANSCO: 03/02/2025 16:38:22: pending with TNPGCL | Pending | Pending
119/I/2 | Complete Outage of 230kV NCTPS Generating station of TANGEDCO | 23-04-2024 04:40 | As per the reports submitted, 8no. of 230kV Feeders are connected to the 230kV NCTPS Generating station. During antecedent conditions, 230kV Gummidipoondi NCTPS was idle charged from Gummidipoondi end. At 04:03hrs, 230kV NCTPS Alamthy and 230kV NCTPS Sriperumbudur lines tripped on R-N fault and the same can be seen in the PMU. At the same time, 230kV NCTPS Athipattu line tripped and the same can be seen in SCADA SOE. For 230kV NCTPS Sriperumbudur line, the fault was sensed in Zone1 at both ends and the line tripped. For 230kV NCTPS Alamathy line, at NCTPS end, the fault was sensed in Zone1. At Alamathy end, the fault was sensed in carrier aided Zone2 and the line tripped. Subsequently, at 04:38hrs, Y B fault was observed in 230kV NCTPS Kilpauk line. At NCTPS end, the fault was sensed in Zone1. At Kilpauk end, the fault was sensed in Zone2 and the line tripped with a delay of 350ms. At 04:39hrs, YB fault was observed in 230kV NCTPS Tondiarpet 2 where the fault was sensed in Zone-1 at NCTPS end and the tripping at Tondiarpet couldt be verified due to non-submission of DR. At the same time NCTPS Tondiarpet Line1 tripped on IN1 at Tondiarpet end and later hand tripped at NCTPS end. After tripping of all these lines, NCTPS Unit 1,2 & 3 tripped on over frequency. Subsequently, 230kV NCTPS Athipattu, 230kV NCTPS ETP line was hand tripped at NCTPS end, this led to complete outage of 230kV NCTPS Generating station | TANTRANSCO to give feedback to planning or maintenance wing for tower upgradation, insulator replacement preventive maintenance system strengthening etc. | TANTRANSCO | cepc:TANTRANSCO: 02/07/2024 13:11:38: will be complied cepc:TANTRANSCO: 06/01/2025 16:20:59: addressed to System operation wing cepc:TANTRANSCO: 03/02/2025 16:56:45: Routine maintenance works Viz replacement of damaged insulators, replacement of weak jumpers, provision of polymer insulators, provision of bybass jumpers in the feeder emanating from NCTPS stage-I are being taken up by the maintenance wing regularly. However, estimate for replacement of damaged towers and conductors in 230KV NCTPS-ETPS, 230KV NCTPS-TPT I & II, 230KV NCTPS-Athipet-Mosur and NCTPS-Alamathy and 230KV NCTPS-Kilpauk and 230KV Korattur-Manali feeders have been got sanctioned & work to be taken up cepc:TANTRANSCO: 04/03/2025 11:50:28: Line maintenace work is being carriedout regularily by System Operation wing. Complied | Complied | Pending
119/I/2 | Complete Outage of 230kV NCTPS Generating station of TANGEDCO | 23-04-2024 04:40 | As per the reports submitted, 8no. of 230kV Feeders are connected to the 230kV NCTPS Generating station. During antecedent conditions, 230kV Gummidipoondi NCTPS was idle charged from Gummidipoondi end. At 04:03hrs, 230kV NCTPS Alamthy and 230kV NCTPS Sriperumbudur lines tripped on R-N fault and the same can be seen in the PMU. At the same time, 230kV NCTPS Athipattu line tripped and the same can be seen in SCADA SOE. For 230kV NCTPS Sriperumbudur line, the fault was sensed in Zone1 at both ends and the line tripped. For 230kV NCTPS Alamathy line, at NCTPS end, the fault was sensed in Zone1. At Alamathy end, the fault was sensed in carrier aided Zone2 and the line tripped. Subsequently, at 04:38hrs, Y B fault was observed in 230kV NCTPS Kilpauk line. At NCTPS end, the fault was sensed in Zone1. At Kilpauk end, the fault was sensed in Zone2 and the line tripped with a delay of 350ms. At 04:39hrs, YB fault was observed in 230kV NCTPS Tondiarpet 2 where the fault was sensed in Zone-1 at NCTPS end and the tripping at Tondiarpet couldt be verified due to non-submission of DR. At the same time NCTPS Tondiarpet Line1 tripped on IN1 at Tondiarpet end and later hand tripped at NCTPS end. After tripping of all these lines, NCTPS Unit 1,2 & 3 tripped on over frequency. Subsequently, 230kV NCTPS Athipattu, 230kV NCTPS ETP line was hand tripped at NCTPS end, this led to complete outage of 230kV NCTPS Generating station | TANTRANSCO to rectify the DR time sync issue in 230kV NCTPS Alamathy line at NCTPS end, 230kV NCTPS SRIPERUMBUDUR at Sriperumbudur end | TANTRANSCO | cepc:TANTRANSCO: 02/07/2024 13:11:38: will be complied cepc:TANTRANSCO: 06/01/2025 16:20:59: will be complied cepc:TANTRANSCO: 03/02/2025 16:38:22: Sriperumpudhur end C&R panel revamped & time sync issue rectified cepc:TANTRANSCO: 04/03/2025 11:42:57: Complied at Sriperumpudhur end cepc:TANTRANSCO: 05/04/2025 15:21:52: Complied at Sriperumpudhur end | Complied | Pending
119/I/8 | Complete Outage of 230kV/110kV Gummudipoondi SS of TANTRANSCO, 230kV Cauvery SS, 230kV Kamachi SS, 230kV Thervoi Kandigai SS, and 230kV Mychelin SS | 08-05-2024 11:14 | 230kV Cauvery SS, 230kV Kamachi SS, 230kV Thervoi Kandigai SS, and 230kV Mychelin SS are being radially connected to 230kV/110kV Gummidipoondi SS. During antecedent conditions, 230kV Gummidipoondi NCTPS line was idle charged from Gummidipoondi end. As per the reports submitted the triggering incident was B-phase jumper failure in 230kV Gummidipoondi Sullurpet line at Gummudipoondi station causing a bus fault in North bus | TANTRANSCO to rectify the time synchronization issue at 230kV Gummidipoondi SS | TANTRANSCO | cepc:TANTRANSCO: 02/07/2024 13:11:38: relay sync with GPS & complied | Complied | Complied
119/III/5 | 400kV/110kV Vellalaviduthi-ICT-1 | 29-04-2024 18:41 | 400KV/110KV Vellalaviduthi-ICT-1 tripped on REF protection for an L-G fault in downstream 110kV Line. | TANTRANSCO to take up the matter with OEM regarding REF operation. | TANTRANSCO | cepc:TANTRANSCO: 02/07/2024 13:11:38: Neutral CT wire were interchanged and after that No tripping was observed for the 110kV feeder faults. & complied cepc:TANTRANSCO: 06/01/2025 16:20:59: Netural CT of ICT 1 Polarity had reversed by OEM and the operation of REF confirmed by further tripping of 110 KV Feeders cepc:TANTRANSCO: 03/02/2025 16:39:30: As per OEM recommendation, Neutral CT polarity reversed | Complied | Complied
119/VI/3 | 220 kV Chittor - Thiruvalem | 02-05-2024 10:46 | For a single line to Ground fault (B, N), PD operated But at 12.02 Hrs, for the same fault AR found successful at Thiruvalam end. | TANTRANSCO to furnish the remedial action taken. | TANTRANSCO | cepc:TANTRANSCO: 02/07/2024 13:11:38: relay sync with GPS. & complied | Complied | Complied
119/VI/9 | 400kV Palavadi Rasipalayam-1 | 09-05-2024 23:04 | For the Line to Line ZONE.2 fault, CAT & 3 phase trip initiated. | TANTRANSCO to furnish the remedial action taken. | TANTRANSCO | cepc:TANTRANSCO: 02/07/2024 13:11:38: relay sync with GPS & complied | Complied | Complied
120/I/1 | Complete Outage of 230kV Tondiarpet SS, 230kV Basin Bridge SS, 400kV/230kV Puliyanthope SS, 230kV Koratturi SS, 230kV CMRL SS, Vyasarpadi SS of TANTRANSCO and 230kV NCTPS Generating station of TANGEDCO: | 17-05-2024 09:01 | As per the reports submitted, the triggering incident is the R ph jumper cut of 230kV NCTPS Tondiarpet 2. The R ph jumper came into contact of Y ph at Tondiarpet end and created an RYN fault and Z1 operated and 3ph tripped | TANTRANSCO Preventive maintenance to be taken up more frequently | TANTRANSCO | cepc:TANTRANSCO: 06/08/2024 10:28:07: Monthly maintenace have been carried out by Maintenance wing | Complied | Pending
120/I/1 | Complete Outage of 230kV Tondiarpet SS, 230kV Basin Bridge SS, 400kV/230kV Puliyanthope SS, 230kV Koratturi SS, 230kV CMRL SS, Vyasarpadi SS of TANTRANSCO and 230kV NCTPS Generating station of TANGEDCO: | 17-05-2024 09:01 | As per the reports submitted, the triggering incident is the R ph jumper cut of 230kV NCTPS Tondiarpet 2. The R ph jumper came into contact of Y ph at Tondiarpet end and created an RYN fault and Z1 operated and 3ph tripped | TANTRANSCO to furnish the feedback to Higher Management for upgradation and modernisation of Intra-state system in that area as feeding to Chennai. | TANTRANSCO | cepc:TANTRANSCO: 06/08/2024 10:28:07: Addressed to System operation wing of TANTRANSCO on 31.07.2024 for necessary action | Complied | Pending
120/I/1 | Complete Outage of 230kV Tondiarpet SS, 230kV Basin Bridge SS, 400kV/230kV Puliyanthope SS, 230kV Koratturi SS, 230kV CMRL SS, Vyasarpadi SS of TANTRANSCO and 230kV NCTPS Generating station of TANGEDCO: | 17-05-2024 09:01 | As per the reports submitted, the triggering incident is the R ph jumper cut of 230kV NCTPS Tondiarpet 2. The R ph jumper came into contact of Y ph at Tondiarpet end and created an RYN fault and Z1 operated and 3ph tripped | TANTRANSCO to rectify the DR time sync issue at NCTPS and Alamathy end. | TANTRANSCO | cepc:TANTRANSCO: 06/08/2024 10:25:10: Can be implemented after revamping of C&R panel by TANGEDCO at NCTPS end . pending with TANGEDCO At Almathay end, one of the main relay is not having IRIG-B port for time sync. Will be complied cepc:TANTRANSCO: 01/10/2024 17:12:08: At Alamathy end Relay has to be changed cepc:TANTRANSCO: 06/01/2025 16:05:13: relay has to be replaced at Alamathy end cepc:TANTRANSCO: 03/02/2025 16:51:19: Relay has to be replaced at Alamathy end cepc:TANTRANSCO: 04/03/2025 13:06:48: Relay has to be replaced at Alamathy end cepc:TANTRANSCO: 04/06/2025 13:47:44: Relay has to be replaced at Alamathy end cepc:TANTRANSCO: 01/07/2025 16:06:38: Relay allotted. Line clear awaited cepc:TANTRANSCO: 06/08/2025 16:25:48: Line clear awaited cepc:TANTRANSCO: 02/09/2025 13:38:09: Line clear awaited. Time line requested upto 31.12.2025 cepc:TANTRANSCO: 03/10/2025 17:02:45: Time line requested upto 31.12.2025 at Alamathy end cepc:TANTRANSCO: 06/11/2025 10:42:00: Time line requested upto 31.12.2025 cepc:TANTRANSCO: 04/12/2025 13:14:47: Time line requested upto 31.12.2025 cepc:TANTRANSCO: 05/01/2026 12:57:59: Line Clear awaited cepc:TANTRANSCO: 02/02/2026 14:40:41: Line Clear awaited cepc:TANTRANSCO: 04/03/2026 16:03:55: Line clear awaited cepc:TANTRANSCO: 30/03/2026 16:34:30: Line clear awaited | Pending | Pending
120/I/1 | Complete Outage of 230kV Tondiarpet SS, 230kV Basin Bridge SS, 400kV/230kV Puliyanthope SS, 230kV Koratturi SS, 230kV CMRL SS, Vyasarpadi SS of TANTRANSCO and 230kV NCTPS Generating station of TANGEDCO: | 17-05-2024 09:01 | As per the reports submitted, the triggering incident is the R ph jumper cut of 230kV NCTPS Tondiarpet 2. The R ph jumper came into contact of Y ph at Tondiarpet end and created an RYN fault and Z1 operated and 3ph tripped | TANTRANSCO to review the Zone-1 settings at NCTPS end. | TNPGCL | cepc:TANTRANSCO: 06/08/2024 10:22:44: Awaiting Line Clear for Transplay the DR cepc:TANTRANSCO: 01/10/2024 11:29:07: DR analysed at NCTPS end & found in order. Line fault Loc.17 from NCTPS_R phase jumper cut cepc:TANTRANSCO: 06/01/2025 16:05:13: addressed to OEM cepc:TANTRANSCO: 03/02/2025 16:50:26: Suspected relay issue. Addressed to OEM cepc:TANTRANSCO: 04/03/2025 11:58:38: OEM recommended to upgrade the relay software. Pending with TNPGCL cepc:TANTRANSCO: 05/04/2025 15:08:14: pending with TNPGCL cepc:TANTRANSCO: 04/06/2025 13:47:44: pending with TNPGCL cepc:TANTRANSCO: 01/07/2025 16:04:57: OEM recommended to upgrade the relay Pending with TNPGCL cepc:TANTRANSCO: 01/07/2025 16:06:38: OEM recommended to upgrade the relay Pending with TNPGCL cepc:TANTRANSCO: 06/08/2025 16:25:48: Pending with TNPGCL cepc:TANTRANSCO: 03/10/2025 17:02:45: pending with TNPGCL | Pending | Pending
120/I/5 | Complete Outage of 230kV/110kV Checkanurani SS of TANTRANSCO | 30-05-2024 16:44 | As per the reports submitted, the triggering incident was R-phase CT failure in 230kV Checkanurani Renganathapuram line at Checkanurani end causing a Bus fault in 230kV Bus-1 at 16.44.54.283 | TANTRANSCO to check & update the BBP settings of Bus bar-2 | TANTRANSCO | cepc:TANTRANSCO: 06/08/2024 11:17:53: Checked & found in order Complied | Complied | Complied
120/I/5 | Complete Outage of 230kV/110kV Checkanurani SS of TANTRANSCO | 30-05-2024 16:44 | As per the reports submitted, the triggering incident was R-phase CT failure in 230kV Checkanurani Renganathapuram line at Checkanurani end causing a Bus fault in 230kV Bus-1 at 16.44.54.283 | TANTRANSCO to check & update the reason for non sensing of fault of 230kV Checkkanurani Ranganathapuram on Z2/Z3 at Ranganathapuram | TANTRANSCO | cepc:TANTRANSCO: 06/08/2024 10:31:34: During the incident, Renganathapuram end senses the fault in Zone.3. The same was Confirmed with DR | Complied | Complied
120/I/5 | Complete Outage of 230kV/110kV Checkanurani SS of TANTRANSCO | 30-05-2024 16:44 | As per the reports submitted, the triggering incident was R-phase CT failure in 230kV Checkanurani Renganathapuram line at Checkanurani end causing a Bus fault in 230kV Bus-1 at 16.44.54.283 | TANTRANSCO to update the DR legends for BBP operation Chechanurani. | TANTRANSCO | cepc:TANTRANSCO: 06/08/2024 11:17:53: Digital signals have been configured based on availability in the BBP relay | Complied | Complied
120/II/1 | Tripping of 400kV/230kV Alamathy SS of TANTRANSCO | 16-05-2024 12:45 | As per the reports submitted, the triggering incident was R-N faut in 400kV Alamathy NCTPS Stage-2 Line-1. At both ends, the fault was sensed in Zone-1 and R-pole opened. After A/R dead time, the SOTF operated due to persistent fault. However, Y-pole of the breaker did not operate causing LBB to operate. Immediately all the breakers connected to the 400kV Bus-2 tripped and DT was sent to NCTPS end, this led to tripping of all main breakers connected to 400kV Bus-2 at 400kV/230kV Alamathy SS. However, from the PMU plot it can be observed that R-phase of the Bus-2 voltage became zero only after 2seconds of LBB operation | TANTRANSCO to check the healthiness of all breakers at Alamathy end | TANTRANSCO | cepc:TANTRANSCO: 06/01/2025 16:09:50: Healthiness of brekaer is being checked during monthly maintenece. Complied cepc:TANTRANSCO: 25/01/2025 13:34:35: Complied Breaker mechanism lubricated , maintenance and testing carried out by System operation wing | Complied | Pending
120/II/1 | Tripping of 400kV/230kV Alamathy SS of TANTRANSCO | 16-05-2024 12:45 | As per the reports submitted, the triggering incident was R-N faut in 400kV Alamathy NCTPS Stage-2 Line-1. At both ends, the fault was sensed in Zone-1 and R-pole opened. After A/R dead time, the SOTF operated due to persistent fault. However, Y-pole of the breaker did not operate causing LBB to operate. Immediately all the breakers connected to the 400kV Bus-2 tripped and DT was sent to NCTPS end, this led to tripping of all main breakers connected to 400kV Bus-2 at 400kV/230kV Alamathy SS. However, from the PMU plot it can be observed that R-phase of the Bus-2 voltage became zero only after 2seconds of LBB operation | TANTRANSCO to rectify the DR time sync issue at NCTPS end | TNPGCL | cepc:TANTRANSCO: 06/01/2025 16:09:50: related to TANGEDCO cepc:TANTRANSCO: 03/02/2025 16:00:15: related to TNPGCL | Pending | Pending
120/II/2 | Tripping of 230kV Bus-2 of NCTPS Generating Station of TANGEDCO | 17-05-2024 02:37 | 230kV NCTPS is equipped with Single Bus with two Bus Sectionalizer scheme. Where in the affected area SLD and network connectivity of 230kV NCTPS is as shown below. In the antecedent conditions the 230kV NCTPS-NCTPSSt3 and 230kV NCTPS-Kilpauk lines were idle charged from 230kV NCTPS end. In Bus-1 the connectivity is STrf-1, Kilpauk (idle charged), NCTPSSt3 (idle charged) and U1. In Bus-2 the connectivity is STrf-2, Tondiarpet-1, Sriperambadur and U2. | TANTRANSCO to ensure the healthiness of the equipment by carry out regular maintenance activities. | TNPGCL | cepc:TANTRANSCO: 06/01/2025 16:17:12: related to TANGEDCO cepc:TANTRANSCO: 03/02/2025 16:55:22: related to TNPGCL | Pending | Pending
120/II/2 | Tripping of 230kV Bus-2 of NCTPS Generating Station of TANGEDCO | 17-05-2024 02:37 | 230kV NCTPS is equipped with Single Bus with two Bus Sectionalizer scheme. Where in the affected area SLD and network connectivity of 230kV NCTPS is as shown below. In the antecedent conditions the 230kV NCTPS-NCTPSSt3 and 230kV NCTPS-Kilpauk lines were idle charged from 230kV NCTPS end. In Bus-1 the connectivity is STrf-1, Kilpauk (idle charged), NCTPSSt3 (idle charged) and U1. In Bus-2 the connectivity is STrf-2, Tondiarpet-1, Sriperambadur and U2. | TANTRANSCO to expedite the process to enable A/R for 230kV NCTPS-Sriperambadur at both ends. | TNPGCL | cepc:TANTRANSCO: 06/01/2025 16:17:12: AR enabled at Sriperumpudhur end. cepc:TANTRANSCO: 03/02/2025 16:45:51: AR enabled at Sriperumpudhur end . NCTPS end pending with TNPGCL cepc:TANTRANSCO: 04/03/2025 13:07:56: AR enabled at Sriperumpudhur end | Pending | Pending
120/II/2 | Tripping of 230kV Bus-2 of NCTPS Generating Station of TANGEDCO | 17-05-2024 02:37 | 230kV NCTPS is equipped with Single Bus with two Bus Sectionalizer scheme. Where in the affected area SLD and network connectivity of 230kV NCTPS is as shown below. In the antecedent conditions the 230kV NCTPS-NCTPSSt3 and 230kV NCTPS-Kilpauk lines were idle charged from 230kV NCTPS end. In Bus-1 the connectivity is STrf-1, Kilpauk (idle charged), NCTPSSt3 (idle charged) and U1. In Bus-2 the connectivity is STrf-2, Tondiarpet-1, Sriperambadur and U2. | TANTRANSCO to take up with Higher Management on upgradation and renovation of transmission system feeding to Chennai area. | TANTRANSCO | cepc:TANTRANSCO: 06/01/2025 16:17:12: addressed to System operation wing cepc:TANTRANSCO: 04/03/2025 11:44:02: addressed to System operation wing | Complied | Pending
120/II/10 | Tripping of 230kV Bus of 230kV/110kV Karaikudi SS of TANTARNSCO | 06-06-2024 08:11 | 230kV/110kV Karaikudi SS is operating with a double bus with bus coupler configuration but high impedance differential relay is equipped where in there is no zone segregation for Bus bar protection. As per the reports submitted, the triggering incident was a Y-N Bus fault at 230kV Karaikudi station. Bus bar protection operated and all the elements connected to 230kV Karaikudi station tripped, but 230kV Karaikudi-NT Kudi-2 feeder was conducting the fault even when the status of breaker was under open condition due to suspected SF6 contamination in the Y-pole of the breaker and the same can be observed from the DR. | TANTRANSCO to ensure the healthiness of the CBs. | TANTRANSCO | cepc:TANTRANSCO: 06/01/2025 16:17:12: healthiness of breaker is being carried out during monthly maintenece complied cepc:TANTRANSCO: 25/01/2025 12:33:10: Complied. The 230kv NT Kudi-2 feeder breaker Y-Ph Limb was overhauled and put in to service on 22-6-2024 | Complied | Complied
120/II/11 | Tripping of 110kV Bus-1&2 of 400kV/230kV/110kV Alamathy SS of TANTRANSCO | 13-06-2024 15:57 | As per the reports submitted, the triggering incident was the Y-B fault in the 110kV Alamathy-Periyapalayam Line. The fault was sensed in Z1 at Alamathy end, where in Y-pole breaker successfully opened but B-Phase breaker failed to open at 110kV Alamathy end. However, Z1 dropped before picking up in the DR even when the fault was being continuously fed in the B-phase | TANTRANSCO to examine the cause for the Non opening of 110kV bus coupler after LBB operation. | TANTRANSCO | cepc:TANTRANSCO: 06/01/2025 16:17:12: will be complied cepc:TANTRANSCO: 03/02/2025 16:52:24: Breaker mechanism lubricated , maintenance and testing carried out Complied | Complied | Pending
120/II/11 | Tripping of 110kV Bus-1&2 of 400kV/230kV/110kV Alamathy SS of TANTRANSCO | 13-06-2024 15:57 | As per the reports submitted, the triggering incident was the Y-B fault in the 110kV Alamathy-Periyapalayam Line. The fault was sensed in Z1 at Alamathy end, where in Y-pole breaker successfully opened but B-Phase breaker failed to open at 110kV Alamathy end. However, Z1 dropped before picking up in the DR even when the fault was being continuously fed in the B-phase | TANTRANSCO to furnish the reason for dropping of Z1 even when the fault was being fed in B-ph for 110kV Alamathy- Periyapalayam at Alamathy | TANTRANSCO | cepc:TANTRANSCO: 06/01/2025 16:17:12: will be complied cepc:TANTRANSCO: 03/02/2025 16:46:32: relay has to be checked. Line clear awaited cepc:TANTRANSCO: 04/03/2025 11:43:21: Line clear awaited cepc:TANTRANSCO: 05/04/2025 15:24:48: Line clear awaited. Time line requested upto 30.04.2025 cepc:TANTRANSCO: 04/06/2025 13:30:57: Conducted relay test & found Normal. The said distance relay is old version, Hence it is proposed to replace the same with spare one. Time line requested upto 31.07.2025 cepc:TANTRANSCO: 03/07/2025 14:57:33: Distance relay is old version.it is proposed to replace the old relay with spare one. Time line requested upto 31.08.2025 cepc:TANTRANSCO: 05/08/2025 13:08:57: Relay alloted .Will be replaced on availing Line clear. cepc:TANTRANSCO: 02/09/2025 13:47:11: Relay allotted.Time line requested upto 31.12.2025 cepc:TANTRANSCO: 03/10/2025 17:02:45: Time line requested upto 31.12.2025 cepc:TANTRANSCO: 06/11/2025 10:42:00: Time line requested upto 31.12.2025 cepc:TANTRANSCO: 04/12/2025 13:14:47: Time line requested upto 31.12.2025 cepc:TANTRANSCO: 05/01/2026 12:57:59: Line clear awaited cepc:TANTRANSCO: 02/02/2026 14:40:41: Line clear awaited cepc:TANTRANSCO: 04/03/2026 16:03:55: Line clear awaited cepc:TANTRANSCO: 30/03/2026 16:34:30: Old distance relay has to be replaced with new one | Pending | Pending
120/III/9 | Tripping of 400/230 kV ICT 4 AT Almathy | 18-06-2024 03:03 | 400/230 kV ICT 4 at Almathy tripped on Bucholz Trip | TANTRANSCO to carry out regular monitoring the parameters of every protection element | TANTRANSCO | cepc:TANTRANSCO: 06/01/2025 16:17:12: will be ensured cepc:TANTRANSCO: 03/02/2025 16:47:24: Regular monitoring of all the parameters are being carried out. Complied | Complied | Complied
120/IV/8 | 400kV-Ariyalur-Kalvendapattu-1 | 22-06-2024 19:08 | Scheme check has to be carried out | TANTRANSCO to carry out the scheme check and furnish the remedial action taken | TANTRANSCO | cepc:TANTRANSCO: 06/08/2024 10:22:00: Awaiting Line Clear cepc:TANTRANSCO: 01/10/2024 11:44:06: Line clear proposed on 17.10.2024 cepc:TANTRANSCO: 01/10/2024 14:48:52: OEM Recommended for replacement of NIC card. Card supplied. Will be replaced on availing Line clear cepc:TANTRANSCO: 06/01/2025 16:09:50: NIC card replaced on 15.10.2024 & checked found normal. Complied cepc:TANTRANSCO: 03/02/2025 16:48:16: NIC card replaced on 15.10.2024 & complied | Complied | Complied
121/I/4 | Complete Outage of 230kV Kilpauk SS | 03-07-2024 20:53 | 230kV Kilpauk is connected to 230kV Koratur and 230kV NCTPS. In the antecedent conditions, 230kV Koratur-Kilpauk was in idle charged condition and 230kV Kilpauk was radially connected to 230kV NCTPS. The triggering incident is the fault in 230kV NCTPS-NCTPSST3 line near to the substation at 230kV NCTPS. At NCTPS end, line tripped on operation of Zone-1 protection | TANGEDCO to expedite the revamping of C&R panels at NCTPS. | TNPGCL | eemrtnctps1:TNPGCL: 04/09/2024 11:41:27: Technical specification preparation work under progress for complete renovation of 8 Nos 230KV feeders control and Relay panels. Technical Specification details requested from P&C wing is yet to be received. Reminder letter sent on 29-08-2024.On finalization, proposal will be submitted to competent authority (HQ) for administrative approval. The auto reclosure feature is included in this proposal eemrtnctps1:TNPGCL: 01/10/2024 11:59:45: Technical specification preparation work under progress for complete renovation of 8 Nos 230KV feeders control and Relay panels. Technical Specification details requested from P&C wing is yet to be received. Reminder letter sent on 29-08-2024.On finalization, proposal will be submitted to competent authority (HQ) for administrative approval. The auto reclosure feature is included in this proposal eemrtnctps1:TNPGCL: 06/01/2025 16:48:45: Technical specification received from P&C wing Budgetary offer called for, from reputed firms. The proposal for administrative approval will be submitted after receipt of budgetary offers. | Pending | Pending
121/I/4 | Complete Outage of 230kV Kilpauk SS | 03-07-2024 20:53 | 230kV Kilpauk is connected to 230kV Koratur and 230kV NCTPS. In the antecedent conditions, 230kV Koratur-Kilpauk was in idle charged condition and 230kV Kilpauk was radially connected to 230kV NCTPS. The triggering incident is the fault in 230kV NCTPS-NCTPSST3 line near to the substation at 230kV NCTPS. At NCTPS end, line tripped on operation of Zone-1 protection | TANTRANSCO to enable Auto reclose at Kilpauk end. | TANTRANSCO | cepc:TANTRANSCO: 01/10/2024 10:19:28: AR enabled at Kilpauk SS on 09.08.2024 | Complied | Pending
121/III/4 | Tripping at 400kV-KAYATHAR-KANARPATTI-2 | 04-07-2024 12:32 | 400kV-KAYATHAR line-2 tripped with B phase Zone-1 indication & AR Lockout was initiated and tripped at both ends. | TANTRANSCO to check the healthiness of the breaker. | TANTRANSCO | cepc:TANTRANSCO: 01/10/2024 11:36:35: Line clear proposed on 14.10.2024 cepc:TANTRANSCO: 06/01/2025 16:09:50: Line clear awaited cepc:TANTRANSCO: 03/02/2025 16:49:03: AR checked on 07.01.2025 and Complied | Complied | Complied
121/III/6 | 400kV/230kV THIRUVALAM ICT-3 | 10-07-2024 22:30 | 400 kV THIRUVALAM SS- 400/230kV 500MVA ICT 3 TRIPPED ON DIFFERENTIAL PROTECTION in main 2 relay LV CBs got tripped during through transient fault in 230kV Kanchipuram | TANTRANSCO to check the logic of within zone grounding selection in all GE T60 relays. | TANTRANSCO | cepc:TANTRANSCO: 01/10/2024 10:20:26: complied | Complied | Complied
121/III/13 | Tripping at 220kV-THENI- SABARIGIRI-1 | 21-07-2024 15:17 | 220 kV SABARIGIRI THENI feeder tripped at both ends. Directional earth pick up indication in the back up relay. | TANTRANSCO to enable DT for DEF operation for 220kV Sabarigiri Theni line | TANTRANSCO | cepc:TANTRANSCO: 01/10/2024 11:29:07: implemented on 11.09.2024 | Complied | Complied
122/I/7 | Complete Outage of 230kV/110kV Kayathar SS | 04-08-2024 11:57 | The triggering incident was Y-N fault in 230kV Kayathar Sanganeri Line-1. At Kayathar end, at the time of lockout, Y-pole breaker failed to open at Kayathar end causing LBB to operate. Immediately, LBB operated and all lines connected to the 230kV Kayathar Bus tripped. This led to complete outage of 230kV/110kV Kayathar SS of TANTRANSCO. | TANTRANSCO to check the breaker operation at Kayathar end in 230kV Kayathar Sanganeri line. | TANTRANSCO | cepc:TANTRANSCO: 01/10/2024 17:12:08: It is proposed to replace the faulty breaker. Now BC breaker substituted cepc:TANTRANSCO: 06/01/2025 16:03:26: breaker replaced on 14.10.2024 cepc:TANTRANSCO: 03/02/2025 17:09:14: defective breaker replaced with new one on 14.10.2024 | Complied | Complied
122/I/7 | Complete Outage of 230kV/110kV Kayathar SS | 04-08-2024 11:57 | The triggering incident was Y-N fault in 230kV Kayathar Sanganeri Line-1. At Kayathar end, at the time of lockout, Y-pole breaker failed to open at Kayathar end causing LBB to operate. Immediately, LBB operated and all lines connected to the 230kV Kayathar Bus tripped. This led to complete outage of 230kV/110kV Kayathar SS of TANTRANSCO. | TANTRANSCO to rectify the DR time sync issues at Sanganeri end. | TANTRANSCO | cepc:TANTRANSCO: 01/10/2024 17:12:08: complied | Complied | Complied
122/I/7 | Complete Outage of 230kV/110kV Kayathar SS | 04-08-2024 11:57 | The triggering incident was Y-N fault in 230kV Kayathar Sanganeri Line-1. At Kayathar end, at the time of lockout, Y-pole breaker failed to open at Kayathar end causing LBB to operate. Immediately, LBB operated and all lines connected to the 230kV Kayathar Bus tripped. This led to complete outage of 230kV/110kV Kayathar SS of TANTRANSCO. | TANTRANSCO to rectify the non-availability of event in SCADA SOE. | TANTRANSCO | cepc:TANTRANSCO: 01/10/2024 17:12:08: C&R panel revamping under progress( 9 bays completed).SCADA availability will be ensured on completion cepc:TANTRANSCO: 06/01/2025 16:03:26: C&R panel revamping work under progress. all 100kV feeder & 6 No of 230kV bay SOE reported & remaining will be complied cepc:TANTRANSCO: 03/02/2025 17:09:14: C&R panel revamping is under progress cepc:TANTRANSCO: 04/03/2025 11:51:50: C&R panel with SAS revamping work under progress cepc:TANTRANSCO: 05/04/2025 15:21:52: C&R with SAS panel revamping work under progress Time line requested upto 30.06.2025 cepc:TANTRANSCO: 07/05/2025 16:28:43: SCADA_ SOE restored on 02.05.2025 | Complied | Complied
122/I/7 | Complete Outage of 230kV/110kV Kayathar SS | 04-08-2024 11:57 | The triggering incident was Y-N fault in 230kV Kayathar Sanganeri Line-1. At Kayathar end, at the time of lockout, Y-pole breaker failed to open at Kayathar end causing LBB to operate. Immediately, LBB operated and all lines connected to the 230kV Kayathar Bus tripped. This led to complete outage of 230kV/110kV Kayathar SS of TANTRANSCO. | TANTRANSCO to review the DR report, analyze the event and submit revised report. | TANTRANSCO | cepc:TANTRANSCO: 01/10/2024 17:12:08: Breaker defective .It is proposed to replace the breaker cepc:TANTRANSCO: 06/01/2025 16:03:26: complied. AR found succesful in subsequent fault. cepc:TANTRANSCO: 03/02/2025 17:09:14: complied | Complied | Complied
122/III/1 | 400KV/110KV KANARPATTI-ICT-5 | 24-07-2024 13:08 | 400KV/110KV KANARPATTI-ICT-5 CT cable of main CT of 413 bay got earthed in R phase and differential protection operated for ICT5 during commissioning works of ICT6. | TANTRANSCO to follow the SOP. | TANTRANSCO | cepc:TANTRANSCO: 01/10/2024 17:12:08: will be followed | Complied | Complied
122/III/9 | 400KV/110KV KAYATHAR-ICT-1 | 12-08-2024 16:11 | 400kV/110kV Kayathar ICT-1 tripped on operation of DC earth fault. | TANTRANSCO to expediate the replacement works at Kayathar substation. | TANTRANSCO | cepc:TANTRANSCO: 01/10/2024 11:30:36: Line clear proposed on 14.10.2024 cepc:TANTRANSCO: 06/01/2025 16:09:50: Line clear awaited cepc:TANTRANSCO: 03/02/2025 16:49:49: DC leakage to be attended Line clear awaited cepc:TANTRANSCO: 04/03/2025 11:48:18: DC leakage was observed due to control cable defect in Karaikudi feeder.1 , The existing 28 x 2.5 Sqmm defectice control cable was replaced with new one on 15.02.2025 & tested found normal Complied cepc:TANTRANSCO: 05/04/2025 15:22:41: Cable replacement done on 15.02.2025 | Complied | Complied
123/I/1 | Complete Outage of 765kV NCTPS ST3 Generating Station of TANGEDCO | 28-08-2024 06:23 | The triggering incident was B-N fault near Unit-1 of 765kV NCTPS ST3. Immediately, overall differential protection operated and the Unit tripped. Simultaneously, 765kV NCPS NCTPS ST3 line-1&2 sensed the fault in zone-2 and tripped instantaneously at NCPS end. Subsequently, 765kV Ariyalur NCPS Line-2 tripped on over voltage protection at NCPS end. Tripping of both lines connected to 765kV NCTPS ST3 Generating Station resulted in Complete outage of the Generating Station. | TANTRANSCO to follow the SOP at the time of initial charging | TANTRANSCO | cepc:TANTRANSCO: 04/11/2024 18:59:20: SOP is being followed.Necessary initiative will be taken to avoid recurrence. | Complied | Complied
123/I/1 | Complete Outage of 765kV NCTPS ST3 Generating Station of TANGEDCO | 28-08-2024 06:23 | The triggering incident was B-N fault near Unit-1 of 765kV NCTPS ST3. Immediately, overall differential protection operated and the Unit tripped. Simultaneously, 765kV NCPS NCTPS ST3 line-1&2 sensed the fault in zone-2 and tripped instantaneously at NCPS end. Subsequently, 765kV Ariyalur NCPS Line-2 tripped on over voltage protection at NCPS end. Tripping of both lines connected to 765kV NCTPS ST3 Generating Station resulted in Complete outage of the Generating Station. | TANTRANSCO to verify the relay settings of all newly commissioned lines are as per the approved relay settings. | TANTRANSCO | cepc:TANTRANSCO: 04/11/2024 18:59:20: will be ensured. | Complied | Complied
123/I/8 | Complete Outage of 230kV/110kV Gummudipoondi SS | 05-09-2024 10:14 | During antecedent conditions, Gummidipoondi Substation was radially connected through 230kV Gummidipoondi_ Sulurpet Line. 230V Gummidipoondi_Suryadev and 230kV Gummidipoondi NCTPS were out of service for power regulation. As per the reports submitted, the triggering incident was Y-N fault in 230kV Gummidipoondi_ Sulurpet Line. Tripping of only connected line led to complete outage of 230kV/110kV Gummidipoondi SS. Since 230kV Surya Dev, 230kV ARS, 230kV Mychelin, 230kV Cauvery, 230kV Thervoi Kandigoi, 230kV Kamachi are radially connected to 230kV/110kV Gummidipoondi SS, complete outage of 230kV/110kV Gummidipoondi SS led to complete outage of the radial connected stations also. | TNSLDC/TANTRANSCO to ensure reliable connection to Gummidipoondi station | TANTRANSCO | cepc:TANTRANSCO: 04/11/2024 18:59:20: Informed to SLDC to ensure reliable connectivity | Complied | Complied
123/I/9 | Complete Outage 230kV/110kV Karaikudi SS | 09-09-2024 10:08 | 230kV Karaikudi SS has double bus with bus coupler without bus segregation in BBP. As per the reports submitted, the triggering incident was R-phase jumper cut in 230kV Karaikudi karaikudi_PG Line-2 between breaker and isolator causing a bus fault. Immediately, 230kV BBP operated and all elements connected to the bus tripped. Tripping of all elements connected to 230kV Bus resulted in tripping of 230kV bus of 230kV/110kV Karaikudi SS. Subsequently, other two110kV source feeders tripped on fault and over current protection. This led to complete outage of 110kV Bus of 230kV/110kV Karaikudi SS leading to complete outage of 230kV/110kV Karaikudi SS. | TANTRANSCO to ensure to carry out regular maintenance at Karaikudi station | TANTRANSCO | cepc:TANTRANSCO: 04/11/2024 18:56:47: Addressed to System operation wing | Complied | Complied
123/I/10 | Complete Outage of 400kV/230kV/110kV MANALI, 400kV/230kV PULIYANTHOPE, 230kV VYSARPADI, 230kV/110kV TONDIARPET, 230kV/110kV BASIN_BRIDGE, 230kV/33kV MYLAPORE_GIS, 230kV/110kV CMRL_CENTRAL, 230kV/33kV TNEB_HQ, 230kV/110kV RAPURAM and 230kV/110kV MYLAPORE. | 12-09-2024 21:54 | During antecedent conditions, 230kV VYSARPADI was radially fed from 400kV/230kV PULIYANTHOPE and due to outage of 230kV Tharamani Rapuram line, 230kV Tharamani Mylapore line, 230kV Tharamani KITZ line, 230kV Rapuram Mambalam line and 230kV Mylapore Mylapore_GIS line on load regulation, 230kV/110kV TONDIARPET, 230kV/110kV BASIN_BRIDGE, and 230kV/33kV MYLAPORE_GIS, 230kV/110kV CMRL_CENTRAL, 230kV/33kV TNEB_HQ, 230kV/110kV RAPURAM and 230kV/110kV MYLAPORE were radially fed from 400kV/230kV/110kV MANALI and 230kV NCTPSC St-1. The triggering incident was tripping of 400kV NCTPS ST-2 Manali line. Due to the tripping of 400kV NCTPS St-2 Manali line, 400kV Alamathy Manali line got overloaded (upto 800MW). Subsequently at 21:54:08hrs, there was BN fault in the line due to failure of B-phase line isolator at Alamathy end. Due to the tripping of both 400kV connected Manali lines, 230kV grid connected lines got overloaded and tripped which led to the Complete Outage of 400kV/230kV/110kV MANALI, 400kV/230kV PULIYANTHOPE, 230kV VYSARPADI, 230kV/110kV TONDIARPET, 230kV/110kV BASIN_BRIDGE, 230kV/33kV MYLAPORE_GIS, 230kV/110kV CMRL_CENTRAL, 230kV/33kV TNEB_HQ, 230kV/110kV RAPURAM and 230kV/110kV MYLAPORE. | TANTRANSCO to carry out periodical maintenance of their substation equipment & lines. | TANTRANSCO | cepc:TANTRANSCO: 04/11/2024 18:49:56: Addressed to System Operation wing | Complied | Pending
123/I/10 | Complete Outage of 400kV/230kV/110kV MANALI, 400kV/230kV PULIYANTHOPE, 230kV VYSARPADI, 230kV/110kV TONDIARPET, 230kV/110kV BASIN_BRIDGE, 230kV/33kV MYLAPORE_GIS, 230kV/110kV CMRL_CENTRAL, 230kV/33kV TNEB_HQ, 230kV/110kV RAPURAM and 230kV/110kV MYLAPORE. | 12-09-2024 21:54 | During antecedent conditions, 230kV VYSARPADI was radially fed from 400kV/230kV PULIYANTHOPE and due to outage of 230kV Tharamani Rapuram line, 230kV Tharamani Mylapore line, 230kV Tharamani KITZ line, 230kV Rapuram Mambalam line and 230kV Mylapore Mylapore_GIS line on load regulation, 230kV/110kV TONDIARPET, 230kV/110kV BASIN_BRIDGE, and 230kV/33kV MYLAPORE_GIS, 230kV/110kV CMRL_CENTRAL, 230kV/33kV TNEB_HQ, 230kV/110kV RAPURAM and 230kV/110kV MYLAPORE were radially fed from 400kV/230kV/110kV MANALI and 230kV NCTPSC St-1. The triggering incident was tripping of 400kV NCTPS ST-2 Manali line. Due to the tripping of 400kV NCTPS St-2 Manali line, 400kV Alamathy Manali line got overloaded (upto 800MW). Subsequently at 21:54:08hrs, there was BN fault in the line due to failure of B-phase line isolator at Alamathy end. Due to the tripping of both 400kV connected Manali lines, 230kV grid connected lines got overloaded and tripped which led to the Complete Outage of 400kV/230kV/110kV MANALI, 400kV/230kV PULIYANTHOPE, 230kV VYSARPADI, 230kV/110kV TONDIARPET, 230kV/110kV BASIN_BRIDGE, 230kV/33kV MYLAPORE_GIS, 230kV/110kV CMRL_CENTRAL, 230kV/33kV TNEB_HQ, 230kV/110kV RAPURAM and 230kV/110kV MYLAPORE. | TANTRANSCO to enable A/R in all lines at NCTPS end. | TNPGCL | cepc:TANTRANSCO: 04/11/2024 18:55:17: AR scheme in feeders emanated from from NCTPS .1was implemented but due to wrong operation of AR scheme . The same was disabled . Procurement activity for replacing the panels has been initiated cepc:TANTRANSCO: 06/01/2025 15:43:38: Related to TANGEDCO cepc:TANTRANSCO: 03/02/2025 17:13:13: pending with TNPGCL cepc:TANTRANSCO: 04/03/2025 11:53:58: pending with TNPGCL cepc:TANTRANSCO: 05/04/2025 15:21:52: pending with TNPGCL cepc:TANTRANSCO: 04/06/2025 13:12:45: pending with TNPGCL cepc:TANTRANSCO: 03/07/2025 14:54:48: Pending with TNPGCL cepc:TANTRANSCO: 05/08/2025 13:22:11: pending with TNPGCL cepc:TANTRANSCO: 04/10/2025 12:34:02: Pending with TNPGCL | Pending | Pending
123/I/10 | Complete Outage of 400kV/230kV/110kV MANALI, 400kV/230kV PULIYANTHOPE, 230kV VYSARPADI, 230kV/110kV TONDIARPET, 230kV/110kV BASIN_BRIDGE, 230kV/33kV MYLAPORE_GIS, 230kV/110kV CMRL_CENTRAL, 230kV/33kV TNEB_HQ, 230kV/110kV RAPURAM and 230kV/110kV MYLAPORE. | 12-09-2024 21:54 | During antecedent conditions, 230kV VYSARPADI was radially fed from 400kV/230kV PULIYANTHOPE and due to outage of 230kV Tharamani Rapuram line, 230kV Tharamani Mylapore line, 230kV Tharamani KITZ line, 230kV Rapuram Mambalam line and 230kV Mylapore Mylapore_GIS line on load regulation, 230kV/110kV TONDIARPET, 230kV/110kV BASIN_BRIDGE, and 230kV/33kV MYLAPORE_GIS, 230kV/110kV CMRL_CENTRAL, 230kV/33kV TNEB_HQ, 230kV/110kV RAPURAM and 230kV/110kV MYLAPORE were radially fed from 400kV/230kV/110kV MANALI and 230kV NCTPSC St-1. The triggering incident was tripping of 400kV NCTPS ST-2 Manali line. Due to the tripping of 400kV NCTPS St-2 Manali line, 400kV Alamathy Manali line got overloaded (upto 800MW). Subsequently at 21:54:08hrs, there was BN fault in the line due to failure of B-phase line isolator at Alamathy end. Due to the tripping of both 400kV connected Manali lines, 230kV grid connected lines got overloaded and tripped which led to the Complete Outage of 400kV/230kV/110kV MANALI, 400kV/230kV PULIYANTHOPE, 230kV VYSARPADI, 230kV/110kV TONDIARPET, 230kV/110kV BASIN_BRIDGE, 230kV/33kV MYLAPORE_GIS, 230kV/110kV CMRL_CENTRAL, 230kV/33kV TNEB_HQ, 230kV/110kV RAPURAM and 230kV/110kV MYLAPORE. | TANTRANSCO to furnish the reason for non-operation of PSB of Main-1 relay for 230kV KoratturManali line. | TANTRANSCO | cepc:TANTRANSCO: 04/11/2024 18:56:47: Main.1 relay has to be checked cepc:TANTRANSCO: 06/01/2025 15:42:35: Main.1 relay has to be checked awaiting line clear cepc:TANTRANSCO: 05/04/2025 15:21:52: Awating Line clear. Time line requested upto 30.04.2025 cepc:TANTRANSCO: 04/06/2025 13:31:25: Line clear awaited cepc:TANTRANSCO: 07/08/2025 12:09:26: Main.2 relay is old version Micom P430C.It is proposed replace the relay with spare one cepc:TANTRANSCO: 02/09/2025 13:32:17: Distance relay has to be procured cepc:TANTRANSCO: 04/10/2025 12:34:02: Distance relay has to be procured cepc:TANTRANSCO: 06/11/2025 10:42:00: Distance relay has to be procured cepc:TANTRANSCO: 04/12/2025 13:14:47: Distance relay has to be procured cepc:TANTRANSCO: 05/01/2026 12:57:59: Distance relay has to be procured cepc:TANTRANSCO: 02/02/2026 14:40:41: Distance relay has to be procured cepc:TANTRANSCO: 04/03/2026 16:03:55: Distance relay has to be procured cepc:TANTRANSCO: 30/03/2026 16:34:30: Distance relay has to be replaced with spare one | Pending | Pending
123/I/11 | Complete Outage of 400kV/220kV Tharamani SS of TANTRANSCO | 12-09-2024 23:36 | As per the reports submitted, during antecedent conditions, 230kV Mylapore Tharamani line and 230kV RAPuram Tharamani lines were under outage for load regulation. The triggering incident was YN fault in 230kV Sriperumbudur Tharamani line due to Y phase dropper cut at Tharamani end. and the line tripped. At the same time, 230kV Kalventhapattu Tharamani line tripped on operation of DEF protection only at Tharamani end. Tripping of these two lines resulted in the complete outage of 400kV/230kV/110kV Tharamani GIS and 230kV/110kV Tharamani SS. | TANTRANSCO to ensure to carry out periodical maintenance of their substation equipment & lines | TANTRANSCO | cepc:TANTRANSCO: 04/11/2024 18:48:38: Addressed to System operation wing | Complied | Complied
123/II/4 | Tripping of 400V Bus-2 of 400V/110kV Alamathy SS | 25-08-2024 10:09 | As per the reports submitted, the triggering incident was B-phase CT failure in 400kV/110kV Alamathy ICT-1 causing Bus fault. Immediately, 400kV Bus-2 BBP operated tripping all elements connected to Bus-2. At the same time, the 400kV/110kV Alamathy ICT-6, which is connected through main breakers to both 400kV Alamathy Bus-1 and Bus-2 without a Tie Bay, also tripped. | TANTRANSCO to explore providing TEED protection in the ICT-6 dia by providing an additional CT for ICT-6 | TANTRANSCO | cepc:TANTRANSCO: 04/11/2024 18:48:38: It is being studied due to space constraint cepc:TANTRANSCO: 06/01/2025 15:44:38: Scheme modified on 28.11.2024 to avert unwanted tripping of ICT.6 hence complied | Complied | Complied
123/II/4 | Tripping of 400V Bus-2 of 400V/110kV Alamathy SS | 25-08-2024 10:09 | As per the reports submitted, the triggering incident was B-phase CT failure in 400kV/110kV Alamathy ICT-1 causing Bus fault. Immediately, 400kV Bus-2 BBP operated tripping all elements connected to Bus-2. At the same time, the 400kV/110kV Alamathy ICT-6, which is connected through main breakers to both 400kV Alamathy Bus-1 and Bus-2 without a Tie Bay, also tripped. | TANTRANSCO to replace the failed B-phase CT | TANTRANSCO | cepc:TANTRANSCO: 04/11/2024 18:50:54: CT replaced on 16.09.2024 cepc:TANTRANSCO: 06/01/2025 15:43:38: complied cepc:TANTRANSCO: 03/02/2025 17:09:45: CT replaced on 16.09.2024 . Complied | Complied | Complied
123/III/6 | Tripping of Vallur U2 during fault in 400KV-NCTPS_STAGE_II-SUNGAVARACHATRAM-2 line | 02-09-2024 22:20 | As per the reports submitted, the triggering incident is the YB fault in 400kV NCTPS-SV Chatram-2 near to NCTPS at location 4 & 5 where in hotline OPGW stringing rope was cut and caused Y & B Phase to Phase fault which sensed in Z1 at NCTPS and Z2 with carrier at SV Chatram end and 3ph tripped at both ends. During this fault Vallur GT-2 tripped on under voltage protection. This led to a generation loss of around 500 MW. | TANTRANSCO to review the fault distance measured by Main-I and Main-2 of 400kV NCTPS-SV Chatram Line-2 | TANTRANSCO | cepc:TANTRANSCO: 04/11/2024 18:48:38: CT secondary circuit has to be checked. cepc:TANTRANSCO: 06/01/2025 15:45:21: Line clear awaited cepc:TANTRANSCO: 04/03/2025 12:16:56: Line clear awaited cepc:TANTRANSCO: 05/04/2025 15:12:49: Line clear awaited cepc:TANTRANSCO: 04/06/2025 13:44:34: Checked & Found in order cepc:TANTRANSCO: 03/07/2025 14:40:38: Complied | Complied | Complied
123/III/9 | Multiple trippings at NCTPS | 06-09-2024 03:10 | As per the reports submitted, the triggering incident was RY fault in the Alamathy-NCTPS_Stage_II line -1 as between location 2 and 3 from NCTPS-2 end OPGW pilot wire cut and fell down on Alamathy feeder. At both ends the tripped on operation of Zone-1 distance protection. During the same time of fault, 400kV NCTPS_Stage_II-Sungavarachathram line-1 tripped only at NCTPS end on operation of Zone-1 distance protection for RY fault. At Sugavarachathram end the line was holding as permissive Carrier received in Channel2. Zone2 & Zone3 pickup and got reset 30ms before carrier receive. | TANTRANSCO to check the reason for non-sensing the fault by Main-II relay at Sunguvarchatiram for 400kV-NCTPS_Stage_II-Sungavarachatram line 1. | TANTRANSCO | cepc:TANTRANSCO: 04/11/2024 18:48:38: Restrain of Micom P543 relay is found in order. Micom P442 relay , | Complied | Complied
123/III/14 | Multiple Trippings at 400kV/220kV Hosur PG | 16-09-2024 13:25 | As per the reports submitted, the triggering incident was YB-N fault in 400kV Hosur Salem Lne-2. At the same time, 230kV Hosur Gurubarapalli line tripped at Gurubarapalli end. | TANTRANSCO to verify the configuration of other elements at Gurubarapalli end. Also to check for other stations | TANTRANSCO | cepc:TANTRANSCO: 04/11/2024 18:38:31: Verified & found in order cepc:TANTRANSCO: 06/01/2025 15:45:21: complied cepc:TANTRANSCO: 03/02/2025 17:09:14: verified & found in order | Complied | Complied
125/II/1 | Line Outage of 230kV Regen_Anaikadavu and Tripping of Bus 2 at 230kV Regen_Anaikadavu SS | 09-10-2024 23:45 | As per the preliminary information received, the triggering incident was R-N fault in 230kV Anaikadavu Regen line and the line tripped. Tripping of the only connected line led to complete outage of 230kV Regen_ Anaikadavu Wind Pooling station | TANTRANSCO /TNSLDC to comply with IEGC Regulations and report the event as per the timeline specified in the Regulations | TANTRANSCO | cepc:TANTRANSCO: 02/01/2025 14:49:42: Addressed to TNSLDC | Complied | Pending
125/II/1 | Line Outage of 230kV Regen_Anaikadavu and Tripping of Bus 2 at 230kV Regen_Anaikadavu SS | 09-10-2024 23:45 | As per the preliminary information received, the triggering incident was R-N fault in 230kV Anaikadavu Regen line and the line tripped. Tripping of the only connected line led to complete outage of 230kV Regen_ Anaikadavu Wind Pooling station | TANTRANSCO to expedite providing LDP for 230kV Regen- Anaikadavu line | TANTRANSCO | cepc:TANTRANSCO: 02/01/2025 14:49:42: Addressed to M/s. regen on 21.11.2024 & will be complied cepc:TANTRANSCO: 03/02/2025 17:13:13: will be complied cepc:TANTRANSCO: 04/03/2025 11:53:58: Addressed to M/s. Regen to provide LDP. cepc:TANTRANSCO: 05/04/2025 15:21:52: Addressed to M/s. Regen to provide LDP relay cepc:TANTRANSCO: 04/06/2025 13:15:32: M/s.. Regen has to procure the LDP relays. cepc:TANTRANSCO: 03/07/2025 14:57:33: M/s. Regen has to procure the LDP relay. cepc:TANTRANSCO: 05/08/2025 13:10:27: Ltter adderssed to M/s. Regen for provision of OPGW and LDP relay cepc:TANTRANSCO: 02/09/2025 13:46:28: Addressed to M/s. Regen for provision of OPGW & LDP cepc:TANTRANSCO: 03/10/2025 17:02:45: Letter addressed to M/s. Regen. cepc:TANTRANSCO: 06/11/2025 10:42:00: Addressed to M/s. Regen cepc:TANTRANSCO: 04/12/2025 13:14:47: Addressed to M/s Regen cepc:TANTRANSCO: 05/01/2026 12:57:59: Reminder letter sent on 11.12.2025 cepc:TANTRANSCO: 02/02/2026 14:40:41: procurement LDP along with OPGW by M/s. Regen under progress cepc:TANTRANSCO: 04/03/2026 16:03:55: Procurement of LDP with OPGW by M/s. regen under progress cepc:TANTRANSCO: 30/03/2026 16:34:30: LDP procurement under progress | Pending | Pending
126/I/7 | Complete Outage of 400kV/230kV/110kV Tharamani SS of TANTRANSCO | 13-12-2024 15:06 | 230kV Tharamani Bus-2 was not in service during antecedent conditions. As per the reports submitted, the triggering incident was tripping of 230kV Bus-1 BBP on maloperation. Tipping of 230kV Tharamani Bus-1 led to complete outage of 400kV/230kV Tharamani SS. | TANTRANSCO to follow SOP and furnish the revised SOP to SRPC & SRLDC. | TANTRANSCO | cepc:TANTRANSCO: 03/02/2025 16:16:36: Addressed to System Operation wing cepc:TANTRANSCO: 04/03/2025 12:16:56: Addressed to System Operation wing cepc:TANTRANSCO: 05/04/2025 15:12:49: Addressed to System operation wing cepc:TANTRANSCO: 04/06/2025 13:46:23: Addressed to System Operation wing cepc:TANTRANSCO: 01/07/2025 16:07:34: Addressed to System operation wing cepc:TANTRANSCO: 06/08/2025 16:25:17: Addressed to System operation wing | Complied | Complied
126/III/4 | 400KV/230KV PULIYANTHOPE-ICT-3 | 27-11-2024 05:23 | As per the reports furnished, got tripped on operation of PRV protection due to ingress of moisture during rain. Tripping is not in order | TANTRANSCO to explore the feasibility of PGCIL-adopted logic for PRV. | TANTRANSCO | cepc:TANTRANSCO: 03/02/2025 16:16:36: PGCIL logic communicated & will be implemented after ensuring feasibility cepc:TANTRANSCO: 03/02/2025 17:02:30: It was found that the switches were defective and was the primary reason for the spurious trippings. Hence action was initiated to replace the PRV Switches in coordination with the EPC Contractor and the OEM of the Transformer i.e. M/s Toshiba. As a result, at Pulianthope 400kV GIS SS, 5 No.s of defective PRV Switches were replaced in ICT-1 on 10-01-2025 and 4 No.s were replaced on 24-01-2025. The performance of the Switches is under observation. It has been programmed to replace the rest of the PRV Switches on 13-02-2025 in ICT-2 . One PRV Switch will be replaced in ICT-3 as well. cepc:TANTRANSCO: 03/03/2025 17:25:42: PRV relay replaced on 24.01.2025. Complied | Complied | Complied
126/III/6 | 400KV/230KV PULIYANTHOPE-ICT-2 | 30-11-2024 10:10 | As per the reports submitted, the 400kV/230kV Puliyanthope ICT-2 tripped on operation of Y Phase OLTC PRV trip due to moisture ingress in the Y phase OLTC PRV Termination box during rain.Tripping is not in order. | TANTRANSCO to explore the feasibility of PGCIL-adopted logic for PRV. | TANTRANSCO | cepc:TANTRANSCO: 03/02/2025 16:16:36: PGCIL logic communicated & will be implemented after ensuring feasibility cepc:TANTRANSCO: 03/02/2025 17:02:30: It was found that the switches were defective and was the primary reason for the spurious trippings. Hence action was initiated to replace the PRV Switches in coordination with the EPC Contractor and the OEM of the Transformer i.e. M/s Toshiba. As a result, at Pulianthope 400kV GIS SS, 5 No.s of defective PRV Switches were replaced in ICT-1 on 10-01-2025 and 4 No.s were replaced on 24-01-2025. The performance of the Switches is under observation. It has been programmed to replace the rest of the PRV Switches on 13-02-2025 in ICT-2 . One PRV Switch will be replaced in ICT-3 as well. cepc:TANTRANSCO: 03/03/2025 17:26:36: Line clear awaited. Time line requested upto 31.03.2025 cepc:TANTRANSCO: 05/04/2025 15:24:48: PRV switch has to be replaced . Time line requested upto 30.04.2025 cepc:TANTRANSCO: 04/06/2025 13:10:35: As field condition PGCIL logic could not be oimplemented at Pulianthope due to derth of relay inputs. However remedial action is studied with OEM. As recommended by OEM, the PRV switch has to be replaced at ICT.2 | Complied | Complied
126/III/12 | 400KV/230KV PULIYANTHOPE-ICT-3 | 12-12-2024 14:31 | As per the reports furnished, got tripped on operation of PRV protection due to ingress of moisture during rain. Tripping is not in order. | TANTRANSCO to explore the feasibility of PGCIL-adopted logic for PRV. | TANTRANSCO | cepc:TANTRANSCO: 03/02/2025 16:16:36: PGCIL logic communicated & will be implemented after ensuring feasibility cepc:TANTRANSCO: 03/02/2025 17:02:30: It was found that the switches were defective and was the primary reason for the spurious trippings. Hence action was initiated to replace the PRV Switches in coordination with the EPC Contractor and the OEM of the Transformer i.e. M/s Toshiba. As a result, at Pulianthope 400kV GIS SS, 5 No.s of defective PRV Switches were replaced in ICT-1 on 10-01-2025 and 4 No.s were replaced on 24-01-2025. The performance of the Switches is under observation. It has been programmed to replace the rest of the PRV Switches on 13-02-2025 in ICT-2 . One PRV Switch will be replaced in ICT-3 as well. cepc:TANTRANSCO: 03/03/2025 17:25:42: PRV relay replaced on 24.01.2025. Complied | Complied | Complied
127/III/13 | 400KV/230KV SUNGAVARACHATRAM-ICT-1 | 11-01-2025 18:54 | As per the reports submitted, 400/230kV Sungavarachatram ICT-1 LV side breaker tripped without indication. Tripping needs review. | TANTRANSCO to check the panel wiring healthiness of all Panels at Sunguvarchatram SS | TANTRANSCO | cepc:TANTRANSCO: 03/03/2025 17:25:42: work under progress .Time line requested on 31.03.2025 cepc:TANTRANSCO: 05/04/2025 15:24:48: Checked & found intact | Complied | Complied
128/III/5 | 220KV-CHITTOOR_AP-THIRUVALAM_TN-1 | 28-01-2025 13:23 | 220kV Chittoor-Thiruvalam line is idle charged from Thiruvalam end. As per the reports submitted, the triggering incident is the R-N fault in the line. The fault was sensed in Z1 at Thiruvalam end on 13:23:39 Hrs and AR operated and was successful. However, within reclaim time another R-N fault was sensed at 13:23:53 Hrs in Z1 and AR operated and ToR. This led to the 3ph tripping at Thiruvalam end. | 1.TANTRANSCO to enable AR in distance relay and set reclaim time as 25 sec | TANTRANSCO | cepc:TANTRANSCO: 05/04/2025 15:07:05: reclaim time revised to 25 sec on 17.03.2025 | Complied | Complied
128/III/7 | 400KV-ALAMATHY-TIRUVALAM_TN-1 | 30-01-2025 16:13 | As per the reports submitted, during retrofitting of the static LBB relay in the tie bay of Thiruvalam Line-1 & 2 at Alamathy end, the tripping was extended to main bay of Thiruvalam line-1 & DT extended to the remote end due to simulation of contact through software by the personnel. This led to the tripping of the line 400KV-ALAMATHY-TIRUVALAM_TN-1 at Alamathy end and DT was extended to TIRUVALAM_TN and 3ph tripped at TIRUVALAM_TN end. | 1.TANTRANSCO and PGCIL SR-II to follow proper SOP and avoid such incidents | TANTRANSCO | cepc:TANTRANSCO: 05/04/2025 15:05:50: Will be ensured | Complied | Complied
128/III/9 | 400KV/110KV KAMUDHI-ICT-3 | 02-02-2025 12:07 | As per the reports submitted, 400/110kV Kamudhi ICT-3 tripped due to fault in 110kV line. Tripping is not in order. | 1.TANTRANSCO to check and review the REF settings of other ICTs connected at Kamudhi SS 2.TANTRANSCO to rectify the time sync issue at Kamudhi SS. | TANTRANSCO | cepc:TANTRANSCO: 05/04/2025 15:05:01: Stabilising resistance of REF protection was revised from 500ohms to 900 ohms on 02-02-2025 During the incident SNTP failure was observed the same was attended on 07.02.2025 | Complied | Complied
128/IV/2 | 400KV-ALAMATHY-MANALI-1 | 23-01-2025 07:51 | As per the reports submitted, the triggering incident was RN fault in the line. At both ends the line tripped on operation of Zone-1 distance protection. A/R did not get operated and the line tripped on 3-phase. Non-operation of A/R needs to be reviewed. | 1.TANTRANSCO to review the reason for the non-operation of A/R and furnish the detailed analysis of the event | TANTRANSCO | cepc:TANTRANSCO: 05/04/2025 15:03:15: Flex logic Modified ie impedence start of phases are included in the trip logic & transplay the DR found OK | Complied | Complied
128/IV/06 | 400KV-ALAMATHY-MANALI-1 | 04-02-2025 05:34 | As per the reports submitted, the triggering incident was BN fault in the line. At Alamathy end, the line tripped on operation of Zone-1 distance protection. A/R operated but again the line tripped due to fault within the reclaim time. At Manali end the line tripped on operation of Zone-1 distance protection. A/R did not get operated and the line tripped on 3-phase. Tripping needs review. | 1.TANTRANSCO to review the reason for the non-operation of A/R and furnish a detailed analysis of the event. | TANTRANSCO | cepc:TANTRANSCO: 05/04/2025 15:02:20: Flex logic Modified ie.impedence start of phases are included in the trip logic & transplay the DR found OK | Complied | Complied
128/IV/7 | 765KV-NCPS-NCTPS STG3-2 | 11-02-2025 00:47 | As per the reports submitted, the triggering incident was RN fault in the line due to earth wire snapped and fell over the R phase. At both ends the line tripped on operation of Differential protection. A/R did not get operated as 86 Lock Out relay operated, and 3 poles were opened. Tripping needs review. | 1.TANTRANSCO to review the reason for the non-operation of A/R and furnish a detailed analysis of the event | TANTRANSCO | cepc:TANTRANSCO: 05/04/2025 15:00:58: Due to subsequent fault sensed by NR PCS 931 relay, Lockout trip initiated at NCPS end At 13msec condition for stage.1 was met out hence bias.1 operated At 33msec condition for stage.2 was met out hence bias.2 operated Detailed report furnished on 03.03.2025 & 28.03.2025 | Complied | Complied
128/IV/10 | 400KV-PUDUCHERRY-SUNGAVARACHATRAM-1 | 16-02-2025 11:57 | As per the reports submitted, the triggering incident was BN fault in the line. At Puducherry end the line tripped on operation of Zone-2, carrier-aided, distance protection. A/R operated successfully and the line was holding. At Sungavarachatram end, the line tripped on operation of Zone-1 distance protection. A/R did not get operated and the line tripped on 3-phase. Tripping needs review. | 1.TANTRANSCO to review the reason for the non-operation of A/R and furnish a detailed analysis of the event. | TANTRANSCO | cepc:TANTRANSCO: 05/04/2025 14:52:55: As recommended by OEM ( M/s. GE) , flex logic has to be modified.Line clear awaited . Time line requested upto 30.04.2025 cepc:TANTRANSCO: 04/06/2025 13:06:36: Compiled. As per OEM recommendation, The trip logic for Zone 1Phase fault have been modified in M1(D60) & M2 (D60) relays on 23.04.2025. | Complied | Complied
128/IV/11 | 400KV-PUDUCHERRY-SUNGAVARACHATRAM-1 | 16-02-2025 13:33 | As per the reports submitted, the triggering incident was BN fault in the line. At Pondy end, the line tripped on operation of Zone-2, carrier aided, distance protection. A/R operated but due to persisting fault, Z2 started and line tripped on Zone-2-time trip, due to non receipt of Carrier signal from the remote end. At Sungavarachatram end the line tripped on operation of Zone-1 distance protection. A/R did not get operated and the line tripped on 3-phase. Tripping needs review. | 1.TANTRANSCO to review the reason for the non-operation of A/R and furnish a detailed analysis of the event | TANTRANSCO | cepc:TANTRANSCO: 05/04/2025 14:52:55: As recommended by OEM ( M/s. GE) , flex logic has to be modified.Line clear awaited . Time line requested upto 30.04.2025 cepc:TANTRANSCO: 04/06/2025 13:47:44: "As per OEM recommendation, The trip logic for Zone 1Phase fault have been modified in M1(D60) & M2 (D60) relays on 23.04.2025. Complied cepc:TANTRANSCO: 01/07/2025 16:07:34: complied on 23.04.2025 | Complied | Complied
129/IV/1 | 400KV-ALAMATHY SUNGAVARACHATRAM-2 | 17-01-2025 12:20 | As per the reports submitted, the triggering incident was RN fault in the line. At both ends the line tripped on operation of Zone-1 distance protection. At Almathy end, A/R operated but again the line tripped due to persistent fault. At SV Chatram end, R pole didnt reclose. Suspected PD operation. Non-operation of A/R at SV Chatram end needs review. | TANTRANSCO to resolve the issue and furnish the report. | TANTRANSCO | cepc:TANTRANSCO: 04/06/2025 16:57:47: Breaker overhauled on 07.03.2025 cepc:TANTRANSCO: 01/07/2025 16:04:57: Complied cepc:TANTRANSCO: 01/07/2025 16:06:38: Complied | Complied | Complied
129/VI/22 | 400KV-ALAMATHY-NCTPS_STAGE_II-1 | 11-03-2025 15:23 | As per the reports submitted, the triggering incident was BN fault in the line. At both ends, the line tripped on operation of Zone-1 distance protection. A/R operated at both ends but again the line tripped due to fault within the reclaim time. Operation of AR after the tripping of the line at the NCTPS end needs review. | TANTRANSCO to expedite to replace the Main-II relay. | TANTRANSCO | cepc:TANTRANSCO: 07/05/2025 13:38:15: Distance relay has to be procured cepc:TANTRANSCO: 04/06/2025 13:06:36: Distance relay has to be procured cepc:TANTRANSCO: 03/07/2025 14:58:14: Relay allotted . Line clear awaited. Time line requested upto 31.08.2025 cepc:TANTRANSCO: 05/08/2025 13:08:57: Relay alloted .Will be replaced on availing Line clear. cepc:TANTRANSCO: 02/09/2025 13:47:43: Relay allotted. Time line requested upto 31.12.2025 cepc:TANTRANSCO: 03/10/2025 17:02:45: Time line requested upto 31.12.2025 cepc:TANTRANSCO: 06/11/2025 10:42:00: Time line requested upto 31.12.2025 cepc:TANTRANSCO: 04/12/2025 13:14:47: Time line requested upto 31.12.2025 cepc:TANTRANSCO: 05/01/2026 12:57:59: Line Clear awaited cepc:TANTRANSCO: 02/02/2026 14:40:41: Line clear awaited cepc:TANTRANSCO: 04/03/2026 16:03:55: Line clear awaited cepc:TANTRANSCO: 30/03/2026 16:34:30: Line clear awaited | Pending | Pending
130/I/6 | Complete Outage of 230kV/110kV Veerapuram SS | 19-03-2025 14:40 | During antecedent conditions, due to outage of 230kV Veerapuram SPKoil line and 230kV Veerapuram Cuddalore line 1& 2 on power regulation, 230kV/110kV Veerapuram SS was radially fed from 230kV Kalvindapattu Veerapuram line and 110kV Veerapuram SP Koil line-2. The triggering incident was RN fault in 230kV Kalvindapattu Veerapuram line and the line tripped. Subsequently, 110kV Veerapuram SP Koil line-2 tripped on overloadeing. Tripping of the only connected line resulted in complete loss of supply to 230kV/110kV Veerapuram SS. | TANTRANSCO to ensure the regular monitoring of Jumper and switchyard equipments through thermovision camera. | TANTRANSCO | cepc:TANTRANSCO: 04/06/2025 13:08:29: Informed to System Operation wing for remedial measure | Complied | Complied
130/I/14 | Complete Outage of 230kV/110kV Veerapuram SS of TANTRANSCO | 11-04-2025 23:38 | During antecedent conditions, 230kV Veerapuram, SS was being radially fed through 230kV Veerapuram Kalivandapattu line and 110kV Veerapuram SP Koil line. As per the reports submitted, the triggering incident was B-phase jumper in 230kV Veerapuram Kalivandapattu line. At Veerapuram end, broken conductor alarm was observed. And DEF protection operated. Tripping of the 230kV Veerapuram Kalivandapattu line led to over loading and tripping of 110kV Veerapuram SP Koil line on over load. Tripping of both lines led to complete outage of 230kV/110kV Veerapuram SS. | 1.TANTRANSCO to analyze and submit the reason for DEF operation at Veerapuram SS. 2.TANTRANSCO to ensure regular monitoring of Jumpers and switch yard equipments through Thermo vision camera. | TANTRANSCO | cepc:TANTRANSCO: 04/06/2025 13:35:05: 1 Detailed report will be submitted 2. Addressed to System Operation wing cepc:TANTRANSCO: 03/07/2025 14:54:48: Detailed report will be submitted Addressed to system operation wing cepc:TANTRANSCO: 07/08/2025 12:09:26: detailed report will be submitted cepc:TANTRANSCO: 02/09/2025 13:32:17: Complied. 1. report sent on 09.09.2025 2.Addressed to System operation wing | Complied | Complied
130/III/15 | Multiple trippings at Myvadi | 10-04-2025 15:39 | As per the reports submitted triggering incident was slow YB-N fault in 220kV Myvadi Udumalpet Line-2. During this event, the voltages in faulty phases has gone high due to improper earthing of neutral. So, the fault was initially sensed in zone-2 for around 370ms. At the same time, 230kV Myvadi - Othakalamndapam tripped on zone-4 protection at Myvadi end and zone-2 protection at Othakalamndapam end. 230kV Mywadi - Kurkathi tripped on zone-4 protection at Myvadi end and zone-2 protection at Kurkathi end. 230kV Mywadi Ponnapuram line-2 tripped only at Myvadi end on zone-4 protection. 400kV/230kV Udumalpet ICT-1 & 2 tripped after around 180ms on suspected tripping at Mywadi end. Subsequently, 400kV/230kV Udumalpet ICT-3 tripped on IV side high set earth fault protection. | 1.TANTRANSCO to inspect the relay cabling and conduct relay testing to verify proper operation of ICT 1&2 relays. 2.TANTRANSCO to review and verify the integrity of the Myvadi station earthing system. | TANTRANSCO | cepc:TANTRANSCO: 04/06/2025 12:56:38: Informed to System Operation wing for suitable remedial measure. cepc:TANTRANSCO: 03/07/2025 14:59:51: informed to system operation wing | Complied | Complied
130/IV/12 | 400KVKARAIKUDI-KAYATHAR- 2 | 06-04-2025 23:00 | As per the reports submitted, the triggering incident was B-N fault in the line. At both ends, the fault was sensed in zone-1. A/R operated and the line tripped on persistent fault. However, Difference in A/R dead time between both ends needs review. | TANTRANSCO to check AR dead time and review the Non operation of AR. | TANTRANSCO | cepc:TANTRANSCO: 04/10/2025 12:34:02: The AR scheme is enabled in external relay. dead time is set as 1000msec but relay issued reclose command after 1000msec. Hence external relay timer setting reduced to 900msec & observation cepc:TANTRANSCO: 05/01/2026 12:57:59: Under observation cepc:TANTRANSCO: 02/02/2026 14:40:41: Under observation cepc:TANTRANSCO: 30/03/2026 16:34:30: Under observation | Pending | Pending
130/VI/12 | 400KV-ALAMATHY-TIRUVALAM_TN-1 | 27-03-2025 13:55 | DR Time Synchronization issue at ALAMATHY - 400KV | TANTRANSCO to resolve the time synchronization issue | TANTRANSCO | cepc:TANTRANSCO: 04/06/2025 12:56:38: Distance relay is old version . This has to be replaced. cepc:TANTRANSCO: 03/07/2025 14:59:51: Relay allotted . Line clear awaited. Time line requested upto 31.08.2025 cepc:TANTRANSCO: 05/08/2025 13:08:57: Relay alloted .Will be replaced on availing Line clear. cepc:TANTRANSCO: 02/09/2025 13:48:09: relay alloted. Time line requested upto 31.12.2025 cepc:TANTRANSCO: 03/10/2025 17:02:45: Time line requested upto 31.12.2025 cepc:TANTRANSCO: 06/11/2025 10:42:00: Time line requested upto 31.12.2025 cepc:TANTRANSCO: 04/12/2025 13:14:47: Time line requested upto 31.12.2025 cepc:TANTRANSCO: 05/01/2026 12:57:59: Line clear awaited cepc:TANTRANSCO: 02/02/2026 14:40:41: Line clear awaited cepc:TANTRANSCO: 04/03/2026 16:03:55: Line clear awaited cepc:TANTRANSCO: 30/03/2026 16:34:30: Line clear awaited | Pending | Pending
130/VI/20 | 400KV-NCTPS_STAGE_II-VALLUR-2 | 11-04-2025 04:15 | DR Time Synchronization issue at NCTPS_STAGE_II - 400KV | TANGEDCO to resolve the time synchronization issue | TNPGCL | cepc:TANTRANSCO: 04/10/2025 12:34:02: Related to TNPGCL aeswydmrtnctps2:TNPGCL: 06/03/2026 15:28:53: NEW GPS CLOCK HAS BEEN COMMISSIONED ON 04.11.2025 AND SUCCESSFULLY SYNCHRONIZED WITH EXISTING SCADA SYSTEM(SERVERS AND RELAYS). NOW ALL RELAYS ARE SYNCHRONIZED WITH GPS CLOCK. | Complied | Complied
131/I/5 | Complete Outage of 230kV Vinnamnagalam and 230kV Tirupatur | 23-04-2025 12:45 | 230kV Thirupathur and 230kV Vinnamangalam stations are connected via Hosur and Singarpet via 230kV Hosur-Thirupathur and 230kV Singarpet-Vinnamangalam. Initially, due to the R-N fault in 230kV Hosur-Thirupathur tripped. Later due to B-N fault 230kV Singarpet-Vinnamangalam led to the complete outage of 230kV Thirupathur and 230kV Vinnamangalam stations | TANTRANSCO to check the healthiness of the Y and B phase limbs at Vinnamangalam SS. | TANTRANSCO | cepc:TANTRANSCO: 03/07/2025 14:36:24: breaker overhauled on 25.04.2025 . Complied | Complied | Complied
131/I/5 | Complete Outage of 230kV Vinnamnagalam and 230kV Tirupatur | 23-04-2025 12:45 | 230kV Thirupathur and 230kV Vinnamangalam stations are connected via Hosur and Singarpet via 230kV Hosur-Thirupathur and 230kV Singarpet-Vinnamangalam. Initially, due to the R-N fault in 230kV Hosur-Thirupathur tripped. Later due to B-N fault 230kV Singarpet-Vinnamangalam led to the complete outage of 230kV Thirupathur and 230kV Vinnamangalam stations | TANTRANSCO to implement the double bus scheme with bus coupler at Thirupathur SS and Vinnamangalam SS. | TANTRANSCO | cepc:TANTRANSCO: 05/08/2025 13:07:41: Thirupathur 230kVSS is having Double bus arrangments. Hence complied Vinnamangalam 230kVSS is having only 2 sources.. Hence operated as single bus for load management. | Complied | Complied
132/II/1 | Tripping of 230kV Bus-1 and Bus-2 of 230kV/110kV Gobi SS | 23-05-2025 13:52 | Triggering incident was failure of B-phase CT of 230kV Bus Coupler at 230kV/110kV Gobi SS. BBP protection of 230kV Bus-1 and Bus-2 operated resulting in the tripping of all connected elements at 230kV/110kV Gobi SS. 110kV Bus was intact during the event. | TANTRANSCO to report CT failure report to CEA | TANTRANSCO | cepc:TANTRANSCO: 07/08/2025 12:09:26: Addressed to System operation wing to furnish the equipment failure report to CEA in prescribed format cepc:TANTRANSCO: 02/09/2025 13:35:24: Addressed to System Operation wing to furnish the equipment failure report to CEA in prescribed format cepc:TANTRANSCO: 04/10/2025 12:34:02: Addressed to System Operation wing cepc:TANTRANSCO: 06/11/2025 10:42:00: Addressed to System Operation wing cepc:TANTRANSCO: 04/12/2025 13:14:47: Addressed to System Operation wing cepc:TANTRANSCO: 05/01/2026 12:57:59: Reminder Letter sent on 09.12.2025 cepc:TANTRANSCO: 02/02/2026 14:40:41: System Operation wing has to furnish the report reminder letter sent on 09.12.2025. cepc:TANTRANSCO: 04/03/2026 16:03:55: Addressed to System operation wing cepc:TANTRANSCO: 30/03/2026 16:34:30: Addressed to System Operation wing | Pending | Pending
132/II/3 | Tripping of 230kV Bus-1 and 230kV Bus-2 of 230kV/110V Kayathar SS of TANTRANSCO | 31-05-2025 06:24 | During antecedent conditions, all 230kV elements were connected to 230kV Bus-1 of 230kV/110kV Kayatha SS. As per the reports submitted, the triggering incident was R-Phase Bus side jumper cut in 230kV Kayathar Kinnimangalam Line. Immdediately, 230kV Bus-1 BBP operated and all elements connected to 230kV Bus-1 tripped. 110kV side was intact during the event | To rectify the Bus selection isolator issue and to verify its correct operation and should enable double bus operation | TANTRANSCO | cepc:TANTRANSCO: 06/08/2025 16:18:56: Informed to System Operation wing for implementing the double bus operation | Complied | Complied
132/III/31 | Tripping of 400KV-ANAIKADAVU-THAPPUKUNDU-2 and loss of RE generation during the event. | 03-06-2025 10:37 | As per the reports submitted, the triggering incident was B-G fault in the line during patroling it was observed that a Juliflora tree has grown upto the arcing distance at loc 87. The fault distance from Anaikadavu end was 12.7kms and from Thappukudu end was 32.6kms. At Anaikadavu end, the fault was sensed in Z1, A/R operated and tripped due to subsequent fault within reclaim time, 3 phase trip initiated. At Thappukundu end, the fault was sensed Z3 and 3 pole tripped. During the event RE generation loss was observed due to suspected LVRT non-compliance and needs review. | As per Regulations, LVRT should be sustained till 0.15 p.u and TANTRANSCO to ensure the compliance by RE generators | TANTRANSCO | cepc:TANTRANSCO: 07/08/2025 12:09:26: Addressed to RE generators to furnish details on or before 25.08.2025 cepc:TANTRANSCO: 02/09/2025 13:35:24: Addressed to RE generators reply awaited cepc:TANTRANSCO: 04/10/2025 12:34:02: Addressed to RE Generators & awaiting reply cepc:TANTRANSCO: 06/11/2025 10:42:00: Addressed to RE generators cepc:TANTRANSCO: 04/12/2025 13:14:47: Informed to TNGECL cepc:TANTRANSCO: 05/01/2026 12:57:59: Informed to TNGECL cepc:TANTRANSCO: 02/02/2026 14:40:41: Informed to TNGECL cepc:TANTRANSCO: 04/03/2026 16:03:55: Informed to TNGECL cepc:TANTRANSCO: 30/03/2026 16:34:30: Informed to TNGECL | Pending | Pending
132/III/31 | Tripping of 400KV-ANAIKADAVU-THAPPUKUNDU-2 and loss of RE generation during the event. | 03-06-2025 10:37 | As per the reports submitted, the triggering incident was B-G fault in the line during patroling it was observed that a Juliflora tree has grown upto the arcing distance at loc 87. The fault distance from Anaikadavu end was 12.7kms and from Thappukudu end was 32.6kms. At Anaikadavu end, the fault was sensed in Z1, A/R operated and tripped due to subsequent fault within reclaim time, 3 phase trip initiated. At Thappukundu end, the fault was sensed Z3 and 3 pole tripped. During the event RE generation loss was observed due to suspected LVRT non-compliance and needs review. | TANTRANSCO to furnish the reasons for LVRT operations and settings of LVRT. | TANTRANSCO | cepc:TANTRANSCO: 07/08/2025 12:09:26: Addressed to RE generators to furnish details on or before 25.08.2025 cepc:TANTRANSCO: 02/09/2025 13:35:24: Addressed to RE generators reply awaited cepc:TANTRANSCO: 04/10/2025 12:34:02: Addressed to RE Generators & awaiting reply cepc:TANTRANSCO: 06/11/2025 10:42:00: Addressed to RE generators cepc:TANTRANSCO: 04/12/2025 13:14:47: Addressed to RE generators cepc:TANTRANSCO: 05/01/2026 12:57:59: Reminder letter sent on 09.12.2025 cepc:TANTRANSCO: 02/02/2026 14:40:41: Reminder letter sent to concerned RE developer . Reply awaited cepc:TANTRANSCO: 04/03/2026 16:03:55: Reminder letter sent to RE devloper cepc:TANTRANSCO: 30/03/2026 16:34:30: reminder letter sent to RE developer. | Pending | Pending
134/VI/7 | 400KV-NCTPS_STAGE_II-SUNGAVARACHATRAM-1 | 08-08-2025 02:10 | NCTPS_STAGE_II - 400KV | TANTRANSCO to furnish detailed report on DR time sync issue at NCTPS 400kV SS. | TANTRANSCO | cepc:TANTRANSCO: 03/10/2025 17:02:45: related to TNPGCL cepc:TANTRANSCO: 06/11/2025 10:42:00: related to TNPGCL cepc:TANTRANSCO: 04/12/2025 13:14:47: related to TNPGCL cepc:TANTRANSCO: 05/01/2026 12:57:59: Pending With TNPGCL cepc:TANTRANSCO: 02/02/2026 14:40:41: related to TNPGCL cepc:TANTRANSCO: 04/03/2026 16:03:55: related to TNPGCL aeswydmrtnctps2:TNPGCL: 20/03/2026 15:41:09: NEW GPS CLOCK HAS BEEN COMMISSIONED ON 04.11.2025 AND SUCCESSFULLY SYNCHRONIZED WITH EXISTING SCADA SYSTEM(SERVERS AND RELAYS). NOW ALL RELAYS ARE SYNCHRONIZED WITH GPS CLOCK. | Pending | Pending
135/I/10 | Complete outage of 230kV Muttur Auto SS of TANTRANSCO and 220kV Bus-2 of 220kV Yerrandahalli SS of KPTCL | 17-09-2025 09:22 | During antecedent conditions, all 230kV elements were connected to 230kV Bus-1 at 230kV Mettur Auto SSAs per the reports submitted, the triggering incident was RY fault 110kV Bus of 220kV Mettur SS. 110kV BBP was disabled at Mettur SS which subsequently led to overloading of Auto transformers and 230kV Mettur connected lines. This caused a RY fault in 230kV Bus. Immediately, 230kV Bus-1 BBP operated and all elements connected to the bus tripped. This led to complete outage of 230kV Muttur Auto SS. During the 110kV fault, 230kV Hosur Hosur_PG line-1 got over loaded causing SPS designed for over loading of 230kV Hosur Hosur_PG lines tripping 220kV Yerrandahalli Hosur line. Since, 220kV Yerrandahalli Hosur line was radially feeding 220kV Yerrandahalli Bus-2, tripping of the line led to loss of power supply to 220kV Yerrandahalli Bus-2 | TANTRANSCO to check the polarities of all the CTs at Mettur SS. | TANTRANSCO | cepc:TANTRANSCO: 06/11/2025 10:42:00: will be complied cepc:TANTRANSCO: 04/12/2025 13:14:47: will be complied awaiting. cepc:TANTRANSCO: 05/01/2026 12:57:59: All CT polarities were checked and Found OK. Further 110kV BBP also commissioned on 15.10.2025 with two zone operation at 110kV side cepc:TANTRANSCO: 02/02/2026 14:40:41: Complied cepc:TANTRANSCO: 04/03/2026 16:03:55: Complied | Complied | Complied
135/II/3 | Tripping of 230kV Bus-1 , 230kV Bus-2, 110kV Bus-1 and 110kV Bus-2 of 400kV Vellalaviduthi SS of TANTRANSCO | 30-08-2025 09:53 | As per the reports submitted, the triggering incident was, failure of DC source-1&2 of 230kV and 110kV level. CTDs of all lines and ICTs operated and tripped all the elements connected to 230kV buses and 110kV buses leading to loss of power supply to 230kV buses and 110kV buses of 400kV Vellalaviduthi SS | 1.SCADA SOE to be made available at the 400kV Vellalaviduthi SS. 2.TANTRANSCO to check the healthiness and adequacy of all the battery cells of 220V DC battery banks intended for Vellalaviduthi SS. | TANTRANSCO | cepc:TANTRANSCO: 06/11/2025 10:42:00: will be complied cepc:TANTRANSCO: 04/12/2025 13:14:47: SCADA SOE now made available Addressed to System Operation wing cepc:TANTRANSCO: 05/01/2026 12:57:59: Reminder Letter sent 09.12.2025 cepc:TANTRANSCO: 02/02/2026 14:40:41: 1. SCADA SOE _ now complied 2. Addressed to system Operation wing cepc:TANTRANSCO: 04/03/2026 16:03:55: Complied. Healthiness o battery now found in order. | Complied | Complied
135/III/2 | SRPDR multi tripping | 24-08-2025 20:14 | As per the reports submitted, the triggering incident was CT failure at GC, resulting to which a B-N fault was also observed. Differential protection, OLTC, main PRV operated. Testing of R, Y phase unit testing was under progress. Replacement of failed unit with spare unit is being arranged. During CT failure at GC, ICT 5 contributed a fault current of 9.7kA, Due to turbulence Buckholz operated, subsequently110kV BBP also operated. | TANTRANSCO to review the velocity settings in the Buchholz relay. | TANTRANSCO | cepc:TANTRANSCO: 06/11/2025 10:42:00: will be complied. cepc:TANTRANSCO: 04/12/2025 13:14:47: Addressed to System Operation wing cepc:TANTRANSCO: 05/01/2026 12:57:59: Addressed to System operation wing cepc:TANTRANSCO: 02/02/2026 14:40:41: Addressed to System Operation wing cepc:TANTRANSCO: 04/03/2026 16:03:55: Informed to System operation wing cepc:TANTRANSCO: 30/03/2026 16:34:30: Informed to System operation wing | Pending | Pending
135/III/4 | 400KV/230KV SALEM_TN-ICT-2 | 31-08-2025 18:40 | As per the reports submitted, the triggering incident was Y-N fault in 230kV Salem Mettur Line-2 at a distance of 3km from Salem end. At the same time, 400/230KV Salem ICT 2 tripped on Y phase Buckholz alarm and Y Phase OLTC OSR trip indications. | TANTRANSCO to review the velocity settings in the Buchholz relay. | TANTRANSCO | cepc:TANTRANSCO: 06/11/2025 10:42:00: will be complied. cepc:TANTRANSCO: 04/12/2025 13:14:47: Addressed to System Operation wing cepc:TANTRANSCO: 05/01/2026 12:57:59: Addressed to System operation wing cepc:TANTRANSCO: 02/02/2026 14:40:41: Addressed to System Operation wing cepc:TANTRANSCO: 04/03/2026 16:03:55: Informed to System operation wing cepc:TANTRANSCO: 04/03/2026 16:37:13: Complied.The Diaphram of the OLTC-OSR chamber was replaced by a new one in the Y-phase unit. The micro switch at OLTC-OSR has been checked and cleaned. The Bucholz relay was completely overhauled. The above were checked to satisfatory. | Complied | Complied
136/I/7 | Complete Outage of 230kV ARS, Kamachi, Cauvery, Thervoi Kandigai, Mychelin, Suryadev and Gummidipoondi SS | 04-10-2025 19:29 | 230kV ARS, Kamachi, Cauvery, Thervoi Kandigai, Mychelin, Suryadev were radially connected to Gummidipoondi. The triggering incident is the Y-B fault in 230kV NCTPSGummidipoondi line and 110kV connected line tripped after around 29s and due to which 230kV Sullurpet-Gummidipoondi also tripped due to wrong bus CVT selection. With the tripping of both 230kV NCTPS-Gummidipoondi and 230kV Sullurpet-Gummidipoondi lines led to the complete outage of 230kV ARS, Kamachi, Cauvery, Thervoi Kandigai, Mychelin, Suryadev and Gummidipoondi SS. | 1.TANTRANSCO to consult OEM regarding SOTF operation of the relay. 2.TANTRANSCO to follow SOP during testing and Maintenance activities. | TANTRANSCO | cepc:TANTRANSCO: 04/12/2025 13:14:47: 1.Will be complied 2. Addressed to System Operation wing cepc:TANTRANSCO: 05/01/2026 12:57:59: 1. Will be complied 2. Addressed to System Operation wing cepc:TANTRANSCO: 02/02/2026 14:40:41: 1. will be complied 2.Addressed to System Operation wing for compliance cepc:TANTRANSCO: 04/03/2026 16:03:55: will be complied Addressed to system operation wing cepc:TANTRANSCO: 30/03/2026 16:34:30: Will be complied | Pending | Pending
136/I/8 | Tripping of 230kV Bus-1 at GUMMIDIPOONDI of TANTRANSCO | 04-10-2025 21:02 | The stations were under the process of restoration and 230KV-SULURPET-GUMMIDIPOONDI-1 line was charged. Due to human error, the 230kV Sullurpet-Gummidipoondi bus CVT selection was kept in 230kV Bus-2 even though it was connected to Bus-1 and 230kV Sullurpet-Gummidipoondi line at Gummidipoondi did not have voltage input and hence the line Z1 protection operated and 3ph tripped for 230KV-SULURPETGUMMIDIPOONDI- 1 at GUMMIDIPOONDI end. Due to the tripping only source line connected to Bus-1 at Gummidipoondi end led to the Tripping of 230kV Bus-1 at Gummidipoondi. | TANTRANSCO to refer the event to OEM and furnish the findings. | TANTRANSCO | cepc:TANTRANSCO: 04/12/2025 13:14:47: Will be complied cepc:TANTRANSCO: 05/01/2026 12:57:59: Will be complied cepc:TANTRANSCO: 02/02/2026 14:40:41: Will be compiled cepc:TANTRANSCO: 04/03/2026 16:03:55: Will be complied cepc:TANTRANSCO: 30/03/2026 16:34:30: will be complied | Pending | Pending
136/I/9 | Complete Outage of 230kV Tondiarpet SS, 230kV Athipattu SS of TANTRANSCO and 230kv NCTPS Generating station of TNPGCL | 06-10-2025 11:02 | As per the reports submitted, the triggering incident was R-N fault in 230kV NCTPS Tondiarpet Line-2. At NCTPS end, the fault was sensed in zone-2 and carrier was received. At Thondiarpet end, the fault was sensed in zone-1. However, the breaker failed to open making LBB to operate. Immediately all elements to 230kV Bus tripped leading to complete outage of 230kV Tondiarpet SS. Subsequently, other 230kV lines connected to 230kV NCTPS tripped on different faults. Tripping of all these lines led to running of NCTPS Units on house load of 38MW. Since, 230kV Athipattu was being radially fed from 230kV NCTPS, loss of power supply to 230kV NCTPS led to complete outage of 230kV Athipattu SS. | 1.DR Time Sync issue to be rectified at NCTPS. . | TNPGCL |  | Pending | Pending
136/I/9 | Complete Outage of 230kV Tondiarpet SS, 230kV Athipattu SS of TANTRANSCO and 230kv NCTPS Generating station of TNPGCL | 06-10-2025 11:02 | As per the reports submitted, the triggering incident was R-N fault in 230kV NCTPS Tondiarpet Line-2. At NCTPS end, the fault was sensed in zone-2 and carrier was received. At Thondiarpet end, the fault was sensed in zone-1. However, the breaker failed to open making LBB to operate. Immediately all elements to 230kV Bus tripped leading to complete outage of 230kV Tondiarpet SS. Subsequently, other 230kV lines connected to 230kV NCTPS tripped on different faults. Tripping of all these lines led to running of NCTPS Units on house load of 38MW. Since, 230kV Athipattu was being radially fed from 230kV NCTPS, loss of power supply to 230kV NCTPS led to complete outage of 230kV Athipattu SS. | 1.TANTRANSCO needs to periodically arrage maintainance using thermos vision camera to identify hotspots | TANTRANSCO | cepc:TANTRANSCO: 04/12/2025 13:14:47: Addressed to System Operation wing cepc:TANTRANSCO: 05/01/2026 12:57:59: Addressed to System Operation wing cepc:TANTRANSCO: 02/02/2026 14:40:41: Addressed to System Operation wing for compliance cepc:TANTRANSCO: 04/03/2026 16:03:55: Addressed to System operation wing cepc:TANTRANSCO: 30/03/2026 16:34:30: Addressed to System operation wing | Pending | Pending
137/I/4 | Complete Outage of 400kV Thappukundu SS of TANTRANSCO | 17-10-2025 03:31 | During antecedent conditions, 400kV Thappukundu SS was being radially fed through 400kV Thappukundu Anaikadavu Line-1. As per the reports submitted, the triggering incident was RY fault in 400kV Thappukundu Anaikadavu Line1 and the line tripped. Tripping of the only connected line led to complete outage of 400kV Thappukundu SS | TANTRANSCO to review the relay settings at Thappakundu end. | TANTRANSCO | cepc:TANTRANSCO: 05/01/2026 12:44:36: Relay setting reviewed. One end tripping may be due to source failure | Complied | Complied
135/I/5 | Complete Outage of 400kV Thappukundu SS of TANTRANSCO | 17-10-2025 04:47 | During antecedent conditions, 400kV Thappukundu SS was being radially fed through 400kV Thappukundu Anaikadavu Line-1. As per the reports submitted, the triggering incident was RY fault in 400kV Thappukundu Anaikadavu Line-1 and the line tripped. Tripping of the only connected line led to complete outage of 400kV Thappukundu SS | TANTRANSCO to configure the DR as per FOLD recommendations at Anaikudu and Thappakundu SS. | TANTRANSCO | cepc:TANTRANSCO: 05/01/2026 12:44:36: will be complied cepc:TANTRANSCO: 02/02/2026 14:40:41: will be ensured cepc:TANTRANSCO: 04/03/2026 16:03:55: Will be ensured cepc:TANTRANSCO: 30/03/2026 16:34:30: will be complied | Pending | Pending
137/III/14 | Multiple trippings at OTTAPIDARAM | 19-11-2025 01:34 | As per the reports submitted, the triggering incident was the tripping of OTTAPIDARAM-ICT-1, 2. It is found that rat entered in C&R panel and bit DC trip wire. Hence master relay operated. As per TANTRANSCO, the damaged wires were restored and normalized and ICT was taken into service through Tie breaker | TANTRANSCO to maintain the control panel integrity and to replace the damaged panel door at Ottapidaram SS. | TANTRANSCO | cepc:TANTRANSCO: 05/01/2026 12:44:36: System Operation wing plugged all holes | Complied | Complied
138/III/10 | 400KV/110KV OTTAPIDARAM-ICT-2 | 05-12-2025 12:27 | As per the reports submitted, in Bay No. 112 (Everrenew1), a jumper was cut between the bus isolator and the circuit breaker. The fault was outside the BBP protection zone. The fault was detected by the feeder protection relay, which issued a trip command and the breaker opened. However, the fault current persisted for more than 200 ms; hence, the LBB protection operated. As a result, all elements connected to 110 kV Bus2 were tripped (110 kV Vinfast, Bus Coupler, TMPL Amplus-1, and ICT2 LV), including the LV side of the 400 kV/110 kV Ottapidaram ICT2. | TANTRANSCO to check the End fault protection settings. | TANTRANSCO | cepc:TANTRANSCO: 02/02/2026 14:26:41: Feasibility will be studied & End fault protection will be enabled cepc:TANTRANSCO: 04/03/2026 16:03:55: Feasibility will be studied & end fault protection will be enabled cepc:TANTRANSCO: 30/03/2026 16:34:30: Feasibility will be studied & end fault protection will be enabled | Pending | Pending
138/III/16 | 400KV/230KV MANALI-ICT-4 | 14-12-2025 05:02 | As per the reports submitted, the 400/230 kV315 MVA ICT4 tripped due to the actuation of differential high-set, bias, and REF protections, along with the operation of the Main Tank PRV, OLTC PRV, OLTC OSR, and Buchholz trip. An HV R-phase bushing failure was observed. | TANTRANSCO to submit equipment failure report to CEA and the details of failed ICT, including make, to the SRLDC. | TANTRANSCO | cepc:TANTRANSCO: 02/02/2026 14:26:41: System Operation has to furnish the report. cepc:TANTRANSCO: 04/03/2026 16:03:55: Informed to System operation wing cepc:TANTRANSCO: 30/03/2026 16:34:30: informed to System operation wing | Pending | Pending
139/II/2 | Tripping of 230kV Bus-1 and 2 at KAYATHAR of TANTRANSCO | 10-01-2026 20:57 | In the antecedent condition, all the elements are connected to 230kV Bus-1 at Kayathar. As per the reports submitted, the triggering incident was Y phase jumper cut in between bus selection disconnector (89A & 89B) in 230kV Chekkanurunni feeder and creating a bus fault leading to Bus Bar protection operation and tripping of all the elements connected to Bus-1 at Kayathar end. This led to the tripping of 230kV Bus-1 and 2 at KAYATHAR of TANTRANSCO. | 1.TANTRANSCO to rectify the DT issue at Chekurani SS. 2.TANTRANSCO to enable the end fault protection at Kayathar SS. | TANTRANSCO | cepc:TANTRANSCO: 04/03/2026 15:35:34: DT wiring has to be carried out at Checkanurani end. End fault protection will be ensured at Kayathar end. | Pending | Pending
139/III/2 | Tripping of 400KV-VALLUR-ALAMATHY-1&2 | 24-12-2025 03:49 | As per the reports submitted the triggering incident is the Y-G fault and subsequent R-B fault in dead time in 400KV-VALLUR-ALAMATHY-2 line during which 400KV-VALLUR-ALAMATHY-1 tripped only at ALAMATHY end on SOTF and needs review. | 1.TANTRANSCO to review the TOR enable function in TANTRANSCO substations. 2.TANTRANSCO to rectify the SR time synchronization at Alamathy. | TANTRANSCO | cepc:TANTRANSCO: 04/03/2026 15:34:01: Line clear awaited. Bay owned by PGCIL. PGCIL has proposed to replace the relay cepc:TANTRANSCO: 30/03/2026 16:34:30: pending with PGCIL | Pending | Pending
139/VI/3 | 400KV-VALLUR-ALAMATHY-1 | 24-12-2025 03:49 | 400KV-VALLUR-ALAMATHY-1 | TANTRANSCO to rectify the DR time synchronization issue at 400kV Alamathy | TANTRANSCO | cepc:TANTRANSCO: 04/03/2026 15:31:58: Bay owned by PGCIL. PGCIL has proposed to replace the relays cepc:TANTRANSCO: 30/03/2026 16:34:30: Pending with PGCIL | Pending | Pending
139/VI/9 | 230KV-Chekkanurani-KAYATHAR(TN)-1 | 10-01-2026 20:57 | 230KV-Chekkanurani-KAYATHAR(TN)-1 | TANTRANSCO to rectify the DR time synchronization issue at KAYATHAR(TN) - 230KV | TANTRANSCO | cepc:TANTRANSCO: 04/03/2026 15:31:05: Time Sync checked & Found in order | Complied | Complied
140/III/2 | 400KV/110KV ALAMATHY-ICT-6 | 23-01-2026 06:45 | As per the reports submitted, the triggering incident is the B-G fault in 110 kV Alamathy - Avadi line. LBB operated due to failure of breaker and tripped all the elements connected to 110 kV Bus-1, where in 400/110kV ICT-6 at Alamathy also tripped. | TANTRANSCO advised to check the healthiness of the all the line breaker at Alamathy SS. | TANTRANSCO | cepc:TANTRANSCO: 30/03/2026 16:34:30: In general, Healthiness of breaker ( measurement of Contact resistance & Breaker timings were checked) is being checked during monthly maintenance. It will be ensured at Alamathy SS | Pending | Pending
140/III/3 | Tripping of main breakers of 400KV-NCTPS_STAGE_II-SUNGAVARACHATRAM-1&2 | 23-01-2026 10:22 | As per the reports submitted incident triggered due to faulty Main-2 D60 relay of 400KV-NCTPS_STAGE_II-SUNGAVARACHATRAM-1 even though DC supply was available, F8L card missing message observed in Main-2 relay leading to tie LBB operation and tripping of both the main breakers connected to Bus-1 and 2. However the tie breaker was in service during the event. | 1.TANTRANSCO to review the Tie Breaker LBB operation and tripping of Main breakers at Sungavarachatram SS during the incident. 2.TANTRANSCO to rectify the DR time sync issue at Sungavarachatram end | TANTRANSCO | cepc:TANTRANSCO: 30/03/2026 16:34:30: Main.2 D60 relay F8L module checked & found healthy & put into service and observed that No Spurious tripping noticed so far | Pending | Pending
140/III/13 | Multiple Trippings at 230kV Kadaperi SS of TANTRANSCO | 12-02-2026 02:39 | As per the reports submitted, the triggering incident was R-G cable fault in 230kV Kadaperi Alandur_CMRL Line-1. At Alandur end, the fault was sensed in zone-1 and the line tripped. At Kadaperi end, the fault was not sensed in any of distance protections till 800 ms though fault voltage dipped to 76 kV with 16.5 kA fault current. Meanwhile during this period, the same fault was sensed in Z3 in the remote ends of other 230kV lines connected to 230kV Kalivvendapattu Bus like 230kV Kadaperi SR Purur Line-1&2, 230kV Kadaperi Pudur and 230kV Kadaperi Kalivvendapattu line and tripped on zone-3. In 230kV Kadaperi Kalivvendapattu line at Kalivvendapattu end, DEF protection also operated and DT was sent to Kadaperi end. However the 230kV Kadaperi Kalivvendapattu line was holding from Kadaperi end as per TANTRANSCO's report. After around 800ms, the fault was sensed in zone-1 at 230kV Kadaperi end of 230kV Kadaperi Alandur_CMRL Line-1 when the voltage dipped to around 2.7 kV and the line tripped immediately. Though all 230 kV lines tripped, 230 kV Kadaperi Bus-1 and 230 kV Alandur Buses were charged from 110 kV side. At both Kadaperi end and Alandur end in 230kV Kadaperi Alandur_CMRL Line-1 carrier was not to sent to remote ends. | 1.TANTRANSCO to check the healthiness of Western Bus PT. 2.TANTRANSCO to implement differential protection in 230 kV KadaperiAlandur CMRL Line1 3.TANTRANSCO to review the distance protection settings in 230 kV Kadaperi Alandur CMRL Line1. | TANTRANSCO | cepc:TANTRANSCO: 30/03/2026 16:34:30: 1.to be checked 2. Line Differential procurement under progress | Pending | Pending
140/III/16 | 400KV/230KV MANALI-ICT-4 | 14-02-2026 11:16 | As per the reports submitted, the OLTC PRV trip was initiated due to moisture ingress and a trip contact defect noticed in the R-phase OLTC, after which the 86-relay operated. | TANTRANSCO to check the healthiness of the all other 400KV/230KV ICT OLTC contacts at MANALI. | TANTRANSCO | cepc:TANTRANSCO: 30/03/2026 16:34:30: will be ensured | Pending | Pending
141/II/2 | Tripping of 230kV Bus-2 of 230kV Kayathar SS of TANTRANSCO | 22-02-2026 12:48 | 230kV Kayathar SS is operating with double bus with bus coupler at 230kV level but all elements were connected to 230kV Bus-2. As per the reports submitted, the triggering incident was 230kV YB fault in 230kV Bus-2. Hence 230kV BBP operated and all elements connected in Bus-2 got tripped. 110kV side was in service during the event. | 1.TANTRANSCO to do periodic thermo vision scanning of Kayathar SS Switchyard. 2.TANTRANSCO to implement double bus operation at Kayathar SS. | TANTRANSCO |  | Pending | Pending
141/III/4 | 400KV-MANALI-PULIYANTHOPE-2 | 28-02-2026 06:15 | As per the reports submitted, the triggering incident is the B-G fault in the line. At Pulianthope end, the fault was sensed in Line Differential Protection, AR operated and tripped due to persistent fault. At Manali end, the fault was sensed in LDP and B pole openend. After around 1 sec AR operated at remote end intertrip and 3 ph tripped, but even after which AR operated after around 200ms and tripped due to persistent fault. | 1.TANTRANSCO to review the AR attempt after inter trip at Manali end. 2.TANTRANSCO to rectify the DR time synchronization issue at PULIYANTHOPE SS 3.TANTRANSCO to review the Non-availability of SCADA SOE at PULIYANTHOPE | TANTRANSCO |  | Pending | Pending
141/IV/1 | 400KV-NCTPS_STAGE_II-SUNGAVARACHATRAM-1 | 22-02-2026 05:58 | As per the reports submitted, the triggering incident is the B-G fault due to insulator flashover at location 101 from NCTPS ST2 and OPGW cut during the event. At both ends the fault was sensed in Z1 and AR did not operate due to carrier fail. | 1.TNPGCL to review the Non availability of SCADA SOE at NCTPS ST2.2. TNPGCL to review Non operation of AR at NCTPS ST2. | TNPGCL |  | Pending | Pending
141/IV/3 | 220KV-SULURPET-GUMMIDIPOONDI-1 | 27-02-2026 11:39 | As per the reports submitted, the triggering incident is the Y-G fault due to tree clearance issue in the vicinity of the line. At Sullurpet end, the fault was sensed in Z1, AR is disabled and 3ph tripped. At Gummidipundi end, the fault was sensed in Z1, and AR did not operate and 3ph tripped. | 1TANTRANSCO to enable the Auto Reclosure at Sullurpet. 2.TANTRANSCO to review the relay coordination at Gummidipoondi SS, as the phase to ground fault was sensed as phase to phase fault. | TANTRANSCO |  | Pending | Pending
141/IV/4 | 765KV-THIRUVALAM-ARIYALUR-1 | 27-02-2026 18:20 | As per the reports submitted, the triggering incident is the Y-G fault in the line. At ARIYALUR, the fault was sensed in Z1, AR operated and was successful and the line was holding. At THIRUVALAM end, the fault was sensed in Z1, AR did not operate in both main and tie and 3ph tripped. | TANTRANSCO to review the Auto Reclosure operation in 765KV-THIRUVALAM-ARIYALUR-1 line at Thiruvalam end. | TANTRANSCO |  | Pending | Pending
141/VI/3 | 400KV-NCTPS_STAGE_II-MANALI-1 | 24-02-2026 05:01 | Station at which DR time synchronisation was not observed NCTPS_STAGE_II - 400KV | TNPGCL to rectify the DR time synchronization issue at 400kV NCTPS Stage2 | TNPGCL |  | Pending | Pending
141/VI/8 | 400KV-SRIPERUMBADUR-CHITTOOR-1 | 01-03-2026 11:24 | Station at which DR time synchronisation was not observed SRIPERUMBADUR - 400KV | TANTRANSCO to rectify the DR time synchronization issue at SRIPERUMBADUR - 400KV | TANTRANSCO |  | Pending | Pending
PUDUCHERRY
124/I/9 | Complete outage of 230kV/110kV Bahoor SS of Pondicherry | 06-10-2024 03:50 | Complete outage of 230kV/110kV Bahoor SS of Pondicherry: During antecedent conditions, 230kV Pondicherry Bahoor was under outage. As per the reports submitted, the triggering incident was R-N fault in 230kV Bahour Karaikal line. Tripping of the only source resulted in complete outage of 230kV/110kV Bahoor SS. | PED to check the A/R scheme on 230KV Karaikal Bahour Line at Karaikal end | PED | ARUMUGAM:PED: 03/12/2024 12:30:05: Auto Reclosure scheme on 230KV Karaikal Bahour Line was tested at Karaikal end on 24.10.2024 and found in order. For Zone I, Phase to Ground fault occurred on the said line on 14.11.2024 at 11:00hrs and 16.11.2024 at 00:20hrs, Auto Reclosure scheme operated successfully at both Karaikal & Bahour ends. | Complied | Complied
124/I/9 | Complete outage of 230kV/110kV Bahoor SS of Pondicherry | 06-10-2024 03:50 | Complete outage of 230kV/110kV Bahoor SS of Pondicherry: During antecedent conditions, 230kV Pondicherry Bahoor was under outage. As per the reports submitted, the triggering incident was R-N fault in 230kV Bahour Karaikal line. Tripping of the only source resulted in complete outage of 230kV/110kV Bahoor SS. | PED to review the Zone-1 impedance and onfigure it to cover 100% of the protected line instead of 80% if the system is in radial mode | PED | ARUMUGAM:PED: 03/12/2024 12:30:05: Zone I impedance will be set with 100 percent of the protected line whenever the system is operated in radial mode in future. | Complied | Complied
124/I/13 | Complete outage of 230kV/110kV Bahoor SS of Pondicherry. | 10-10-2024 12:55 | During antecedent conditions, 230kV Pondicherry Bahoor was under outage. As per the reports submitted, the triggering incident was R-N fault in 230kV Bahour Karaikal line. Tripping of the only source resulted in complete outage of 230kV/110kV Bahoor SS. | PED to check the A/R scheme on 230KV Karaikal Bahour Line at Karaikal end | PED | ARUMUGAM:PED: 03/12/2024 12:30:05: Auto Reclosure scheme on 230KV Karaikal Bahour Line was tested at Karaikal end on 24.10.2024 and found in order. For Zone I, Phase to Ground fault occurred on the said line on 14.11.2024 at 11:00hrs and 16.11.2024 at 00:20hrs, Auto Reclosure scheme operated successfully at both Karaikal & Bahour ends. | Complied | Complied
124/I/13 | Complete outage of 230kV/110kV Bahoor SS of Pondicherry. | 10-10-2024 12:55 | During antecedent conditions, 230kV Pondicherry Bahoor was under outage. As per the reports submitted, the triggering incident was R-N fault in 230kV Bahour Karaikal line. Tripping of the only source resulted in complete outage of 230kV/110kV Bahoor SS. | PED to review the Zone-1 impedance and cover 100% of the protected line instead of 80% if the system is in radial mode | PED | ARUMUGAM:PED: 03/12/2024 12:30:05: Zone I impedance will be set with 100 percent of the protected line whenever the system is operated in radial mode in future. | Complied | Complied
132/I/2 | Complete Outage of 230kV/110kV/22kV Bahoor SS and 230kV/110kV Karaikal SS | 21-05-2025 07:36 | During antecedent conditions, 230kV Karaikal NLC TS-2 line was under outage to control the overloading of 400kV/230kV NLC TS-2 ICTs. Hence, 230kV/110kV/22kV Bahoor SS and 230kV/110kV Karaikal SS were radially fed from 400kV/230kV Pondy SS. The trigerring incident was RN fault in 230kV Pondy Bahoor line. Tripping of 230kV Pondy Bahoor line resulted in complete outage of 230kV/110kV/22kV Bahoor SS and 230kV/110kV Karaikal SS. | PED and TANTRANSCO to discuss and propose the line for ISTS status to enhance reliable power supply to Puducherry in time of contingency. | PED | ARUMUGAM:PED: 07/08/2025 11:13:02: Will be updated shortly. ARUMUGAM:PED: 25/08/2025 11:26:36: Will be updated shortly ARUMUGAM:PED: 19/09/2025 08:52:45: Will be updated shortly. | Pending | Pending
132/I/2 | Complete Outage of 230kV/110kV/22kV Bahoor SS and 230kV/110kV Karaikal SS | 21-05-2025 07:36 | During antecedent conditions, 230kV Karaikal NLC TS-2 line was under outage to control the overloading of 400kV/230kV NLC TS-2 ICTs. Hence, 230kV/110kV/22kV Bahoor SS and 230kV/110kV Karaikal SS were radially fed from 400kV/230kV Pondy SS. The trigerring incident was RN fault in 230kV Pondy Bahoor line. Tripping of 230kV Pondy Bahoor line resulted in complete outage of 230kV/110kV/22kV Bahoor SS and 230kV/110kV Karaikal SS. | PED to furnish the 110kV connectivity diagram of Karaikal Substation | PED | ARUMUGAM:PED: 07/08/2025 11:13:02: Furnished by email dated 07.08.2025. ARUMUGAM:PED: 25/08/2025 11:26:36: Complied. ARUMUGAM:PED: 19/09/2025 08:52:45: Complied. Furnished by email dated 07.08.2025. | Complied | Pending
132/I/2 | Complete Outage of 230kV/110kV/22kV Bahoor SS and 230kV/110kV Karaikal SS | 21-05-2025 07:36 | During antecedent conditions, 230kV Karaikal NLC TS-2 line was under outage to control the overloading of 400kV/230kV NLC TS-2 ICTs. Hence, 230kV/110kV/22kV Bahoor SS and 230kV/110kV Karaikal SS were radially fed from 400kV/230kV Pondy SS. The trigerring incident was RN fault in 230kV Pondy Bahoor line. Tripping of 230kV Pondy Bahoor line resulted in complete outage of 230kV/110kV/22kV Bahoor SS and 230kV/110kV Karaikal SS. | PED to furnish the connectivity diagram of the Karaikal Gas Power Plant | PED | ARUMUGAM:PED: 07/08/2025 11:13:02: Furnished by email dated 07.08.2025. ARUMUGAM:PED: 25/08/2025 11:26:36: Complied ARUMUGAM:PED: 19/09/2025 08:52:45: Complied, Furnished by email dated 07.08.2025. | Complied | Pending
138/I/6 | Complete Outage of 230kV Bahour SS of Pondy | 18-12-2025 10:27 | As per the reports submitted, the triggering incident was R-N fault in 230kV Bahour Bus-2. Since, 230kV Bahour is operating with no bus segregation due to non availability of CTs at bus coupler, BBP operated tripping all elements to 220kV Bus-1 and Bus-2. This led to complete outage of 230kv Bahour SS> | PED to ensure all relay settings are updated in DMNS portal. PED to implement the BUSBAR zone segregation. | PED | ARUMUGAM:PED: 31/01/2026 10:25:18: 1. PED already updated all the relay settings through DMNS portal. As the updated relay settings could not be accessed, the matter has been referred to PRDC for which they have agreed to setright the issues at the earliest. 2. Presetly no attendent CTs are available to 230KV B/C Breaker. Arrangement is being made to provide attendent CTs to the B/C Breaker. Will be implemented multi bus multi zone bus bar protection on or before 28.02.2026. ARUMUGAM:PED: 02/03/2026 09:59:19: 1. PED already updated all the relay settings through DMNS portal. As the updated relay settings could not be accessed, the matter was referred to PRDC. PRDC responded and now the relay settings are available in DMNS Portal. 2. Presetly no attendent CTs are available to 230KV B/C Breaker. Arrangement is being made to provide attendent CTs to the B/C Breaker. Will be implemented multi bus multi zone bus bar protection on or before 31.05.2026. ARUMUGAM:PED: 30/03/2026 16:41:59: PED already updated all the relay settings through DMNS portal. As the updated relay settings could not be accessed, the matter was referred to PRDC. PRDC responded and now the relay settings are available in DMNS Portal. 2. Presetly no attendent CTs are available to 230KV B/C Breaker. Arrangement is being made to provide attendent CTs to the B/C Breaker. Will be implemented multi bus multi zone bus bar protection on or before 31.05.2026. | Pending | Pending
140/III/17 | 230KV-NEYVELI_TS_II-VILLIANUR-1 | 14-02-2026 15:49 | 230 KV-NEYVELI_TS_II-VILLIANUR-1 was idle charged from Villianur end. As per the reports submitted, the triggering incident was B-G fault in the line at a distance of 1.7 km from Villianur end. At Villianur end, the fault was sensed in zone-1. A/R operated and the line tripped on persistent fault. However, another A/R attempt was observed during dead time and the same needs review. | PED is advised to review the A/R operation in 230KV Neyveli Villianur Line. | PED | ARUMUGAM:PED: 30/03/2026 16:41:59: During the special relay testing conducted on 05.03.2026, it is observed that A/R close command timing and A/R dead time are set with 1second and and 900milliseconds respectively. It is proposed to revise the above said timing to 100-150milliseconds and 1seconds respectively. As the above said time correction is requiring database updation, it is proposed to implement A/R scheme in Main-I & Main-II Distance Protection relays after discarding the same from BCU. Will be implemented on or before 30.04.2026. | Pending | Pending
PGCIL
110/II/1 | Tripping of 400 kV RAMAGUNDAM - CHANDRAPUR 1&2 | 25-Jul-2023 19:11 | As per the reports submitted, the triggering incident was Y-N fault in 400kV Ramagundam Chandrapaur line-1. At Ramagundam end, the fault was sensed in zone-1, A/R operated, and the line was holding. The line tripped only at Chandrapur end. Subsequently, 400kV Ramagundam Chandrapur Line-2 tripped at Ramagundam end on suspected zone-3 protection maloperation with a delay of 1 second. Tripping is not in order. Points for review: 1. Reason for tripping of 400kV Ramagundam Chandrapur Line-2 on zone-3 protection. 2. Reason for tripping of 400kV Ramagundam Chandrapur Line-1 at Chandrapur end. | PGCIL SR-I to consult with their HVDC wing on this incident and submit detailed report to SRPC&SRLDC | PGCIL (SR-I) | Venkatasai:PGCIL (SR-I): 30/09/2024 18:07:23: As per the information from WR team, remote closing of main CB did not happen from CRP panel and mimic also. During further checking of closing circuitry, it was observed that negative coming from CB coil (Y-phase) was terminated in CSD and dropping to 55 volt which resulted in AR failure of main CB. The issue with CSD card was rectified. AR was checked and found to be operating satisfactorily. As per the philosophy adopted at Chandrapur SS, AR of tie CB will be kept in Non-auto mode. Only main CB AR will be kept in Auto mode. | Complied | Complied
116/III/4 | 400KV-VELLALAVIDUTHI- KARAIKUDI- 1 | 07-02-2024 17:44 | Overvoltage stage-1 operation at the Karaikudi end due to a suspected B-ph Voltage issue and DT was received at the Vellalaviduthi end | PGCIL SR-2 is recommended to replace the relay and inform to SRPC. | PGCIL (SR-II) | rtamcsr2:PGCIL (SR-II): 07/08/2024 15:30:45: Shutdown of line availed on 15/07/2024 and issue rectified. Hence point may be closed | Complied | Complied
118/III/1 | HVDC GAJUWAKA POLE 1 | 27-03-2024 06:24 | Pole -1 got blocked on Valve Cooling Pump changeover fail due to nearby station line fault at 220kV level of AP TRANSCO station | PGCIL to refer the matter with OEM. | PGCIL (SR-I) | Venkatasai:PGCIL (SR-I): 03/07/2024 18:08:28: Matter has been referred to OEM. But support from OEM is not available as the technology is obsolete. Refurbishment of pole-1 will be taken up for resolving the issues with Pole-1 at Vizag HVDC. Venkatasai:PGCIL (SR-I): 30/09/2024 18:03:15: As per the current torque characteristics for the subject motor, the allowable full load current is 191A for full load speed. For short term balance of Moment of Inertia of the complete system the OLR setting is changed to 230A keeping the torque characteristics graded as a remedial measure to avoid tripping of Valve cooling pump due to OLR. | Complied | Complied
119/III/1 | Multiple Trippings at HVDC Gazuwaka | 26-04-2024 16:24 | 400kV Gazuwaka Jeypore Line-1 was hand tripped on Emergency basis to isolate Line Reactor Circuit Breaker. Subsequently, 400kV Gazuwaka Jeypore Line-2 tripped on over voltage at Gazuwaka end and Gazuwaka HVDC Pole-1&2 was blocked due to non-availability of Bus voltage. | PGCIL SR-I to furnish the report on whether RPC settings are appropriate concerning the grid parameters and also furnish the RPC logic document. | PGCIL (SR-I) | Venkatasai:PGCIL (SR-I): 03/07/2024 18:08:28: Detailed report has been furnished. Venkatasai:PGCIL (SR-I): 03/10/2024 11:57:44: Report furnished. | Complied | Complied
119/III/4 | 400/220kV ICT-1 at Gazuwaka | 29-04-2024 01:50:00 | Triggering incident was R-N fault in 400kV Kalpakka Gazuwaka Line-2. At both ends, A/R operated and the line was holding. At the same time, 400/220kV ICT-1 at Gazuwaka tripped on TEED protection. | PGCIL SR-I to expedite to replace the static relay with numerical relay. | PGCIL (SR-I) | Venkatasai:PGCIL (SR-I): 03/07/2024 18:08:28: Static Teed relay of ICT-1 was replaced with numerical relay. | Complied | Complied
122/IV/8 | 400KV-GHANAPUR-RAMAGUNDAM-4 | 19-08-2024 14:32 | On 19.08.2024 14:32 Hrs, Ramagundam-Hyderabad Line-4 sensed zone-1 multiphase fault and tripped all three poles. However zone-1 Rph-E is sensed at remote end substation and A/R was successful at remote end. | PGCIL to verify to A/R issues at Ramagundam end. | PGCIL (SR-I) | Venkatasai:PGCIL (SR-I): 03/10/2024 11:57:44: The settings were checked and are found to be in order. AR scheme was also checked and is found to be in order. AR was successful during subsequent fault on 04.09.2024. However, the issue was referred to SIEMENS by NTPC. Corrective actions suggested by them will be implemented. | Complied | Complied
124/III/15 | Multiple trippings at 400kV Kolar_PG of PGCIL SR-2 | 20-10-2024 03:14 | Multiple trippings at 400kV Kolar_PG of PGCIL SR-2: As per the reports submitted, the triggering incident was fault in HVDC500KV-TALCHER-KOLAR_DC-1. LFL operated with recovery sequence and fault was cleared in 2nd attempt. During this event, the voltage in 400kV Kolar Bus has raised to 430kV and 400kV Kolar Hoody Line-2 and 400kV Kolar Hosur Line-1 tripped on Over Voltage Stage-1 protection operation at Kolar end. | PGCIL SR-II to take up with OEM regarding the process involved during filter activation and furnish the update in this regard. | PGCIL (SR-II) | rtamcsr2:PGCIL (SR-II): 01/01/2025 17:44:40: After anlysing the events and OEM Manual the filter activation is in Auto mode . The filter activation is operating correctly as per the operating principle. The System overvoltages were above the OV setting and the Protection Scheme operation is correct. | Complied | Complied
128/III/2 | 400KV/220KV GHANAPUR-ICT-2 | 23-01-2025 10:12 | As per the reports submitted, while tracing persisting DC Earth fault in 220V Source 1&2, ICT-2 tripped on operation of Group-A relays of 220KV CBs. The disconnected (+Ve) wire has touched the Group-A trip bus and extended tripping to 86A relays of ICT-2. Tripping is not in order. | 1.PGCIL SR-I to strictly follow SOP and inspect for any loose wire condition at any other locations of Gazuwaka SS | PGCIL (SR-I) | Venkatasai:PGCIL (SR-I): 01/04/2025 15:16:39: Standard Operating Procedures (SOP) are being strictly followed. Before the commencement of Earth fault tracing, all work panels are being inspected for any loose wires and are being taped to prevent inadvertent contact. | Complied | Complied
129/III/1 | Multiple trippings at BIDADI_PG | 15-02-2025 17:21 | As per the reports submitted, the triggering incident is the Y-B fault in 400KV BIDADI_PG-SOMANAHALLI-2 and at both ends, the fault was sensed in Z1 and 3ph tripped. During the event 400KV-BIDADI_PG TUMKUR-2 line also tripped at BIDADI end only and needs review. | 1. PGCIL to ensure relay firmware updates, in consultation with OEM. | PGCIL (SR-II) | rtamcsr2:PGCIL (SR-II): 09/05/2025 12:46:49: Bidadi tumkur Line 2 Main-1 relay P444 Firmware Updated to latest Firmware on 24.03.3025 during Line Shutdown. Allso Email sent to SROC Protection regarding details of updated firmware is sent on 09.05.2025 . rtamcsr2:PGCIL (SR-II): 02/06/2025 18:41:04: FIRMWARE IS UPGRADED ON 24.04.2025 THE SAME WAS INTIMATED TO SRPC - SRPCPROTECTIONDATA@GMAIL.COM VIDE EMAIL DATED 09.05.2025 . ALSO COMPLIANCE TO THE SAME IS MENTIONED IN PREC ALSO ON 09.05.2025 | Complied | Complied
130/III/19 | 400KVVijayawada- Vemagiri_PG- 2&3 | 12-04-2025 18:16 | As per the reports submitted, the triggering incident is the suspected fault in the multi circuit portion of 400KV-VIJAYAWADA- Vemagiri_PG- 2&3 where in fault was developed between R-ph of 400KV- Vijayawada -Vemagiri_PG-2 and B- ph of400KV-Vijayawada-Vemagiri_PG-3 near Vemagiri end, as illustrated in the figure below. For 400KVVijayawada- Vemagiri_PG-2, at Vemagiri end the fault was sensed in Z1 only in R-ph as B-ph current contributed was very low (but voltage dip can be seen from the DR), AR operated and was successful. At Vijayawada end, the default was sensed in Z2 R-B phases and the carrier was received leading to 3ph trip of the line. For 400KV-Vijayawada- Vemagiri_PG-3, at Vemagiri end the fault was sensed in Z1 only in B-ph as R-ph current contributed was very low (but voltage dip can be seen from the DR), AR operated and was successful. At Vijayawada end, the default was sensed in Z2 R-B phases and the carrier was received leading to 3ph trip of the line. The lines were holding from Vemagiri end. | PGCIL SR-1 to submit the required details of the incident to the SRLDC for the further analysis. | PGCIL (SR-I) | Venkatasai:PGCIL (SR-I): 31/05/2025 12:00:21: Information Furnished in SPOORTHI portal of SRLDC in Ticket No- T-Tr-PGCIL SR-1-5241-1. | Complied | Complied
130/IV/20 | 400KVGOOTYKURNOOL_ PG- 1 | 20-04-2025 17:09 | As per the reports submitted, the triggering incident is the B-N fault in the line. At Gooty end, the fault was sensed in Z2 carrier aided trip and AR operated and tripped due to persistent fault. At Kurnool end, the fault was sensed in Z1, AR did not operate (due to intermittent failure of carrier channels as per FIR). | PGCIL SR-1 to review the non-operation of AR at Kurnool end | PGCIL (SR-I) | Venkatasai:PGCIL (SR-I): 31/05/2025 11:31:30: At Kurnool SS, Line tripped on persisting fault in B-N All the phases of both main & tie CBs tripped for the first fault. Upon checking, it is understood that failure of both the carriers was persisting prior to the fault due to which AR L/O relay operated in both main & tie bays. The A/R function was tested on 20.04.2025 during line breakdown period and the logic is in order. Both channels were healthy. The operation is in order. Already details submitted in 130 PCSC. | Complied | Complied
130/VI/3 | 220KV-ELAPULLY-PALAKKAD(KL)-2 | 21-03-2025 20:08 | DR time synchronization was not observed at PALAKKAD(KL) - 220KV | PGCIL SR-II to resolve the time synchronization issue | PGCIL (SR-II) | rtamcsr2:PGCIL (SR-II): 02/06/2025 18:36:15: NO ISSUE OBSERVED AT PGCIL END PALAKKAD END. HOWEVER THE TIME SYNCH WAS CHECKED IN ALL RELAYS AND FOUND CORRECT. | Complied | Complied
132/III/26 | HVDC 500KV GAZUWAKA Pole 1 | 15-06-2025 15:52 | Tripping of the HVDC 500KV GAZUWAKA Pole 1 blocked on AC>DC fault alarm | PGCIL SR-1 to consult PGCIL ER and update on the reason for the voltage dip and furnish a detailed report | PGCIL (SR-I) | Venkatasai:PGCIL (SR-I): 06/08/2025 09:51:43: Consulted POWERGRID Odisha projects, as per the report submitted during the same time at 15:52 Hrs 765KV Jharsuguda - Dharamjaygarh _4 line A/R operated and there are no other faults reported. The report attached. Due to the weak East grid conditions, it is suspected the origin might the EHV disturbance. SRLDC may further furnish information for voltage dip during the incidence. The consequence to the voltage dip detailed tripping analysis is already deliberated in 132 PCSC and once again submitted. Requested close of the PREC. | Complied | Complied
132/III/28 | Tripping of 400kV Gazuwaka-Kalpakka-1&2 | 16-06-2025 14:58 | As per the reports submitted and data available (SCADA and PMU), 400KV-GAZUWAKA-KALPAKKA-1&2 tripped at GAZUWAKA end only without any fault and needs review. | PGCIL SR-1 to enable only DEF at Gazuwaka end for Gazuwaka-Kalpakka Lines | PGCIL (SR-I) | Venkatasai:PGCIL (SR-I): 06/08/2025 09:51:43: The detailed tripping analysis is deliberated in 132nd PCSC. As per the recommendations and in consultation with APTRANSCO, Only DEF is enable for Kalapa lines at Gajuwaka and Definite Time is disabled. Requested for close of PREC. | Complied | Complied
134/III/7 | Tripping of 400KV-MYSORE-KOZHIKODE-2 | 13-08-2025 03:33 | As per the reports submitted, the triggering incident was fault in 400kV Hiriyur Mysore Line-1. At the same time, momentary over voltage was observed at 400kV Mysore SS and OV protection operated in 400kV Mysore Kozhikode Line-2 at Mysore end and DT was sent to Kozhikode end. From the DR at Mysore end, voltages observed are Vr-251kV, Vy-247kV, Vb-248kV. Tripping is not in order as the over voltage is momentary. | PGCIL SR-2 to follow SOP during Testing activities | PGCIL (SR-II) | rtamcsr2:PGCIL (SR-II): 09/10/2025 18:09:49: Site has been sensitized to followup the SOP always and same will be ensure in future also. | Complied | Complied
135/II/7 | Tripping of 400kV Bus-2 of Yelahanka SS of PGCIL SR2 | 11-09-2025 18:55 | The triggering incident is the R-G bus fault in 400kV Bus-2 of Yelahanka SS during the process of restoration of failed breaker bay (400kV Yelahanka-Nelmangala which occurred during 08/09/2025 23:04), during which due to closing of isolator and since still the fault was not fully rectified leading to the Bus fault and tripping of the elements connected to Bus-2 at Yelahanka. This led to the tripping of 400kV Bus-2 of Yelahanka SS. | PGCIL SR-2 to rectify time synchronization issue at Yelahanka | PGCIL (SR-II) | rtamcsr2:PGCIL (SR-II): 03/11/2025 12:44:01: There was no time synchronization issue at Yelhanka. however cross checked found ok. | Complied | Complied
135/II/9 | Tripping of 400kV Bus-1 of 400kV Pavagada SS | 18-09-2025 11:04 | As per the reports submitted, the triggering incident was Y-N fault in 400kV Pavagada Bus-1. Immediately, 400kV Bus-1 BBP operated and all elements connected to the bus tripped. | 1.PGCIL SR-II to enable DT for BBP operation 2.PGCIL SR-II to rectify DR Time Synch at Tumkur | PGCIL (SR-II) | rtamcsr2:PGCIL (SR-II): 03/11/2025 12:50:01: 1. DT send scheme provided with Busbar operated. However Busbar scheme is One and half. 2. DR time synchronization issue rectified at Tumkur end. | Complied | Complied
135/III/11 | 400KV-GHANAPUR-GAJWEL-1 | 07-09-2025 23:36 | As per the reports submitted, the triggering incident was Y-N fault in the line. The fault distance from Ghanapur end was 14.3kms. At both ends, the Y-pole tripped on Y-N fault and further tripped on over-voltage stage-2 operation after 0.6sec before attempting auto recloser. The voltage has gone to 393kV as per the DR submitted at Ghanapur end. | PGCIL SR-1 to furnish the detailed report in consultation with their technical department for three phase tripping of Reactor during single phase faults. | PGCIL (SR-I) | Venkatasai:PGCIL (SR-I): 03/11/2025 17:44:39: CC-AM consented for implementation. Applied Shutdown in OCC 01.02.2025. Will be completed as per the approval of Shutdown. Venkatasai:PGCIL (SR-I): 02/01/2026 09:15:27: The tripping of reactor for single phase line fault is implemented on 10.12.2025. Submitted for closure. | Complied | Complied
135/III/14 | 400KV-NELLORE_PG-THIRUVALAM-1 | 14-09-2025 05:07 | As per the reports submitted, the triggering incident is the B-G fault in the line, during the auto recloser Over Voltage ST-2 operated at Thiruvalam end due to suspected LV oscillations and 3ph tripped. | PGCIL SR-II to conduct a detailed analysis of the event in consultation with their technical department and furnish the report | PGCIL (SR-II) | rtamcsr2:PGCIL (SR-II): 03/11/2025 12:50:50: Issue has been referred to our T&D department. The analysis is under progress. Once the detailed report received same will be shared to SRPC. Kindly close this point. | Complied | Complied
137/III/15 | 400KV-NELLORE_PG-VIJAYAWADA-2 | 19-11-2025 15:15 | As per the reports submitted, the triggering incident was Relay Maloperation. At Nellore end, tripped on L/R differential relay Maloperation at Nellore SS and DT was sent from Nellore end to Vijayawada end. At Vijayawada end, the DT was received from Nellore end and the line got tripped. | PGCIL SR-I to check the Differential protection CTs healthiness. | PGCIL (SR-I) | Venkatasai:PGCIL (SR-I): 02/01/2026 09:11:07: Differential protection CT Insulation resistance, CT winding Resistance carried out and found normal. At present, the reactor is removed from Service and is being replaced with new reactor under ADD-CAP. Submitted for closure of the observation. | Complied | Complied
137/VI/18 | 400KV-KARAIKUDI-MADURAI_PG-1 | 19-11-2025 11:53 | 400KV-KARAIKUDI-MADURAI_PG-1 | PGCIL SR-2 to rectify the DR time synchronization issue at MADURAI_PG - 400KV. | PGCIL (SR-II) | rtamcsr2:PGCIL (SR-II): 02/01/2026 19:15:58: DR time synchronization rectified in Madurai | Complied | Complied
140/III/5 | 400KV-KURNOOL_PG-NARNOOR-1 | 25-01-2026 18:27 | As per the reports submitted, the triggering incident occurred during 400kV Bus-1 bus bar testing during the shutdown, where in Kurnool main breaker (410) was unavailable. During the bus bar testing activity, BBP operation was high (as per DR) and after around 200ms 41152 tie breaker also got tripped on LBB operation. Due to the tripping of both main and tie breaker led to the tripping of 400kV Kurnool-Nannoor-1 line and DT was sent to remote end. At Narnoor end, the Breaker tripped on DT receive. | PGCIL SR-I advised to follow the SOP during the Bus bar testing. | PGCIL (SR-I) |  | Pending | Pending
141/VI/11 | 400KV-KOLAR_AC-SRIPERUMBADUR-1 | 03-03-2026 14:09 | Station at which DR time synchronisation was not observed KOLAR_AC - 400KV | PGCIL SR-II to rectify the DR time synchronization issue at KOLAR AC - 400KV | PGCIL (SR-II) |  | Pending | Pending
OTHERS
109/II/4 | Tripping of 230kVNEYVELI_ TS_II - KADALANGUDI & 230kV NEYVELI KADALANGUDI LINE | 17-06-2023 3.16.00 AM | the triggeirng incident was RN fault in 230kV Neyveli Kadalangudi line. At both ends, A/R operated and the line tripped on persistent fault. At the same time 230kV Neyveli TS-2 Kadalangudi Line-2 tripped only at Neyveli TS-2 end on zone-1.protection. | NLC TS II to transplay the event and check the correctness of operation and furnish their findings to SRPC & SRLDC | NLCIL (NLCTS II) | NLCI/TS2:NLCIL: 06/11/2024 12:08:00: According to SLD submitted by Kadalangudi SS to the trip portal, the distance is mentioned as 89KM. The implemented settings at Neyveli TPS is 94.5KM. When a transplay conducted in spare relay wirh 89KM distance, the relay did not mal-operate. A mail dated 07.05.2024has been sent to SRPC in this reg for resolving the issue. NLCI/TS2:NLCIL: 05/04/2025 15:26:06: Relay reach settings modified and relay testing done found in order. kept in observation. | Complied | Complied
110/I/4 | Complete Outage of 230kV JSW_Vilathikulam Wind | 13-08-2023 14:31 | As per the reports submitted, the 230kV TTGS JSW_Vilathikulam_Wind line tripped only at JSW_Vilathikulam end and the details are awaited. Tripping of the only connected line resulted in complete outage of 230kV JSW_Vilathikulam Wind. | JSWEL to block all Distance Scheme protection during VT fuse fail condition and enable non-directional over current. | JSWEL |  | Pending | Pending
110/II/1 | Tripping of 400 kV RAMAGUNDAM - CHANDRAPUR 1&2 | 25-Jul-2023 19:11 | As per the reports submitted, the triggering incident was Y-N fault in 400kV Ramagundam Chandrapaur line-1. At Ramagundam end, the fault was sensed in zone-1, A/R operated, and the line was holding. The line tripped only at Chandrapur end. Subsequently, 400kV Ramagundam Chandrapur Line-2 tripped at Ramagundam end on suspected zone-3 protection maloperation with a delay of 1 second. Tripping is not in order. Points for review: 1. Reason for tripping of 400kV Ramagundam Chandrapur Line-2 on zone-3 protection. 2. Reason for tripping of 400kV Ramagundam Chandrapur Line-1 at Chandrapur end. | NTPC to furnish the findings in detail and modified Zone-3 settings suggested by their Engineering Division to SRPC/SRLDC. | NTPC -RAMAGUNDAM | RSTPS:NTPC: 05/03/2025 11:16:12: Settings reviewed | Complied | Complied
110/II/10 | Tripping of 400kV Bus-1 of 400kV/220kV Kaiga APS of NPCIL Kaiga | 11-Aug-2023 05:19 | 400kV/220kV Kaiga APS is operating with one and half breaker scheme at 400kV level. As per the reports submitted, the triggering incident was Main CB LBB maloperation of 400kV/220kV Kaiga ICT-1 which was under LC. Immediately all the Main CBs connected to 400kV Bus-1 tripped causing the de-energisation of 400kV Bus-1 at Kaiga APS. | KGS, NPCIL to check the CT Star neutral connection and submit report to SRPC/ SRLDC | NPCIL-KAIGA | KGS34:NPCIL: 23/10/2023 11:05:23: Star Neutral connections of CTs were checked for ICT1 & found OK | Complied | Complied
111/II/1 | Tripping of 400kV VEMAGIRI - SIMHADRI 1 | 22-08-2023 04:15 | As per the reports submitted, the triggering incident was Y-N fault in 400 kV VEMAGIRI - SIMHADRI 2 and 400 kV VIJAYAWADA - VEMAGIRI 2. A/R operated at both ends of both lines and the lines tripped on persistent fault. At the same time, 400kV VEMAGIRI - SIMHADRI 1 tripped only at Simhadri end and the same needs review. | NTPC Simhadri to check Main-I and Main-II relay settings for Vemagiri-Line1, transplay the event, check the earth fault compensation factor and consult OEM regarding the relay behavior for both circuits. | NTPC |  | Pending | Pending
111/I/1 | Complete Outage of 220kV Tirumani SS-1 of KSPDCL occurred on 09-09-2023 | 09-09-2023 at 09:10 hrs | As per the reports submitted, the triggering incident was tripping of 220kV Pavagada Tirumani Line-1 only at Tirumani end on relay mal-operation. Tripping of only connected line resulted in complete outage of 220kV Tirumani SS-1. | KSPDCL to take up the GE make relay (Main-I) mal-operation issue with OEM and furnish a report in this regard. | KSPDCL | ceokspdcl:KSPDCL: 03/04/2025 15:34:22: The relay Mal operation issue is escalated to OEM and they confirmed that the relay is in healthy condition and till today the relay is functioning satisfactorily. Now KSPDCL has planned for relay calibration and the report will be submitted. | Complied | Complied
107/I/12 | . | 18-03-2023 5.18.00 PM | . | KSPDCL to enable Auto reclosure to all 220 kV lines at KSPDCL substation. | KSPDCL | ceokspdcl:KSPDCL: 03/04/2025 15:25:42: Action will be taken to enable the autoreclosure settings in coordination with KPTCL RT team. ceokspdcl:KSPDCL: 05/07/2025 16:30:15: Action initiated to enable AR settings in coordination with KPTCL RT team. | Pending | Pending
97/II/14 | . | 24-06-2021, 09:10 hrs. | triggering incident was tripping of 220 kV NP Kunta PS-3 Line 2 due to isolator jumper clamp breakdown. Since this is the only line connected to Bus-1, this led to de-energisation of 220 kV Bus-1 at 220 /33 kV NP Kunta PS-3. | i) APSPCL, in coordination with PGCIL (SR-I), to take steps to restore communication link and bring Line Differential Protection (LDP) into service on 220 kV NPKunta PS-3 their NP Kunta PS-3 station, and configure them for appropriately for capturing all requisite protection operations. | APSPCL |  | Pending | Pending
54/I/1 | Complete outage of 230 kV S.P.Koil Station of TANTRANSCO | 02-04-2016 at 17:08 hrs | B-phase CT failure occurred in 230 kV S.P.Koil - MAPS line-1. Busbar protection got operated at SP.Koil station. All elements except 230kV Oragadam and 230kV Kalivandapattu got tripped at 230kV S.P.Koil station. Y phase CT and support insulators also got damaged. | 1.MAPS to furnish a detailed report on the tripping of SP Koil MAPS lines 1 & 2 at MAPS end with focus on the correctness of the settings of Main-I & Main-II relays (for primary & back-up protections) on both the lines. 2.MAPS to take steps to provide down-loading facility for DR & EL from Main-I & Main-II relays on all 230 kV lines emanating from MAPS. 3.MAPS, in co-ordination with SP Koil, to carry out PLCC end-to-end testing, on SP Koil MAPS lines 1 & 2, and ensure healthiness of PLCC communication & carrier-aided protection. 4.MAPS to put in service Auto-Reclosure feature on all four 230 kV lines emanating from MAPS by June, 2016. | NPCIL -MAPS | srpcadmin:SRPC: 09/11/2023 15:59:35: NPCIL (MAPS) Mail dated 19.11.2021: The AR scheme is implemented in 230 kV SPKoil-1 line. The performance will be observed during line transients and based on the satisfactory results it is proposed to implement in other three lines Discused in bilateral meeting held on 05.06.2023: No representatives. NPCIL (MAPS) Mail dated 22-06-2023 CVTs of all 230KV lines (Line-1,2,3,4) and BHAVINI tie cable feeder are replaced. Auto reclosure (TDAR)is implemented in Line-1,2,3. Line-4 Acharapakkam feeder AR scheme will be implemented by 03.7.2023 . As per 203rd OCC meeting held on 09.06.2023, LC for Line-4 will be provided on 01.07.2023. | Pending | Pending
69/I/1 | Complete outage of 400kV TPCIL station | 25-10-2017 at 19:33 hrs | 400 kV TPCIL-Nellore PS line-1 got tripped from TPCIL end during fault in 400kV Nellore-Nellore PS line-2. Running units at TPCIL got tripped due to loss of evacuating line. 400kV Nellore PG - Nellore PS line-2 and 400kV TPCIL - Nellore PS line-1 were under shutdown. | TPCIL to configure DEF protection such that it remains in blocked condition as long as Distance Protection is active, and becomes active only when distance protection does not pickup. | TPCIL | srpcadmin:SRPC: 09/11/2023 16:03:28: Discused in bilateral meeting held on 05.06.2023: Yet to inform the new updates. | Pending | Pending
80/II/17 | Tripping of 400 kV Nellore PS SGPL line 1 | 14-11-2018 at 20:20 hrs | Y- ph to earth fault occurred in line due to snapping of GIS to Air bushing conductor at SGPL switchyard. The conductor got grounded such that the fault was being fed by NPS bus and there was earth fault and broken conductor start at SGPL end. NPS end got tripped in Zone-2 due to non-receipt of carrier resulting in a 3-ph trip at NPS. After 500ms, earth fault occurred at SGPL end resulting in Zone-1 operation and 3 phase trip. A/R was not attempted at SGPL end | SGPL to examine the reasons for no-operation / failure of Auto-reclosure from their end for the subject tripping, and furnish an action taken report detailing remedial measures taken to PCSC forum | SGPL | srpcadmin:SRPC: 09/11/2023 16:03:28: Discused in bilateral meeting held on 05.06.2023: Yet to inform the new updates. | Pending | Pending
84/I/5 | Complete outage of 400kV NLC1 Expansion(NLC1EXP) | 05-06-2019at 18:51 hr. | Triggering incident was failure of Y-phase CT of GT-1 (Generator Transformer) at 400kV NLC1EXP. Bus-1 Bus bar protection operated resulting in the tripping of NLC1EXP U1 and 400kV NLC1EXP- Nagapattinam line | 1. NLCIL to check the healthiness of R & B ph CT of Unit-1 at NLC TS1(Exp) and if found unhealthy replace the same alongwith replacement of Y-ph CT. CT replacement plan and timeframe shall be informed to SRPC. 2.NLCIL in coordination with PGCIL(SR-II) to resolve the time syncronisation issues in 230kV NLC TS1(Exp) Nagapattinam line. 3. NLCIL was also requested to investigate the reason of unwarranted DT sent to NLC TS1 (Exp) end from NLC TS2 end and resolve the same. | NLCIL | srpcadmin:SRPC: 09/11/2023 16:09:32: NLCIL mail dated 11.01.2020: 3. Michro mho Relay Testing was carried out at TS2 end on 15/11/19 and found the relay was normal.Proposal has already been initiated to replace distance relays with line differential relays. It is also proposed to replace the PLCC panels at both ends. -- Completed. Discused in bilateral meeting held on 05.06.2023: NO representatives. Yet to inform the new updates. NLCI/TS1EXPN:NLCIL: 24/10/2024 12:33:58: 1. All CT's were replaced and healthiness checked. Unit 1 was synchronized on 07.06.2019. 2. 400 kV NPS feeder M1 relay is time synchronized and M2 (REL521) is periodically manually synchronized. 3. DT signals sent / receive were checked and found normal. NLCI/TS1EXPN:NLCIL: 08/12/2024 10:37:02: 1. Healthiness of all CT's were checked and replaced in Unit 1 and synchronised on 07.06.2019. 2. NPS feeder M1 relay is time synchronised and M2 is periodically synchronised manually. 3. DT signals rceive/sent were checked and found normal. | Complied | Complied
85/II/21 | Tripping of 400kV JSW -Guttur line and 400 kV Kaiga - Guttur line-2 | 05-06-2019 at 18:27 hrs | Y-phase to earth fault occurred in 400kV Kaiga-Guttur line-2. A/r was successful at Guttur end. At Kaiga end A/r was not attempted and breakers got tripped due to operation of Pole discrepancy (1.65 Sec). 400kV JSW-Guttur line tripped on operation of over-voltage at Guttur and direct trip was received at JSW. From DR of Guttur, it is observed that there was swell in R & Y phase voltage for few cycles ' | 1. NPCIL (KGS) is recommended to identify the issue related to unsuccessful A/R attempt of 400kV KaigaGuttur line and non-opening of R-pole CB. It is recommended to check the healthiness of all breakers including breaker timing. 2. Time synchronization of DR and EL at Kaiga end shall be ensured. | NPCIL - KAIGA | srpcadmin:SRPC: 09/11/2023 16:09:32: Discused in bilateral meeting held on 05.06.2023: No representatives, yet to inform the updates. KGS34:NPCIL: 31/05/2024 16:37:00: The issue was related to CB mal-operation. The same was rectified during maintenance in 2023. However, now all the hydraulic breakers are replaced with New motor operated Spring based CB in KAIGA 400kV SWYD. In recent event in 2024 breakers A/R function ensured. Hence requested to close the point. | Complied | Complied
85/IV/7 | Tripping of 400kV Ramadugu-Singareni line | 11-06-2019 at 08:24 hrs | Line tripped due to Direct Trip receive at Ramadugu end | Singareni STPP is recommended to submit a detailed report regarding sending of DT from singareni end that resulted in tripping of 400kV Ramadugu-Singareni line. | Singareni TPP | srpcadmin:SRPC: 09/11/2023 16:09:32: Discused in bilateral meeting held on 05.06.2023: No representatives, yet to inform the updates. | Pending | Pending
90/II/21 | Tripping of 400kV Vallur NCTPS line 1 | 19-Mar-2020 at 12:05 Hr. | Shutdown for 400kV Vallur- NCTPS line-1 was planned from 09 hr. -1700 hr. on 19.03.2020. While closing NCTPS line 1 Earth switch at NTECL end, heavy voltage dip was experienced and all the three running units of Vallur tripped on Low Forward Power Protection at 12:05 hr. Earth switch of the line was closed at Vallur end without opening of remote end breaker, which resulted in three phase to ground fault in 400kV Vallur - NCTPS line-1 at Vallur end. Gen Loss: 1893 MW. | i. NTECL-Vallur to ensure proper communication regarding remote end isolation before closing of earth switch in their switchyard to prevent recurrence of such faults in future. ii. NTECL-Vallur, in coordination with TANGEDCO, to restore communication channel between the NTECL-Vallur and NCTPS and submit a report to SRPC regarding healthiness of the same. | NTECL-Vallur | srpcadmin:SRPC: 09/11/2023 16:22:53: NTECL Vallur Mauil dated 18-04-2023 1.Vallur NCTPS line - 1&2 remote end trip established through protection coupler. OPGW communication is established via Vallur- Alamaty and Alamaty-NCTPS. 2.Differential protection is not in service. Distance Protection is enabled for both Vallur- NCTPS lines 1 and 2. 3. Direct OPGW cable laying work between Vallur and NCTPS is in progress. This work is being carried out by M/s TANTRANSCO communication team. Discused in bilateral meeting held on 05.06.2023: TANTRANSCO Mail dated 19-06-2023 OPGW WORK COMPLETED ON 14.06.2023 & LDP ENABLED IN VALLUR FEEDER_2 14.06.2023 Line clear proposed during July 2023 after getting OCC approval .During that time LDP in Vallur 1 feeder will be enabled Anupama:NTECL: 01/08/2024 15:11:07: Line differential protection enabled in NCTPS -VALLUR Line -2 on 14.06.2023 and shutdown applied for line 1 relay replacement work at NCTPS end on 12th aug 2024. Line 1 differential protection will be enabled after that. BrajeshKumarPandey:NTECL: 20/03/2025 18:28:19: Vallur NCTPS Line_1 Main-2 Relay replacement work in progress at NCTPS end. Differential protection will be enabled after clearance from NCTPS. | Complied | Complied
94/I/11 | Complete Outage of 230 kV BHAVINI | 25-Nov-20 22:53 hrs | As per the information received, all connected lines tripped only at Bhavini end due to Over voltage resulting in complete loss of supply. Details are awaited. | Bhavini to ensure that DR of all protection relays are configured properly with all required protection (digital & analog) signals. | Bhavini | srpcadmin:SRPC: 09/11/2023 16:22:53: Discused in bilateral meeting held on 05.06.2023: BHAVINI representatives have furnished all the reports in Dec, 2022. Yet to inform the recent updates. | Pending | Pending
108/I/7 | Complete Outage of 400kV Gautami CCPP | 23-04-2023 06:35 | . | M/s GVK to approach OEM to resolve the issue of extraction of the files and to enable Auto-reclosure for the 400 kV GVK Gautami-Vemagiri lines at GVK end. | GVK |  | Pending | Pending
112/I/6 | Complete Outage of 400kV/22kV UPCL SS and Tripping of 220kV Bus-1 of 220kV/110kV Kemar SS of KPTCL | 09-10-2023 17:15 | The triggering incident was Y-N fault in 400kV UPCL Hebbanahalli Line-2. Immediately, UPCL unit-2 tripped on SPS operation. At 16:54hrs, 400kV UPCL Hebbanahalli Line-1 tripped on R-N fault. Subsequently, UPCL Unit-1 tripped on over frequency. Tripping of units and lines resulted in complete outage of 400kV/22kV UPCL SS. Since, 220kV Kemar Bus-1 was radially fed from 400kV/220kV UPCL SS, this resulted in loss of supply to 220kV Bus-1 of 220kV/110kV Kemar SS. | UPCL to take up the matter in the OCC meeting for discussion about operational issues and to review/finalize the SPS. | UPCL |  | Pending | Pending
112/III/1 | TRIPPING OF 400 kV NELLORE - SPDR-2 | 26-09-2023 04:16 | The triggering incident was Y-N fault in 400kV Nellore Sriperumbudur Line-2. During fault after A/R dead time, the Main CB failed to open, and the line tripped on the PD relay. | SRLDC was requested to perform the trans play of the event in order to analysis the sequence of operations. The simulation results shall be shared to SRPC. | SRLDC | srpcadmin:SRPC: 17/02/2024 16:06:00: As per the information from site and VMS system fire was observed in 80MVAR reactor at the first instance and subsequently 400kV Nellore-Sriperumbdur line-2 charging attempted without line reactor at Nellore at 06:42Hrs/26.09.2023. The same was attempted in PSCAD, however similar results were not observed from what is as per the DR from the event | Complied | Pending
112/III/4 | TRIPPING OF 400 kV VEMAGIRI - SIMHADRI 1 AND 2 | 29-09-2023 12:03 | As per the reports submitted, while changing the bay control unit of Tie Bay of 400kV Vemagiri Simhadri Line-1&2 LBB trip persisted and gave trip signals to both line-1&2. DT was sent to remote ends and the line tripped at both ends. | NTPC Simhadri to follow SOP during BCU change over activities. | NTPC- Simhadri |  | Pending | Pending
113/I/4 | Complete Outage of 220kV/66kV HN_Pura_SS of KPTCL and 220kV/33kV Gopalpura SS of Suzlon_KA | 27-10-2023 04:05 | As per the reports submitted, the triggering incident is the R-N fault in 220kV Gopalpura-HN-Pura-1 line and AR was not available. At HN-Pura the fault was sensed in Z1 and 3ph tripped. At Gopalpura end, the fault was sensed in Z2 carrier aided protection and only R-ph opened and Y, B phases were in closed condition due to air pressure low/breaker lockout condition and after around 100ms from Z1 trip command at Gopalpura end, LBB operated and all the feeders connected to Gopalpura end tripped other than in 220kV Gopalpura-Hassan line only tripped in R-phase. Y-B phases is suspected to be healthy in the bus at Gopalpura through Hassan line even after 5sec from the fault which can conclude that PD did not operate. This led to the complete outage of 220kV HN-Pura and 220kV Gopalpura stations | 1.M/s Suzlon to rectify the compressor issue at Gopalpura and submit a detailed report. 2.M/s Suzlon to furnish the detailed settings of PD relay to SRPC & SRLDC. 3.M/s Suzlon to enable the DR facility for all lines at Gopalpura and submit a detailed report. | M/s Suzlon |  | Pending | Pending
115/III/16 | 765KV-WARANGAL(NEW)-CHIL-AKALURIPETA-1 | 21-01-2024 17:35 | During the fault in 765KV CUDDAPAH_CHILAKURIP-ETA-2 line, 765KV-WARAN-GAL(NEW)-CHILAKALURIP-ETA-1 line tripped only at WA-RANGAL(NEW) end | WKTL to trans-play the event and furnish the findings to SRPC & SRLDC. Also sug-gested to review the settings. | WKTL |  | Pending | Pending
115/IV/4 | 230KV-NEYVELI TS II-KARAIKAL-1 | 20-01-2024 19:12 | A/R Failure | NLCIL to submit the corrective measures taken. | NLCIL | ARUMUGAM:PED: 29/02/2024 11:30:26: PED: P & C wing of TANTRANSCO Ltd had consented to visit the station on 10.02.2024. But, they could not make it as assured in view of their busy schedule in their own state. However, they agreed to attend the issue in the first fortnight of March 2024 ARUMUGAM:PED: 01/04/2024 07:03:39: P&C wing of TANTRANSCO Ltd is yet to visit Karaikal Auto SS. They are still at busy schedule in their own state. However, they have agreed to attend the issue after the General Lok Sabha Election 2024 which scheduled to be held in Puducherry & Tamil Nadu on 19th April, 2024. ARUMUGAM:PED: 06/05/2024 18:50:09: PED: P&C wing of TANTRANSCO Ltd visited Karaikal Auto SS on 06.05.2024 and revised the A/R setting of 230KV Neyveli - Karaikal Line. ARUMUGAM:PED: 07/08/2024 11:52:46: P&C wing of TANTRANSCO Ltd revised A/R setting of 230KV Neyveli - Karaikal Line at Karaikal on 06.05.2024. For the Zone-I, Single Phase to Ground fault occured on 20.05.2024 at 13:49hrs on 230KV Neyveli - Karaikal Line, A/R operated successfully at both ends. Hence, the recommendation may be treated as complied. | Complied | Complied
116/I/2 | Complete outage of 220KV Renew_Surya_Ojas_Koppal | 14-01-2024 08:40 | As per the reports submitted the triggering incident is the failure of R phase BPI post insulator Failure in 201Bay causing fault in 220kV RSOPL Koppal line. At both ends, line differential protection operated and the line tripped. Tripping of the only connected line resulted in a complete outage of 220kV Renew_Surya_Ojas_Koppal. | DR at RSOPL to be configured properly. | M/s RSOPL |  | Pending | Pending
116/I/2 | Complete outage of 220KV Renew_Surya_Ojas_Koppal | 14-01-2024 08:40 | As per the reports submitted the triggering incident is the failure of R phase BPI post insulator Failure in 201Bay causing fault in 220kV RSOPL Koppal line. At both ends, line differential protection operated and the line tripped. Tripping of the only connected line resulted in a complete outage of 220kV Renew_Surya_Ojas_Koppal. | M/s RSOPL to take up the periodical maintenance. | M/s RSOPL |  | Pending | Pending
116/I/4 | Complete Outage of 400kV HNPCL Generating station | 17-01-2024 08:40 | At 400kV HNPCL station, 2/2 Bus Bar scheme is present with P741 CU and P743 PU in 2 sets. The Bus bar protection will only operate and give a trip command to all the main breakers when both the bus bar sense the fault and give the signal to the PU to trip | HNPCL may explore the replacement of the disc insulators with SRC insulators. | M/s HNPCL |  | Pending | Pending
116/I/4 | Complete Outage of 400kV HNPCL Generating station | 17-01-2024 08:40 | At 400kV HNPCL station, 2/2 Bus Bar scheme is present with P741 CU and P743 PU in 2 sets. The Bus bar protection will only operate and give a trip command to all the main breakers when both the bus bar sense the fault and give the signal to the PU to trip | HNPCL to implement the Independent BUSBAR Main-1 and Main-2 relays in consultation with the OEM, and to inform SRPC and SRLDC after the implementation. | M/s HNPCL |  | Pending | Pending
116/I/4 | Complete Outage of 400kV HNPCL Generating station | 17-01-2024 08:40 | At 400kV HNPCL station, 2/2 Bus Bar scheme is present with P741 CU and P743 PU in 2 sets. The Bus bar protection will only operate and give a trip command to all the main breakers when both the bus bar sense the fault and give the signal to the PU to trip | HNPCL to increase the frequency of hot line washing, Conduct PID testing of disc insulators (tension and suspension). | M/s HNPCL |  | Pending | Pending
116/I/4 | Complete Outage of 400kV HNPCL Generating station | 17-01-2024 08:40 | At 400kV HNPCL station, 2/2 Bus Bar scheme is present with P741 CU and P743 PU in 2 sets. The Bus bar protection will only operate and give a trip command to all the main breakers when both the bus bar sense the fault and give the signal to the PU to trip | HNPCL to take up with OEM regarding the issues of CU-B circuitry and the non-operation of Bus- 1 Busbar protection PU relay. | M/s HNPCL |  | Pending | Pending
116/II/1 | Tripping of 230kV Bus-2 of 230kV Bhavini Station | 28-11-2023 19:10 | As per the reports submitted, the triggering incident was an R-N fault in 230kV Bus-2 at the CB (in open condition) compartment of Bay-5 of 230kV Bhavini Station.The isolator connecting the 230kV Bus-2 and the circuit breaker remained in the closed position during the event, as it was meant to energize the breaker according to the planned schedule. With the R-N fault in the Bus-2 zone, immediately, BBP operated and all the lines connected to the bus tripped. This led to the tripping of 230kV Bus-2 of 230kV Bhavini Station | BHAVINI to monitor the status of the GIS equipment. | M/s BHAVINI |  | Pending | Pending
117/III/12 | Tripping of 400kV Ramagundam - Chandrapur Line-1&2 | 19-03-2024 10:01 & 20-03-2024 16:36 | L-G fault in 400kV Ramagundam Chandra- pur Line-2. B-pole opened but A/R failed to open causing the line to trip on PD. 400kV Ramagundam Chandrapur Line-1 also tripped as both these lines were on the same dia | NTPC Ramagundam to connect 400kV Ramagundam- Chandrapur D/c lines in two different DIA instead of same DIA. | NTPC- Ramagundam | RSTPS:NTPC: 05/03/2025 11:16:12: proposal for swapping is with Powergrid | Complied | Complied
118/I/8 | Complete outage of Ayana_Six_Koppal | 18-04-2024 17:27 | - | M/s Ayana Six to disable the over current protection for 220kV feeder and to furnish the detailed report on the incident. | M/s Ayana Six |  | Pending | Pending
118/III/6 | 230KV-NEYVELI_TS_II - KA- DALANGUDI | 07-04-2024 15:52 | 230KV-NEYVELI_TS_II - KADALANGUDI line tripped only at Neyveli end on zone-1 protec- tion for B-N fault in 230kV Kadalangudy Kumba- Konam Line. A/R was successful and the 230kV Kadalangudy Kumbakonam Line line was hold- ing at both ends | NLCIL TS-2 to review the Zone reach settings. | NLCIL TPS II | NLCI/TS2:NLCIL: 07/11/2024 18:53:46: According to SLD submitted by Kadalangudi SS to the trip portal, the distance is mentioned as 89KM. The implemented settings at Neyveli TPS is 94.5KM. When a transplay conducted in spare relay wirh 89KM distance, the relay did not mal-operate. A mail dated 07.05.2024has been sent to SRPC in this reg for resolving the issue. NLCI/TS2:NLCIL: 05/04/2025 15:26:06: Relay reach settings modified and relay testing done found in order. kept in observation. | Complied | Complied
118/III/14 | 765KV-MAHESHWARAM_PG- WARANGAL(NEW)-2 | 21-04-2024 11:35 | While fine tuning of CSD a,86B Master trip relay 765KV-MAHESHWARAM_PG-WARAN-GAL(NEW)-2 was burnt at Warangal end and the line tripped only at Warangal end. | M/s WKTL to furnish the report after analysis. | M/s WKTL |  | Pending | Pending
118/IV/3 | 765KV-WARANGAL(NEW)- WARORA-2 | 12-04-2024 23:43 | Warangal(New)(Multiple A/R attempts were observed) | M/s WKTL to furnish the report after analysis. | M/s WKTL |  | Pending | Pending
118/I/8 | Complete outage of Ayana_Six_Koppal | 18-04-2024 17:27 | Complete outage of 220kV Ayana | M/s Ayana Six to disable the over current protection for 220kV feeder and to furnish the detailed report on the incident. | M/s Ayana |  | Pending | Pending
119/I/9 | Complete Outage of 230kV Ettayapuram Solar Plant | 10-05-2024 15:12 | As per the reports submitted, the triggering incident was the R-N fault in the line. At NTPC Ettyapuram end fault was sensed in Diff trip and since AR is disabled 86 relay operated and 3ph tripped and 86 trip was extended to DT signal send. At TTGS end the fault was sensed in Diff trip and R-pole opened and subsequently DT received and 3ph tripped. Tripping of the only available feeder led to the Complete Outage of 230kV NTPC Ettayapuram Solar Plant and generation loss of 60 MW | SRLDC to discuss the possibility of enabling of auto closure for RE plants with NLDC/Grid-India and update the forum | SRLDC | srpcadmin:SRPC: 05/07/2024 09:03:33: As per the 119th PCSC meeting, it was noted that "SRLDC to discuss the possibility of enabling of auto closure for RE plants with NLDC/Grid-India and update the forum" as per the recommendations (119/I/9 and 119/I/13). The same was discussed with NLDC/Grid-India and the following observations were noted Auto reclose for RE plants can be enabled for single line connected stations. However, OEM consultation and approval is requisite for enabling auto reclose. ArthiV~1776856274:SRLDC: 02/07/2025 19:01:16: The issue was discussed during 120th PCSC on 05-07-2024 and SRLDC has provided the opinion for the same. Proof attached. The point may be closed. ArthiV~1776856274:SRLDC: 02/07/2025 19:02:04: The issue was discussed during 120th PCSC on 05-07-2024 and SRLDC has provided the opinion for the same. Proof attached. The point may be closed. | Complied | Complied
119/I/13 | Complete Outage of 230kV JSW_Vilathikulam_Wind | 13-05-2024 12:40 | At TTGS end, the fault was sensed by Line Differential Protection and B-pole opened. After around 1 sec B pole close was observed without any current increase and AR locked out leading to 3ph trip. At JSW Vilathikulam, the fault was sensed by Line Differential Protection and since AR was disabled at JSW Vilathikulam end led to the 3ph trip of the line. Tripping of the only available line led to the Complete Outage of 230kV JSW_Vilathikulam_Wind | SRLDC to discuss the possibility of enabling of auto reclosure for the lines connected to RE plants with Grid-India, NLDC and update the forum | SRLDC | srpcadmin:SRPC: 05/07/2024 09:03:33: As per the 119th PCSC meeting, it was noted that "SRLDC to discuss the possibility of enabling of auto closure for RE plants with NLDC/Grid-India and update the forum" as per the recommendations (119/I/9 and 119/I/13). The same was discussed with NLDC/Grid-India and the following observations were noted Auto reclose for RE plants can be enabled for single line connected stations. However, OEM consultation and approval is requisite for enabling auto reclose. ArthiV~1776856274:SRLDC: 02/07/2025 19:01:16: The issue was discussed during 120th PCSC on 05-07-2024 and SRLDC has provided the opinion for the same. Proof attached. The point may be closed. ArthiV~1776856274:SRLDC: 02/07/2025 19:02:04: The issue was discussed during 120th PCSC on 05-07-2024 and SRLDC has provided the opinion for the same. Proof attached. The point may be closed. | Complied | Complied
119/III/9 | 765KV-Warangal (NEW)-Warora-2 | 08-05-2024 18:42 | 765KV Warangal (New)-Warora ckt-2 main and Tie CB opened while checking DC Earth Fault | WKTL to furnish a detailed report after analyzing the tripping incident. | M/s WKTL | srpcadmin:SRPC: 05/07/2024 09:01:58: WKTL vide mail dated 04.07.2024 has furnished the report | Complied | Complied
120/I/2 | Complete outage of 220kV Ostro Kannada | 18-05-2024 20:10 | 220kV Ostro Kannada is being radially connected through 220kV Hiriyur Ostro kannada line. As per the reports submitted, the triggering incident was operation of over voltage stage-1 protection at Ostro Kannada end and DT was sent to Hiriyur end in the line and the line tripped. Tripping of the only connected line resulted in complete outage of 220kV Ostro Kannada | 1.M/s Ostro Kannada to disable under voltage, over voltage, over current, under frequency and over frequency settings | M/s Ostro Kannada |  | Pending | Pending
120/I/2 | Complete outage of 220kV Ostro Kannada | 18-05-2024 20:10 | 220kV Ostro Kannada is being radially connected through 220kV Hiriyur Ostro kannada line. As per the reports submitted, the triggering incident was operation of over voltage stage-1 protection at Ostro Kannada end and DT was sent to Hiriyur end in the line and the line tripped. Tripping of the only connected line resulted in complete outage of 220kV Ostro Kannada | M/s Ostro Kannada to implement logic when distance picks up DEF should be dropped. | M/s Ostro Kannada |  | Pending | Pending
120/I/2 | Complete outage of 220kV Ostro Kannada | 18-05-2024 20:10 | 220kV Ostro Kannada is being radially connected through 220kV Hiriyur Ostro kannada line. As per the reports submitted, the triggering incident was operation of over voltage stage-1 protection at Ostro Kannada end and DT was sent to Hiriyur end in the line and the line tripped. Tripping of the only connected line resulted in complete outage of 220kV Ostro Kannada | M/s Ostro Kannada to rectify the A/R logic issue at Hiriyur end. | M/s Ostro Kannada |  | Pending | Pending
120/II/6 | Tripping of 400kV Bus-1&2 of 765kV/400kV Warangal_New SS of WKTL | 26-05-2024 14:48 | As per the reports submitted, the triggering incident was B-N fault in 400kV-Warangal-Warangal(New)-2. At Warangal end, the fault was sensed in Zone-1 and the line tripped. At Warangal(New ) end the line was holding. At the same time, 765KV/400KV Warangal (New)-ICT-1 & 2 tripped on highest earth fault protection. Subsequently, the same fault was sensed as R-B fault in 400kV-Warangal-Warangal(New)-1 at Warangal(New) end and evolved from Ir-2.2kA Ib-2.3kA to Ir-2.7kA, Ib-5.6kA in 250ms. This fault was sensed in Zone-1 and the line tripped only at Warangal(New) end. Tripping of all elements connected to 400kV Bus-1&2 resulted in loss of power supply to 400kV Bus-1&2 of 765kV/400kV Warangal_New SS of WKTL. | M/s WKTL to furnish the detailed report in the prescribed format. | M/s WKTL |  | Pending | Pending
120/II/6 | Tripping of 400kV Bus-1&2 of 765kV/400kV Warangal_New SS of WKTL | 26-05-2024 14:48 | As per the reports submitted, the triggering incident was B-N fault in 400kV-Warangal-Warangal(New)-2. At Warangal end, the fault was sensed in Zone-1 and the line tripped. At Warangal(New ) end the line was holding. At the same time, 765KV/400KV Warangal (New)-ICT-1 & 2 tripped on highest earth fault protection. Subsequently, the same fault was sensed as R-B fault in 400kV-Warangal-Warangal(New)-1 at Warangal(New) end and evolved from Ir-2.2kA Ib-2.3kA to Ir-2.7kA, Ib-5.6kA in 250ms. This fault was sensed in Zone-1 and the line tripped only at Warangal(New) end. Tripping of all elements connected to 400kV Bus-1&2 resulted in loss of power supply to 400kV Bus-1&2 of 765kV/400kV Warangal_New SS of WKTL. | M/s WKTL to rectify the A/R issue at PGCIL end of the line. | M/s WKTL |  | Pending | Pending
120/II/6 | Tripping of 400kV Bus-1&2 of 765kV/400kV Warangal_New SS of WKTL | 26-05-2024 14:48 | As per the reports submitted, the triggering incident was B-N fault in 400kV-Warangal-Warangal(New)-2. At Warangal end, the fault was sensed in Zone-1 and the line tripped. At Warangal(New ) end the line was holding. At the same time, 765KV/400KV Warangal (New)-ICT-1 & 2 tripped on highest earth fault protection. Subsequently, the same fault was sensed as R-B fault in 400kV-Warangal-Warangal(New)-1 at Warangal(New) end and evolved from Ir-2.2kA Ib-2.3kA to Ir-2.7kA, Ib-5.6kA in 250ms. This fault was sensed in Zone-1 and the line tripped only at Warangal(New) end. Tripping of all elements connected to 400kV Bus-1&2 resulted in loss of power supply to 400kV Bus-1&2 of 765kV/400kV Warangal_New SS of WKTL. | M/s WKTL to review the Earth Fault Stage-2 Protection of the ICTs | M/s WKTL |  | Pending | Pending
120/III/5 | Tripping of Telangana STPP Unit-1&2 | 04-06-2024 14:45 | For a through fault in 400kV Ramadugu Medaram Line-1, Telangana STPP Unit-1&2 tripped on Differential Protection | NTPC TSTPP to conduct CT & Relay testing | NTPC-TSTPP | RSTPS:NTPC: 20/03/2025 09:36:13: conducted CT testing and relay testing .Reports found ok. VSCGUPTAMUKKAMALA:NTPC: 04/04/2025 17:51:42: conducted CT testing and relay testing .Reports found ok. | Complied | Complied
120/VI/1 | 400kV Jsw Toranagallu BPS-1 | 02-06-2024 01:52 | Jsw Toranagallu D/R Time sync issue | M/s JSWEL to rectify the DR time synchronisation | M/s JSWEL | JSW@ENERGY1:JSWE: 30/06/2025 16:14:50: Purchase order placed. Material expected by 31.07.25 JSW@ENERGY1:JSWE: 12/08/2025 16:14:06: New GPS clock installed and Time sync is in order JSW@ENERGY1:JSWE: 12/08/2025 16:17:53: New GPS clock installed and Time sync is in order | Complied | Complied
122/I/2 | Complete Outage of 230kV JSW_Vilathikulam Wind Station | 18-07-2024 12:14 | As per JSW email dated 22-07-2024, it was mentioned that P546 relay issued trip while changing settings and configuration. It was further mentioned that,The measurement mode was kept as Ph to N rather than Ph to Ph. The relay generated the tripping command, as in the relay configuration under voltage protection, which was not removed from the tripping logic. Tripping is not in order | M/s JSWEL to furnish the Compliance reporT. | M/s JSW -Vilathikulam |  | Pending | Pending
122/I/2 | Complete Outage of 230kV JSW_Vilathikulam Wind Station | 18-07-2024 12:14 | As per JSW email dated 22-07-2024, it was mentioned that P546 relay issued trip while changing settings and configuration. It was further mentioned that,The measurement mode was kept as Ph to N rather than Ph to Ph. The relay generated the tripping command, as in the relay configuration under voltage protection, which was not removed from the tripping logic. Tripping is not in order | M/s JSWEL to review the protection settings completely in both Main relays | M/s JSW -Vilathikulam |  | Pending | Pending
122/I/10 | Multiple trippings at 220kV/33kV Mytrah and Complete Outage of 230kV/33kV JSW_Vilathikulam, and 230kV/33kV JSW_Savalperi | 10-08-2024 14:49 | The triggering incident was a Y-N fault caused by a bird strike on the 33kV bay BCU311 LA of a 33kV feeder at Mytrah. At Mytrah , 220kV/33kV PTR-1&2 tripped on Earth fault protection | JSWEL to verify the protection settings at JSWEL end and confirm to be in line with SR Protection Protocol. | M/s JSW -Vilathikulam |  | Pending | Pending
122/I/10 | Multiple trippings at 220kV/33kV Mytrah and Complete Outage of 230kV/33kV JSW_Vilathikulam, and 230kV/33kV JSW_Savalperi | 10-08-2024 14:49 | The triggering incident was a Y-N fault caused by a bird strike on the 33kV bay BCU311 LA of a 33kV feeder at Mytrah. At Mytrah , 220kV/33kV PTR-1&2 tripped on Earth fault protection | Mytrah to furnish the detailed report regarding this event. | M/s Mytrah |  | Pending | Pending
122/I/11 | Complete Outage of 230kV/33kV GRT Solar Station | 13-08-2024 13:16 | As per the reports submitted, the triggering incident was R-N fault in 230kV TTGS GRT line. At TTGS end, the fault was sensed in differential protection and R-pole opened. A/R operated after 800ms and the line was holding. At GRT end, it is suspected that highset earth fault protection operated(IN= 1147A and IN>2 start was observed from EL). All three poles tripped at GRT end and the snap of the EL is attached below. Tripping of only connected line led to complete outage of 230kV GRT. | GRT to furnish the detailed report regarding this event. | M/s GRT |  | Pending | Pending
122/I/11 | Complete Outage of 230kV/33kV GRT Solar Station | 13-08-2024 13:16 | As per the reports submitted, the triggering incident was R-N fault in 230kV TTGS GRT line. At TTGS end, the fault was sensed in differential protection and R-pole opened. A/R operated after 800ms and the line was holding. At GRT end, it is suspected that highset earth fault protection operated(IN= 1147A and IN>2 start was observed from EL). All three poles tripped at GRT end and the snap of the EL is attached below. Tripping of only connected line led to complete outage of 230kV GRT. | GRT to verify the protection settings at GRT end and confirm to be in line with SR Protection Protocol. | M/s GRT |  | Pending | Pending
122/II/8 | Tripping of 400kV Bus-2 of 400kV/220kV UPCL | 09-08-2024 23:48 | As per the reports submitted, while de-synchronising UPCL Unit-2, The R and Y poles of the 4-852 Tie breaker opened at 23:47:31.777 hrs, but the B phase pole failed to open. Due to this, the Tie CB LBB was initiated, causing the Tie LBB to operate from the protection relay at 23:47:32.312 hrs, which extended a trip to both main breakers, 4-752(UPCL Unit-2) and 4-952(400kV Hebbanahalli Line-2). As a result, the 4-952 Breaker should have opened, but only the R and Y poles of the main breaker opened, while the B pole did not. Since the B phase pole of the main breaker 4-952 did not open after the LBB initiation, the Bus bar protection for the 400kV Bus-2 was operated at 23:47:32.533 hrs, leading to the tripping of all connected breakers: 4-352, 4-652, and 4-1252. | UPCL to monitor the trip mechanism of all breakers and practice regular maintenance | UPCL /ADANI |  | Pending | Pending
123/III/1 | 220KV-NP_KUNTA PSS2-NP_KUNTA-2 | 22-08-2024 19:25 | Line tripped on differential protection maloperation while carrying out relay testing at APSPCL end. | APSPCL to take proper SOP while carrying out testing of the relay | APSPCL |  | Pending | Pending
123/IV/5 | 765KV-MAHESHWARAM_PG-WARANGAL(NEW)-2 | 05-09-2024 13:03 | WKTL: 1. Non operation of A/R needs to be reviewed. 2. DR of M2 is not available. | M/s WKTL to furnish the detailed report regarding the non-operation of A/R. | M/S WKTL |  | Pending | Pending
123/IV/11 | 230KV-NEYVELI_TS_II-KADALANGUDI | 20-09-2024 15:45 | NLC TS II: 1. A/R not operated. | NLCIL TS-II to furnish the detailed report regarding the non-operation of A/R | NLCIL TS-II | NLCI/TS2:NLCIL: 01/11/2024 15:11:05: AR not enabled in relay. Phase segregated LBB to be retrofitted. To carry out the work 3 days LC shall be approved. The same has been conveyed in special meeting on 25/10/2024 at Neyveli | Complied | Complied
123/VI/10 | VALLUR - 400KV | 02-09-2024 22:20 | DR TIME SYNC ISSUE | NTECL to furnish the report regarding the action taken to rectify the DR time syn issue at Vallur station | NTECL | BrajeshKumarPandey:NTECL: 19/03/2025 17:34:45: GPS Server antenna and cable procurement in progress. BrajeshKumarPandey:NTECL: 20/03/2025 18:05:34: GPS Server antenna and cable procurement in progress. Target 31.05.2025 | Complied | Complied
123/VI/12 | 400KV-NCTPS_STAGE_II-VALLUR-2 | 03-09-2024 20:26 | DR TIME SYNC ISSUE | NTECL to furnish the report regarding the action taken to rectify the DR time syn issue at Vallur station | NTECL | BrajeshKumarPandey:NTECL: 19/03/2025 17:31:06: Antenna and cable procurement in progress. expected to complete by 31.05.2025 | Complied | Complied
124/III/13 | 400KV-KAIGA-GUTTUR-2 | 17-10-2024 23:25 | As per the reports submitted, the triggering incident was fault current in B-phase of 1.07kA in 400kV Kaiga Guttur Line-2. At Kaiga end, the fault was sensed in zone-3 and the line tripped on SOTF. At Guttur end, line tripped on receiving DT. | NPCIL KGS to furnish the updates on the findings of this event. | NPCIL-KAIGA | KGS34:NPCIL: 02/12/2024 16:37:07: Relay settings were reviewed and found that the SOTF was enabled for all the 3 zones viz. Z-1; Z-2 & Z-3. Hence, the line tripped on SOTF. It has been decided to disable the SOTF for Z-3. KGS34:NPCIL: 02/12/2024 18:08:04: Requested to CLOSE the point | Complied | Complied
124/III/13 | 400KV-KAIGA-GUTTUR-2 | 17-10-2024 23:25 | As per the reports submitted, the triggering incident was fault current in B-phase of 1.07kA in 400kV Kaiga Guttur Line-2. At Kaiga end, the fault was sensed in zone-3 and the line tripped on SOTF. At Guttur end, line tripped on receiving DT. | NPCIL KGS to review the settings and enable operation of SOTF for only Zone-1 and Zone-2. | NPCIL-KAIGA | KGS34:NPCIL: 02/12/2024 16:40:08: SOTF settings in protection relay has been modified. Now SOTF has been disabled for Zone-3 protection and kept enabled for only Zone-1 & Zone-2. KGS34:NPCIL: 02/12/2024 18:08:04: Requested to CLOSE the point | Complied | Complied
124/IV/6 | 230KV-NEYVELI_TS_II-KADALANGUDI | 10-10-2024 13:05 | As per the reports submitted, the triggering incident was YN fault in the line. At Neyveli end the line tripped on operation of Zone-1 distance protection but the line tripped on three phases. A/R did not get operated. At Kadalangudi end the line tripped on operation of Zone-1 distance protection. A/R operated but again the line tripped due to fault within the reclaim time | NLCIL to furnish the action plan taken regarding this event | NLC TS-II | NLCI/TS2:NLCIL: 04/04/2025 15:56:17: Since phase segregated LBB not available A/R disabled. Retrofitting of the LBB relay is pending due to non-availability of continuous 2 days outage. Once relay retrofit completed A/R will be enabled. NLCI/TS2:NLCIL: 07/11/2025 10:12:32: "Phase segregated LBB relay has been retrofitted. A/R function tested. The same shall be enabled by getting concurrence from the other end. " | Complied | Complied
124/IV/7 | 400KV-KOPPAL-KUDGI_PG-2 | 12-10-2024 03:33 | As per the reports submitted, the triggering incident was YN fault in the line. At Kudgi end the line tripped on operation of Zone-1 distance protection. A/R operated successfully and the line was holding. At Koppal end the line tripped on operation of Zone-1 distance protection. A/R did not get operated. | KNTL to furnish the action plan taken regarding this event | M/s KNTL |  | Pending | Pending
124/VI/13 | 220KV-KOPPAL-Ayana_Six_Koppal-1 | 16-10-2024 15:59 | Ayana_Six_Koppal - 220KV | Ayana Six, Koppal to furnish the action plan taken regarding this event | M/s Ayana Koppal |  | Pending | Pending
125/I/3 | Complete Outage of 220kV Vena_GadagPS | 22-10-2024 11:08 | As per the reports submitted, the triggering incident was tripping of 220kV Gadag Vena line at Gadag end on receiving DT from Vena end. Tripping of the only connected line to complete outage of 220kV Vena_Gadag PS. | M/s Vena Energy to check the DT Send philosophy employed for orderliness and submit a detailed report on the event. | M/s Vena Energy |  | Pending | Pending
125/I/4 | Complete Outage of 220kV Betam Wind | 31-10-2024 15:52 | As per the reports submitted, the triggering incident was R-N fault in 220kV TTGS Betam line and the line tripped. Tripping of the only connected line led to complete outage of 220kV Betam Wind SS. | M/s Betam to furnish the detailed report on the incident, and ensure to provide Phase Discrimination and Re-Trip for LB Protection operation. | M/s Betam |  | Pending | Pending
125/I/8 | Complete Outage of 230kV/33kV Karur_JSW_Dharapuram Wind Station. | 04-11-2024 06:54 | The triggering incident was failure of the 230kV dropper Bus gantry insulator connected to Bus-2 at 230kV/33kV Karur_JSW_Dharapuram Wind Station. Immediately, the2 30kV Bus-2 BBP operated at 230kV/33kV Karur_JSW_Dharapuram Wind Station and DT was sent to remote end. Trippping of the only connected line resulted in complete outage of 230kV/33kV Karur_JSW_Dharapuram Wind Station. | M/s JSW Dharapuram to carry out the scanning of all insulators in the switchyard. | M/s JSW Dharapuram |  | Pending | Pending
125/I/9 | Complete Outage of 220kV Tirumani. | 05-11-2024 13:22 | As per the reports submitted, the triggering incident was RY fault in the line due to jumper damage in 220 kV line CT in the 220kV Pavagada_PG- Tirumani line-2. At both ends, line differential protection operated and the line tripped. Tripping of only connected line led to complete outage of 220kV Tirumani. | KSPDCL to take steps to provide Auto Reclosure on all its 220kV lines. | KSPDCL | ceokspdcl:KSPDCL: 03/04/2025 15:18:14: Action will be taken to enable the autoreclosure settings in coordination with KPTCL RT team. ceokspdcl:KSPDCL: 05/07/2025 16:30:15: Action initiated to enable AR settings in coordination with KPTCL RT team. | Pending | Pending
125/IV/7 | Tripping of 220KV-NP_KUNTA-NP_KUNTA PSS1-1 | 14-11-2024 14:56 | As per the reports submitted, the triggering incident is the Y-N fault in the line. At NP Kunta end (PGCIL) the fault was sensed in LDP with If- 21kA and at a distance of 2 km, AR operated and ToR. At NP Kunta PSS end, fault was sensed in LDP and AR is suspected to not operate and could not be concluded as APSPCL did not furnish DR. This led to the tripping of the line. | APSPCL to update the status of Auto reclose. | APSPDCL |  | Pending | Pending
125/VI/9 | 230KV-KARUR-KARUR_JSW_Dharapuram-1 | 04-11-2024 06:54 | DR Time Synchronization Issues Related Events at KARUR_JSW_Dharapuram 230KV | M/s JSW Dharapuram to furnish the action report in this regard | M/s JSW Dharapuram |  | Pending | Pending
125/VI/14 | 400KV-RTPS-BTPS-1 | 15-11-2024 23:55 | DR Time Synchronization Issues Related Events at RTPS - 400KV | KPCL to furnish the action report in this regard | KPCL |  | Pending | Pending
125/VI/15 | 400KV-BHADRAVATHI-RAMAGUNDAM-2 | 18-11-2024 19:04 | DR Time Synchronization Issues Related Events at RAMAGUNDAM - 400KV | NTPC Ramagundam to furnish the action report in this regard | NTPC Ramagundam | RSTPS:NTPC: 05/03/2025 11:16:12: Done.Completed | Complied | Complied
126/I/2 | Complete Outage of 400kV GREENKO_PSP | 23-11-2024 11:51 | During relay testing works, 400kV Bus-3 BBP operated resulting in the complete outage of 400kV GREENKO_PSP due to the tripping of the only connected 400kV Kurnool Greenko_PSP line. | M/s Greenko to follow the SOP and to furnish the revised SOP to SRPC & SRLDC. | M/s Greenko | kvchenchaiah:GREENKO: 04/02/2025 17:14:13: As per SOP we are doing all testing and Operations. kvchenchaiah:GREENKO: 21/02/2025 16:34:55: SOP is prepared & updated for Operation & Maintenance AP01 IREP PSP & CPSS GIS 400kV & Same was shared via email to Srldc & Srpc dated 21-02-2025. | Complied | Complied
126/I/5 | Complete Outage of 400kV/110kV Thappagundu SS of TANTRANSCO | 03-12-2024 11:00 | During antecedent conditions, 400kV Annaikadavu Thappagundu line-2 was under outage. The triggering incident was RN fault in 400kV Annaikadavu Thappagundu line-1. Due to loss of both 400kV connected lines there was complete outage of 400kV/110kV Thappagundu SS of TANTRANSCO. | TANTRANSCO to furnish the anti-Islanding protection Scheme available with the RE stations, connected downstream. | SRLDC | cepc:TANTRANSCO: 03/02/2025 16:16:36: will be complied cepc:TANTRANSCO: 04/03/2025 12:16:56: Uniform Setting details awaited from SRLDC cepc:TANTRANSCO: 05/04/2025 15:12:49: Anti islanding Setting awaited from SRLDC cepc:TANTRANSCO: 04/06/2025 13:45:11: Anti islanding setting awaited from SRLDC cepc:TANTRANSCO: 01/07/2025 16:10:54: Anti islanding setting awaited from SRLDC cepc:TANTRANSCO: 06/08/2025 16:25:17: Islanding setting awaited from SRLDC | Pending | Pending
126/II/5 | Tripping of 400kV Bus-1 at 400/220kV Jindal TPS | 02-12-2024 20:52 | The triggering incident is the breaker flashover (Unit side to Grid side external breaker flashover) in Unit-6 during synchronizing the unit. Due to the breaker flash-over Y-pole started conducting even when the breaker was open leading to LBB operation and tripping of 400kV Bus-1 at 400/220kV Jindal TPS. | M/s JSWEL to enable retrip feature (time delay of 100ms) for LBB operation. | M/s JSWEL | JSW@ENERGY1:JSWE: 05/03/2025 11:01:29: During Bus bar stability while commissioning new transformer, settings will be updated JSW@ENERGY1:JSWE: 30/06/2025 16:09:29: Re-trip enabled | Complied | Complied
126/II/6 | Tripping of 400kV Bus-2 of 400/220kV Jindal TPS | 02-12-2024 21:35 | The triggering incident is the Y-N fault after isolator and before the breaker at TR-18 of Jindal TPS (within the bus zone). During the previous event at 20:52 Hrs all the elements connected to 400kV Bus-1 tripped including TR-18 breaker. For the restoration of TR-18, the isolator to Bus-2 was closed on a suspected Y-N fault leading to Bus bar protection operation and tripping of all elements connected to 400kV Bus-2. | 1.JSWEL to submit a comprehensive report and the corrective action done on receipt of the OEM report. 2.JSWEL to check the healthiness of all breakers and equipment in the switchyard. 3.JSWEL to rectify the DR time sync issue. | M/S JSWEL | JSW@ENERGY1:JSWE: 05/03/2025 11:01:29: OE JSW@ENERGY1:JSWE: 05/03/2025 11:03:49: 1. OEM report is awaited 2. JSWEL 400KV bay are checked and found healthy 3. New GPS clock procurement is in progress | Pending | Pending
126/II/9 | 400KV/230KV KUDANKULAM-ICT-1 | 03-12-2024 13:24 | During the antecedent condition both 400/220kV ICT-1 and ICT-2 were in idle charged condition from 400kV side due to 220kV GIS shutdown. As per the reports submitted, during the normalization of 220kV GIS, 220kV BUS-1 (ADA) was charged through ICT-1. While charging BUS-2 through ICT-2, BUS-1 (ADA) was tripped on Busbar differential protection (87BB). Subsequently LV side Breaker of ICT-1 was tripped. Tripping of ICT-1 needs review. | NPCIL, KKNPP to furnish the draft detailed report of the event. | NPCIL- KKNPP | purvabhoj:NPCIL: 31/01/2025 13:27:34: Detailed event report on 230KV bus bar trip , Status of CB before & after trip event log submitted through email dated:30.01.2025 | Complied | Complied
126/III/2 | Tripping of 400kV Ramagundam Ghanapur Line-3 and 4 | 23-11-2024 10:37 | As per the reports submitted, the triggering incident was RN fault in 400kV Ramagundam Ghanapur Line-4 due to insulator flashover. At both ends the line tripped on operation of Zone-1 distance protection. A/R operated but again the line tripped due to persistent fault. Meanwhile, 400kV Ramagundam Ghanapur Line-3 tripped at Ramagundam end on operation of Zone-1 distance protection. Suspected distance overreach in M1 7SA522 relay. At Ghanapur end, the line was holding. Tripping needs review. | NTPC Ramagundam to explore the requirement of firmware upgradation of SIEMENS make 7SA522 relay at other locations in consultation with OEM. | NTPC Ramagundam | RSTPS:NTPC: 05/03/2025 11:16:12: Firmware Upgradation completed,Complied | Complied | Complied
126/III/3 | Multiple trippings at HNPCL | 26-11-2024 10:50 | As per the reports submitted, the triggering incident was BN fault in 400kV Guddigudem Hinduja line-2 due to tree fault. At Guddigudem end the line tripped on operation of Zone-2, carrier-aided distance protection. A/R operated and the line was holding. At Hinduja end the line tripped on operation of Zone-1 distance protection. A/R did not get operated due to the delay in sensing the voltage at the remote end. From the DR, the voltage at the line side appears after 1.2 Sec and the relay has a 200mSec time delay to cross-check the line voltage and the total time taken is 1.4 Sec which crosses the existing setting time of the relay. (Time setting of the relay for Auto-recloser operation at HNPCL end was 1.350 Sec at end). Meanwhile 420kV/21kV Hinduja GT-2 tripped on operation of REF protection and contributed 7kA for the fault. | HNPCL to set the dead time operation for A/R as 1.5 sec. | HNPCL | Anilkumar:HNPCL: 06/02/2025 11:38:23: Completed. Implemented for both the Guddigudem Line -1 and Line-2. | Complied | Complied
126/III/15 | Tripping of NCTPS U-1 and Vallur U-2 during fault in 400kV Alamathy NCTPS_Stage_II line-1 | 17-12-2024 20:10 | As per the reports submitted, the triggering incident was RN fault in the line due to insulator decap. At both ends the line tripped on operation of Zone-1 distance protection. A/R operated at both ends but again the line tripped due to persistent fault. Meanwhile, NCTPS Unit 1 load got drifted from 195 MW to 0 MW and the turbine got tripped, leading to tripping of the Generator. At Vallur TPS end, Unit-2 tripped on shaft vibration high. A/R operation for 400kV Alamathy NCTPS_Stage_II line-1 at NCTPS end and tripping of NCTPS Unit 1 and Vallur TPS Unit-2 during the fault needs to be reviewed. | NTECL to refer the matter to OEM and furnish the detailed report along with action plan. | NTECL | BrajeshKumarPandey:NTECL: 19/03/2025 17:32:58: After implementation of OEM recommendations, recent trends show that vibration level is substantially reduced during the grid faults. BrajeshKumarPandey:NTECL: 20/03/2025 18:09:35: 1. PSS Tuning done. 2.Survey done on earthing system. Rectified all the defects. Ground potential rise now dropped considerably. | Complied | Complied
126/IV/2 | 400KV-NPS-SEIL_P1-1 | 26-11-2024 00:47 | As per the reports submitted the triggering incident was RN fault in the line due to R phase conductor jumper damage in tower-12. At NPS end the line tripped on operation of Zone-1 distance protection. A/R operated but again the line tripped due to persistent fault. At SEIL_P1 end the line tripped on operation of differential protection. A/R did not get operated, the line tripped on 3-phase. | SEIL to furnish the reason for A/R at SEIL end for 400kV NPS-SEIL line. | SEIL |  | Pending | Pending
126/VI/6 | 420KV/21KV HINDUJA-GT-2 | 26-11-2024 10:50 | As per the reports submitted, the triggering incident was BN fault in 400kV Guddigudem Hinduja line-2 due to tree fault. At Guddigudem end the line tripped on operation of Zone-2, carrier-aided distance protection. A/R operated and the line was holding. At Hinduja end the line tripped on operation of Zone-1 distance protection. A/R did not get operated due to the delay in sensing the voltage at the remote end. From the DR, the voltage at the line side appears after 1.2 Sec and the relay has a 200mSec time delay to cross-check the line voltage and the total time taken is 1.4 Sec which crosses the existing setting time of the relay. (Time setting of the relay for Auto-recloser operation at HNPCL end was 1.350 Sec at end). Meanwhile 420kV/21kV Hinduja GT-2 tripped on operation of REF protection and contributed 7kA for the fault. | HNPCL to provide DR time synchronization for the GRP panel. | HNPCL | Anilkumar:HNPCL: 06/02/2025 11:35:25: Contacted OEM of Relays - Schneider and GE. Offer yet to receive from GE and Schneider not responding. We will proceed once offer is received. | Pending | Pending
126/VI/18 | 400KV-JINDAL-BPS-4 | 02-12-2024 21:35 | The triggering incident is the Y-N fault after isolator and before the breaker at TR-18 of Jindal TPS (within the bus zone). During the previous event at 20:52 Hrs all the elements connected to 400kV Bus-1 tripped including TR-18 breaker. For the restoration of TR-18, the isolator to Bus-2 was closed on a suspected Y-N fault leading to Bus bar protection operation and tripping of all elements connected to 400kV Bus-2. | JSWEL to rectify the DR time sync issues | JSWEL | JSW@ENERGY1:JSWE: 05/03/2025 10:59:52: New GPS clock procurement is in progress JSW@ENERGY1:JSWE: 30/06/2025 16:10:23: Purchase order placed for new Clock. material expected by 31.07.25 JSW@ENERGY1:JSWE: 12/08/2025 18:00:25: New GPS clock installed and Time sync is in order | Complied | Complied
126/VI/20 | AMGEPL_WIND - 400KV | 04-12-2024 17:44 | During antecedent conditions, 400kV Greenko CPSS, 400kV AMGEPL Wind Plant and 400kV Pinnapuram PSP were radially connected to 765kV/400kV Kurnool SS through 400kV Greenko CPSS Kurnool line-1. Triggering incident was inadvertent tripping of 400kV Greenko CPSS Kurnool line-1 at Greenko CPSS end during testing activity. This resulted in the complete outage of 400kV Greenko CPSS, 400kV AMGEPL Wind Plant, and 400kV Pinnapuram PSP. | AMGEPL to rectify the DR time sync issues. | AMGEPL | ravishekhawat:AMGEPL: 31/01/2025 16:07:28: Working along with OEM towards the closure of this time synch issue. ravishekhawat:AMGEPL: 31/01/2025 16:10:10: Working along with OEM towards closure of time synch issue. ravishekhawat:AMGEPL: 01/03/2025 15:37:30: The Toshiba OEM is addressing a time synchronization error. Since all Toshiba IED software patches are developed overseas, the Indian team is entirely reliant on the overseas team for resolution which is expected very soon. ravishekhawat:AMGEPL: 04/03/2025 16:48:39: OEM committed to close this through a software patch in IED by 1st June 2025. Developing of new MDB fi e through our standard QA, Testing process will take 3 months considerable time. | Complied | Complied
126/VI/21 | 400KV-KAIGA-GUTTUR-2 | 05-12-2024 17:32 | As per the reports submitted, the triggering incident was BN fault in the line. At Kaiga end the line tripped on operation of Zone-1 distance protection. A/R operated successfully and the line was holding. At Guttur end the RB-N fault was sensed in Zone-2 distance protection. The line tripped on 3-phase on receipt of carrier from the remote end. Tripping is in order. | NPCIL KGS to furnish the detailed report in this regard. | NPCIL KGS | KGS34:NPCIL: 05/03/2025 15:53:31: Since the event is SLT (as per SPHOORTHI) portal, there is no provision for uploading Detailed report. For this event Trip report already submitted. The same is mailed to SRPC along with SRLDC detailed report. As per SRLDC detailed report, it shows that DR time synch issue at GUTTUR end and there is no DR synch issue at Kaiga end. But In PCSC agenda 126, it was shown as DR sync issue at NPCIL-KGS (VI/21 event). You may please review the same and close the pending point. KGS34:NPCIL: 05/03/2025 15:53:58: Since the event is SLT (as per SPHOORTHI) portal, there is no provision for uploading Detailed report. For this event Trip report already submitted. The same is mailed to SRPC along with SRLDC detailed report. As per SRLDC detailed report, it shows that DR time synch issue at GUTTUR end and there is no DR synch issue at Kaiga end. But In PCSC agenda 126, it was shown as DR sync issue at NPCIL-KGS (VI/21 event). You may please review the same and close the pending point. | Complied | Complied
126/VI/24 | Vallur TPS - UNIT 2 | 17-12-2024 20:10 | UNIT-2 TRIPPED ON SHAFT VIBRATION HIGH, DURING GRID DISTURBANCE (NCTPS-ALAMATHY 400KV LINE TRIP) | NTECL Vallur to furnish the detailed report in this regard. | NTECL | BrajeshKumarPandey:NTECL: 19/03/2025 17:27:45: PSS Tuning done with OEM. After implementation of OEM recommendations , recent tends show substantial reduction in vibration during grid fault. BrajeshKumarPandey:NTECL: 20/03/2025 18:10:43: 1. PSS Tuning done. 2.Survey done on earthing system. Rectified all the defects. Ground potential rise now dropped considerably. | Complied | Complied
126/VI/29 | 400KV-NCTPS_STAGE_II-VALLUR-2 | 20-12-2024 14:52 | As per the reports submitted, the triggering incident was YN fault in the line due to jumper cut at location 3. At both ends the line tripped on operation of differential protection. A/R not in service as the line is between two generating stations. Tripping is in order. | NTECL Vallur to furnish the detailed report in this regard. | NTECL | BrajeshKumarPandey:NTECL: 07/02/2025 16:53:24: Detailed report sent in mail | Complied | Complied
127/I/2 | Complete Outage of 220kV RSRPL | 04-01-2025 13:51 | As per the reports submitted, the triggering incident was B-N fault in 220kV KNTL RSRPL line and the line tripped at both ends. Tripping of the only connected line led to a complete outage of 220kV RSRPL | 1.M/s Renew to check the healthiness of all the switchyard equipment and furnish the report to SRPC. 2.M/s Renew to standardize the DR as per the FOLD recommendations. | M/s Renew |  | Pending | Pending
127/I/3 | Complete Outage 220kV KSPDCL Generating station | 06-01-2025 21:37 | As per the submitted reports, the triggering incident was a B-N fault in the 220kV cable of the 400kV/220kV Pavagada ICT-6. Immediately, the Main-1 differential protection of the ICT operated, resulting in the tripping of the ICT. Simultaneously, the 220kV Pavagada KSPDCL-4 line tripped at the KSPDCL end due to the operation of under-voltage protection. The tripping of the only connected line led to the complete outage of the 220kV KSPDCL-4 generating station. | 1.KSPDCL to furnish the detailed report regarding the reason for BUSBAR operation. 2.KSPDCL to standardise the DR as per FOLD recommendations. | KSPDCL | ceokspdcl:KSPDCL: 08/04/2025 17:24:42: Bus Bar relay operation is due to relay configuration issue and the same is rectified and caliberated. ceokspdcl:KSPDCL: 08/04/2025 22:36:16: The reason for Busbar relay zone-1 operation is due to momentary deferential current sensed from its connected transfarmer-1 bay. All the bay CT terminals are checked & found good condition and Busbar relay also calibrated and found working satisfactory. | Complied | Complied
127/II/5 | Tripping of 230kV Bus-1 of 400kV/230kV Kudankulam Generating Station | 04-01-2025 02:56 | As per the reports submitted, the triggering incident was LBB maloperation in Kudankulam GT-1. All elements connected to 230kV Bus-1 tripped resulting in the outage of 230kV Bus-1. | NPCIL-KKNPP to review the LBB operation logic at both 400kV and 220kV by incorporating both current value and breaker status. | NPCIL-KKNPP | purvabhoj:NPCIL: 03/03/2025 17:13:48: LBB operation by using Circuit Breaker contact logic in addition to current detectors proposal under review in site.Subsequently it will be taken up with NPCIL-HQ designer. purvabhoj:NPCIL: 02/04/2025 21:25:58: As per CBIP 328 clause no13.12. For breaker-fail relaying for low energy faults like buchholz operation, special considerations to be taken to ensure proper scheme operation by using CB contact logic in addition to current detectors. In KKNPP Transformer feeders are considered as per CBIP for low energy faults. For T/F feeders only, in protection relay Low current BF ON means when current of T/F is less than 0.2In of rated current, if any trip initiates the breaker is still closed even after 250ms then LBB will initiate (only breaker position) . In case if T/F running current exceeds more than 0.2In of rated, this low-current mode is blocked automatically. If any trip initiates , however the immediate breaker is not opened even after 250ms, then LBB will initiate based on the current detection in addition to breaker contact logic. KKNPP transformer feeders protection setting is compiled as per the CBIP328 for consideration in low energy faults as well as CB contact logic in addition to current detectors. | Complied | Complied
127/III/4 | 400KV/33KV AMGEPL_SOLAR-ICT-2 | 26-12-2024 19:33 | As per the reports submitted, the triggering incident was RB fault in the 33kv outgoing feeder. Due to heavy fault current fed, 400/33kV AMGEPL_Solar ICT-2 tripped on operation of differential protection. Tripping is not in order. | 1.M/s AMGEPL to rectify the Non reporting of SCADA SOE. 2.M/s AMGEPL to analyse the reason for Differential relay operation for through fault. | M/s AMGEPL | ravishekhawat:AMGEPL: 27/02/2025 12:50:50: 1. Real time data(analog & digital) is reporting confirmed with srldc. 2. Under analysis with oem regarding RCA. ravishekhawat:AMGEPL: 05/03/2025 09:52:11: We observed unbalanced currents for a through fault in the system due to a dead short circuit between phases in the 33 KV feeder. We are seeking a solution/change in relay settings from OEMs to avoid tripping during such faults. ravishekhawat:AMGEPL: 10/04/2025 14:38:01: Submitted RCA report on email on dated 09.04.25 | Complied | Complied
127/III/8 | 400KV-GREENKO_CPSS-KURNOOL_PG-1 | 02-01-2025 15:56 | As per the reports submitted, 400kV Greenko_CPSS Kurnool_PG line-1 tripped only at Greenko end. At Greenko end, Bay No. 409 Greeenko_CPSS to Kurnool Line-1 CB opened on ploe discrepancy. As per the information furnished by Greenko, loose contact in positive was observed which extended to Y phase trip coil directly. Subsequently R&B phases opened on PD operation. At Kurnool end, the line was in service. Tripping is not in order. | GREENKO to check whether all panel connections are proper at CPSS end. | GREENKO | kvchenchaiah:GREENKO: 25/02/2025 15:02:37: As per PCSC 127th recommendations for the tripping happened on 02-01-25 at 15:56 Hrs. At CPSS end. Action taken:-Checked all CRP Panels at CPSS physically & Tightness also checked found all OK. Checked dated. 03.01.25 AMGEPL WIND & AMGEPL SOLAR CRP-1&2 ..PGCIL-1&2 CRP Panels checked dated 04.01.2025 and Remaining all CRP Panels are checked on dated: 05.01.2025 along with valid work permit system. | Complied | Complied
127/III/10 | 400KV-SEIL_P2-NPS-1 | 03-01-2025 18:08 | As per the reports submitted, 400kV SEIL_P2- NPS line-1 tripped on operation of OV protection due to adoption of wrong Over Voltage setting. At SEIL_P2 end, the online checking and adoption of new OV setting was under progress. While checking P546 (M2), the engineer assumed the setting as wrong and changed it from 122V---10 sec and 154V---100ms (which was in order as per the new setting) to 110V---10sec and 140V---100ms instead of 110%---10sec and 140%---100ms. Wrong setting adoption resulted in unwanted tripping. AT NPS end, the line tripped on receipt of DT from the remote end. Tripping is not in order. | 1.SEIL to check the OVR settings of all feeders. 2.SEIL to ensure the participation in PCSC meeting. | SEIL |  | Pending | Pending
127/IV/1 | 400KV-GADAG_PSS-KUDGI_PG-1 | 21-12-2024 06:43 | As per the reports submitted, the triggering incident was BN fault in the line. At Gadag end the line tripped operation of Zone-1 distance protection. A/R did not get operated and the line tripped on 3-phase. At Kudgi end the line tripped on operation of Zone-1 distance protection. A/R operated successfully and the line was holding. | M/s GTL to review the scheme in consultation with OEM and furnish a report. | M/s GTL |  | Pending | Pending
127/VI/6 | 400KV/33KV AMGEPL_SOLAR-ICT-2 | 26-12-2024 19:33 | As per the reports submitted, the triggering incident was RB fault in the 33kv outgoing feeder. Due to heavy fault current fed, 400/33kV AMGEPL_Solar ICT-2 tripped on operation of differential protection. Tripping is not in order. | AMGEPL to rectify the DR time sync issues. | AMGEPL | ravishekhawat:AMGEPL: 27/02/2025 12:25:53: Already taken up the issue with OEM. closely working with oem for closure. ravishekhawat:AMGEPL: 05/03/2025 09:52:11: We observed unbalanced currents for a through fault in the system due to a dead short circuit between phases in the 33 KV feeder. We are seeking a solution/change in relay settings from OEMs to avoid tripping during such faults. ravishekhawat:AMGEPL: 28/03/2025 11:57:46: OEM committed to close this through a software patch in IED by 1st June 2025. Developing of new MDB file through our standard QA, Testing process will take 3 months considerable time. | Complied | Complied
127/VI/7 | 400KV-BHADRAVATHI-RAMAGUNDAM-2 | 28-12-2024 13:41 | As per the reports submitted, the triggering incident was OV St-1 protection at Bhadravathi end. At Ramagundam end the line tripped on receipt of DT from remote end. Tripping is in order. | NTPC Ramagundam to rectify the DR time sync issues. | NTPC Ramagundam | RSTPS:NTPC: 05/03/2025 11:16:12: Completed,Complied | Complied | Complied
128/III/3 | 400KV-NTPL-TUTICORIN_PS-1 | 26-01-2025 08:05 | As per the reports submitted, the line tripped on Low Gas pressure trip on Bus Isolator compartment. At NTPL end, R phase Distance Protection Main 2 CT secondary cable got cut inside GIS. SF6 Gas leaked through CT terminal box which tripped the line in SF6 Gas pressure low trip in 89B isolator compartment. No tripping at Tuticorin end. Tripping needs review. | 1.NTPL to inspect the overall condition of the GIS bay | NTPL |  | Pending | Pending
128/V/2 | 765KV-WARANGAL(NEW)-WARORA-2 | 01-02-2025 15:44 | As per the reports submitted, the line tripped only at Warora end on DT Receive due to suspected PLCC maloperation at Warangal end. Tripping is not in order | 1.WKTL to furnish a detailed analysis of the event. | WKTL |  | Pending | Pending
128/VI/6 | 400KV-KTPS_VII-JULURUPADU-2 | 26-01-2025 18:03 | As per the reports submitted, the line tripped on the operation of OV St-1 protection at KTPS end and DT was received at Julurupadu end. From DR at KTPS end, the voltages observed were: Vr-247kV, Vy-245kV and Vb-243kV. Tripping needs review | KTPS to furnish the detailed analysis of the event. | KTPS |  | Pending | Pending
128/VI/9 | KARUR_JSW_Dharapuram_1 - 230KV | 31-01-2025 15:27 | As per the reports submitted, the triggering incident was tripping of 230kV Karur JSW_Dharapuram-1 line at Karur end on DEF protection and DT was received at Dharapuram end. Tripping of the only connected line led to complete outage of 230kV JSW_Dharapuram Wind Station | 1.Karur/JSW Dharapuram to furnish a detailed analysis of the event. | Karur/JSW |  | Pending | Pending
128/VI/16 | 400KV-KTPS_VII-JULURUPADU-2 | 20-02-2025 18:20 | As per the reports submitted, 400kV KTPS VII Julurupadu line-2 tripped on operation of OV St-1 protection at KTPS end and DT was received at Julurupadu end. From the DR at Julurupadu end, voltages observed are: Vr-247.766kV, Vy-245.772kV, Vb-242.429kV. Tripping is in order | KTPS to furnish a detailed analysis of the event. | KTPS |  | Pending | Pending
129/III/3 | 400KV-KAIGA-GUTTUR 1 | 22-02-2025 10:35 | As per the reports submitted, the triggering incident is the maloperation of TEED protection R-Y phases at Kaiga end for 400KV-KAIGA GUTTUR-1 and 3ph tripped at Kaiga end. DT was sent to Guttur end and 3ph tripped. Tripping needs review. | 1.NPCIL Kaiga to ensure that SOP would be adhered to while carrying out check/tests/maintenance activities etc. | NPCIL Kaiga | KGS34:NPCIL: 04/06/2025 11:26:05: NPCIL Revised the SOP for activity & measures has been placed to follow the revised SOP during maintenance activities on Grid elements. Hence requested to close the point. | Complied | Complied
129/III/9 | Multiple trippings at 230kV BHAVINI | 11-03-2025 08:05 | As per the reports submitted, the triggering incident is the R-N fault which developed into R-B fault in 230KV-KALVENDAPATTU SIRUSERI. At Siruseri end, the fault was sensed in Z1 and AR operated and tripped due to persistent fault where in while reclosing the fault developed into R-Y fault. At Kalivendapattu end, the fault was sensed in Z2 carrier aided trip and AR operated but tripped subsequently in Z2 time trip. During the event both 230KV-BHAVANI-SIRUSERI-1&2 sensed the fault in Z1 and 230KV-BHAVANI SIRUSERI-2 AR operated and successful but 230KV-BHAVANI-SIRUSERI-1 tripped due to non-operation of AR at BHAVINI end. Both the line (230KV-BHAVANI-SIRUSERI-1&2) were holding from Siruseri end. Tripping needs review. | 1.BHAVINI to furnish the detailed report on the event. 2.BHAVINI to furnish the relay settings to PSSG to review the settings. | BHAVINI |  | Pending | Pending
130/I/1 | Complete outage of 220kV/110kV Kavoor SS, 220kV/110kV MSEZ(Bajpe) SS, tripping of 220kV Bus-1 of 220kV/110kV Kemar SS of KPTCL and tripping of 400kV Bus-1 and 220kV Bus-1 and 2 at 400kV/220kV UPCL of Adani | 19-02-2025 08:55 | During antecedent conditions, there was bus split operation at 220kV Kemar SS. The triggering incident was opening of Main Bay of 400kV/220kV ICT1 at UPCL for planned maintenance coincided with the LV breaker tripping, leading to an overload on ICT2. The UPCL SPS operated and tripped U2 despite 400kV lines being in service, and 400kV/220kV ICT2 later tripped on backup OC protection, causing complete outage of 220kV/110kV Kavoor SS, 220kV/110kV MSEZ (Bajpe) SS, tripping of 220kV Bus-1 of 220kV/110kV Kemar SS of KPTCL and tripping of 400kV Bus-1 and 220kV Bus-1 and 2 at 400kV/220kV UPCL of Adani | 1.APL to investigate the reason for LV braker tripping during manual tripping of HV breaker. 2.APL /KPTCL to implement the SPS logic and inform the same to SRPC & SRLDC. 3.APL to rectify the DR time sync issue | APL |  | Pending | Pending
130/I/12 | Complete Outage of 400/33 kV AMGEPL SOLAR | 04-04-2025 11:38 | 400kV AMGEPL-Solar is connected to 400kV GREENKO with only one 400kV line. In the antecedent condition 400/33kV ICT-2 at AMGEPL SOLAR was tripped on 04/04/2025 11:03 Hrs. During the charging of 400/33kV ICT-2 at AMGEPL due to the suspected inrush of the transformer, 400kV AMGEPL Solar-GREENKO line got tripped at GREENKO end due to DEF operation and DT was sent to remote end leading to tripping at AMGEPL Solar end also. Due to the tripping of the only connected line led to the complete outage of 400/33kV AMGEPL Solar. | 1.M/s GREENKO to consult OEM and furnish the reason for DEF operation during ICT charging at AMGEPL. 2.M/s AMGEPL to consult Transformer manufacturer for the reason for unbalance currents during charging of transformer | AMGEPL | ravishekhawat:AMGEPL: 05/06/2025 10:25:35: AMGEPL: Discussed with OEM, they recommended to check healthiness of transformer earthing and earth-pit | Complied | Complied
130/I/13 | Complete Outage of 220kV Vena_Gadag | 08-04-2025 21:48 | As per the reports submitted, the triggering incident was YB-N fault in the line. At both ends, zone-1 protection operated and the line tripped. Tripping of the only connected line led to complete outage of 220kV Vena Generating Station. | SRLDC to furnish the revised report incorporating correct details and correct PMU plots. | SRLDC | ArthiV~1776856274:SRLDC: 02/07/2025 19:08:27: Modified report of Complete Outage of 220kV Vena_Gadag PS on 08-04-2025 at 21:48 was sent on 03-06-2025. The point may be closed. | Complied | Complied
130/I/16 | Complete outage of 220kV Rychalu SS of KSPDCL | 20-04-2025 20:15 | As per the reports submitted, the triggering incident was B-N fault in 220kV Pavagada Rychalu line and the line tripped. Tripping of the only connected line led to complete outage of 220kV Rychalu SS | KSPDCL to expedite enabling of AR . | KSPDCL | ceokspdcl:KSPDCL: 11/06/2025 13:23:38: Action taken to enable AR in coordination with KTPCL RT team. ceokspdcl:KSPDCL: 05/07/2025 16:26:24: Action Initiated to enable AR coordination with KPTCL RT team. ceokspdcl:KSPDCL: 05/07/2025 16:26:36: Action Initiated to enable AR coordination with KPTCL RT team. | Pending | Pending
130/III/1 | BETAMWIND - 230KV | 27-02-2025 17:06 | As per the reports submitted, the triggering incident is the Y-N fault developed into R-Y- B fault at 33kV LV side of 220/33kV PTR-01 due Insulator failure near Y Phase Isolator and B Phase Isolator. PTR-1 and 2 tripped at Betam station during the event | BETAM WIND to submit the detailed report on the incident. | BETAM WIND |  | Pending | Pending
130/III/6 | 400KV/33KV AMGEPL_SOLAR-ICT- 2 | 02-04-2025 17:10 | As per the information furnished, 400kV/33kV AMGEPL_SOLAR-ICT-2 tripped during CT testing activity. It was further mentioned that, while doing CT testing on the 33kV Spare feeder, CB failure trip protection operated and tripped the complete 33kV Bus-4 connected breakers. LV side of 315MVA 400kV/33kV AMGEPL_SOLAR- ICT-2 was connected to 33kV Bus-4. Tripping is not in order. | AMGEPL to follow the SOP while carrying out the testing activities. | AMGEPL | ravishekhawat:AMGEPL: 05/06/2025 10:34:04: Implemented SOP | Complied | Complied
130/III/18 | Multiple Trippings at Jindal TPS | 11-04-2025 19:45 | As per the reports submitted, the triggering incident is the B-N fault in 400KV- PAVAGADA_PG-BPS-1 line. The fault was sensed in Z1 at both ends, AR operated, and was successful. However, during the same time 400KV-JINDAL-BPS-3&4 tripped only at Jindal end due to suspected potential rise (as per FIR). | 1.JSW to review and verify the integrity of the station earthing system. 2.JSW to review the distance protection zone settings. | JSW | JSW@ENERGY1:JSWE: 30/06/2025 16:08:17: 1. Earthing system checked. 2. Distance settings are inline with recommendations | Complied | Complied
130/III/21 | 400KVNeyveli_ TS_IINeyveli_ TS1_E xp-1 | 14-04-2025 22:45 | As per the reports submitted, the triggering incident is the suspected maloperation of Over Voltage protection due to faulty of O/V relay C phase (VTIG instantaneous) at NLC TS1Exp end leading to 3ph tripping of the line and DT sent to remote end. | NEYVELI TS1 EXP to submit the detailed report on the incident | NEYVELI TS1 EXP | NLCI/TS1EXPN:NLCIL: 01/08/2025 15:45:06: O/V - 1/2 operated, Auto reclose trip, Remote Trip signal operated annunciation appeared in control panel. Over voltage protection C phase stage-1 relay acted at TPS-1 Expansion end and Timer overvoltage protection 2/59 L1 acted. In MICOM relay no fault appeared. No other abnormalities noticed and no relay acted. At that time 400 KV bus voltage is 410 KV. Remote tripping checked at both end. Found normal. Upon further checking, O/V relay C phase (VTIG instantaneous) was found faulty. Same was replaced with the same existing settings. After getting clearance from SRLDC, line charged from TPS 2 end. Line charged at 02:15 hrs on 15-04-2025. | Complied | Complied
130/IV/15 | 400KVGUDDIGUDEMHINDUJA- 2 | 09-04-2025 16:47 | As per the reports submitted, the triggering incident was R-N fault in the line at a distances of 16km from Guddigudem end. At both ends, the fault was sensed in zone-1. A/R operated and the line tripped on persistent fault. Difference in A/R dead time is observed between both ends. | HNPCL to submit the detailed report on the incident. | HNPCL | Anilkumar:HNPCL: 01/09/2025 17:06:22: At HNPCL end, the dead time is 1.4 Sec and it is time differentiated AR dependent on the line UV. Remote end AR operated and line withstood 280ms. However at HNPCL end, reset timer is 200ms. Hence the line is considered as healthy and AR operated at HNPCL end. | Complied | Complied
130/VI/8 | 400KV-OTTAPIDARAM-SEPC-2 | 23-03-2025 12:44 | DR time synchronization was not observed at SEDAM - 220KV | SEPC to resolve the time synchronization issue | SEPC |  | Pending | Pending
130/VI/18 | 400KV-NCTPS_STAGE_II-VALLUR-1 | 11-04-2025 04:15 | DR Time Synchronization issue at VALLUR - 400KV | NTECL VALLUR to resolve the time synchronization issue | NTECL VALLUR | BrajeshKumarPandey:NTECL: 19/08/2025 16:04:48: GPS installation in progress | Pending | Pending
130/VI/23 | 400KV-JINDAL-BPS-3 | 11-04-2025 19:45 | DR time synchronization issue at JINDAL - 400KV | JSW to resolve the time synchronization issue | JSW | JSW@ENERGY1:JSWE: 05/06/2025 12:28:03: 1. Earth pits checked, found normal 2. Relay settings are in line with charging approval. JSW@ENERGY1:JSWE: 30/06/2025 16:06:15: Purchase order placed. Expected new Clock by 31.07.25 JSW@ENERGY1:JSWE: 12/08/2025 16:14:32: New GPS clock installed and Time sync is in order | Complied | Complied
131/I/4 | Complete Outage of 400kV CEPL Generating Station | 22-04-2025 15:14 | During antecedent conditions, 400kV CEPL Tuticorin PS line-2 was under shut down for maintenance. Triggering incident was BN fault in 400kV CEPL Tuticoirn PS line-1 due to LA failure at CEPL end. Due to tripping of the only connected line, there was complete outage of 400kV CEPL generating station. | 1. CEPL to check the healthiness of the R & Y phase LAs. 2. CEPL to furnish the LA failure report to CEA | CEPL / APL |  | Pending | Pending
131/I/7 | Complete Outage of 220kV Veena_GadagPS | 25-04-2025 21:29 | Triggering incident was RN fault in 220KV-GADAG_PSS-Vena_GadagPS-1. Due to tripping of the only connected line, there was complete outage of 220kV Veena_GadagPS. | 1. Gadag to review the distance protection settings. 2. Gadag to review the A/R logic settings in all Gadag connected lines 3. Gadag to review the non-operation of the Main-2 relay. 4. Vena to review the non-operation of the Main-2 relay. 5. Gadag to rectify the SCADA SOE issue | M/s Veena / Gadag |  | Pending | Pending
131/I/9 | Complete Outage of 230kV Sprng Pugalur Wind Station | 26-04-2025 07:19 | During charging of 230kV/33kV PTR3 at 230kV Sprng Pugalur Wind Station, LBB operted resulting in the tripping of all the elements connected to 230kV Bus1 and Bus2 at 230kV/33kV Sprng Pugalur Wind Station. | Sprng Pugalur to submit the relay settings to SRPC for approval | M/s Spring Pugalur | ramakrishnang:Sprng Energy Ltd(Pugalur): 31/07/2025 16:57:31: 230KV BUS BAR PROTECTION SCHEME CHANGE AND RELAY SETTING SUBMITTED FOR SRPC/SRLDC APPROVAL. DNMS TICKET ALSO RAISED.5738 ON 10-06-2025. SAME HAS BEEN APPROVED AND RECOMMENDATIONS GIVEN BY PSSG TO FOR FURTHER IMPLEMENTATION. RECOMMENDATIONS ISUED ON 10-07-2025. WORK IN PROGRESS FOR IMPLEMENTATION OF RECOMMENDATION | Complied | Complied
131/I/11 | Complete Outage 220kV Hiriyur Ostro | 27-04-2025 19:13 | As per the reports submitted, the triggering incident was R-N fault in 220kV Hiiryur Ostro Kannada line and the line tripped. Tripping of the only connected line led to complete outage of 220kV Hiriyur Ostro | OSTRO Kannada to rectify the A/R issue within a week | M/s Ostro Kannada |  | Pending | Pending
131/I/15 | Complete outage of 400kV AMGEPL_Solar | 02-05-2025 18:32 | As per the reports submitted, the triggering incident was BN fault in 400kV Greenko AMGEPL line. At both ends, the fault was sensed in differnetial protection. A/R operated and the line tripped on persistant fault. Tripping of the only connected line led to complete outage of 400kV AMGEPL_Solar. | Greenko to rectify the DR time sych issue. | M/s Greenko | kvchenchaiah:GREENKO: 05/07/2025 10:00:34: The time synchronisation DR of relay 7SL87 has been verified with respect to GPS and no deviation has been noticed. Summited for further needful. | Complied | Complied
131/I/16 | Complete Outage of 220kV Hiriyur Ostro Wind Station | 05-05-2025 20:12 | Triggering incident was RN fault in 220KVHIRIYUR_OSTROHIRIYUR1 due to failure of suspension pilot insulator. Tripping of the only connected line resulted in the complete outage of 220kV Hiriyur Ostro Wind Station. | OSTRO Kannada to rectify the A/R issue at both ends of Hiriyur OSTROHiriyur. | M/s Ostro Kannada |  | Pending | Pending
131/VI/9 | 400KV-GREENKO_CPSS-AMGEPL_SOLAR1 | 02-05-2025 18:36 | GREENKO_CPSS - 400KV | Greenko to furnish the reasons for DR Time sync issues | M/s Greenko | kvchenchaiah:GREENKO: 05/07/2025 10:00:14: The time synchronisation DR of relay 7SL87 has been verified with respect to GPS and no deviation has been noticed. Summited for further needful. | Complied | Complied
131/VI/13 | 400KV-LKPPL_STG2-VIJAYAWADA-1 | 16-05-2025 06:01 | LKPPL_STG2 - 400KV | LANCO to furnish the reasons for DR Time sync issues | M/s Lanco |  | Pending | Pending
132/I/5 | Complete Outage of 230kV Mytrah | 02-06-2025 14:54 | As per the reports submitted, the triggering incident was B-Phase jumper cut in 220kV TTGS Mytrah Line-2 causing B-N fault and the line tripped. Tripping of the only connected line led to complete outage of 230kV Mytrah Generating station. | Mytrah to furnish the detailed report for Non operation of A/R and 3-phase trip initiation | M/s Mytrah |  | Pending | Pending
132/I/6 | Complete Outage of 230kV JSW_Vilathikulam_300MW Wind Station | 15-06-2025 12:01 | Triggering incident was BN fault in 230kV TTGS JSW_Vilathikulam_300MW line. Due to the tripping of only connected line, there was complete outage of 230kV JSW_Vilathikulam_300MW Wind Station | GRT-Solar to furnish the reason for Tripping of PTR at their end during the incident. | M/s GRT Solar |  | Pending | Pending
132/I/6 | Complete Outage of 230kV JSW_Vilathikulam_300MW Wind Station | 15-06-2025 12:01 | Triggering incident was BN fault in 230kV TTGS JSW_Vilathikulam_300MW line. Due to the tripping of only connected line, there was complete outage of 230kV JSW_Vilathikulam_300MW Wind Station | JSW-Vilthikulam to furnish a detailed report for Differential intertrip signal sent to TTGS end. | M/s JSW-Vilthikulam | jeganraj:JSW Vilathikulam: 07/11/2025 13:39:09: Report Shared | Complied | Pending
132/I/6 | Complete Outage of 230kV JSW_Vilathikulam_300MW Wind Station | 15-06-2025 12:01 | Triggering incident was BN fault in 230kV TTGS JSW_Vilathikulam_300MW line. Due to the tripping of only connected line, there was complete outage of 230kV JSW_Vilathikulam_300MW Wind Station | JSW-Vilthikulam to rectify the DR time sync issue at their station | M/s JSW-Vilthikulam | jeganraj:JSW Vilathikulam: 07/11/2025 13:39:09: Rectified | Complied | Pending
132/I/6 | Complete Outage of 230kV JSW_Vilathikulam_300MW Wind Station | 15-06-2025 12:01 | Triggering incident was BN fault in 230kV TTGS JSW_Vilathikulam_300MW line. Due to the tripping of only connected line, there was complete outage of 230kV JSW_Vilathikulam_300MW Wind Station | LVRT compliance to be collected by TANTRANSCO/TNSLDC | TANTRANSCO /TNSLDC |  | Pending | Pending
132/V/8 | 765KV-WARANGAL(NEW)-WARORA-2 | 18-06-2025 15:34 | As per the reports submitted, the triggering incident is the tripping of the line only at Warora end and DT was sent from Warangal end due to PLCC issue and needs review. | M/s WKTL to furnish the detailed report for Mal operation of PLCC. | M/s WKTL / ADANI |  | Pending | Pending
132/V/9 | 765KV-WARANGAL(NEW)-WARORA-2 | 19-06-2025 16:57 | As per the reports submitted, the triggering incident is the tripping of the line only at Warora end and DT was sent from Warangal end due to PLCC issue and needs review. | M/s WKTL to furnish the detailed report for Mal operation of PLCC. | M/s WKTL / ADANI |  | Pending | Pending
132/VI/1 | 220KV-RAMAGUNDAM-MALYALAPALLI-4 | 21-05-2025 16:14 | Station at which DR time synchronisation was not observed - RAMAGUNDAM - 220KV | NTPC Ramagundam to furnish the reasons for DR Time sync Issues | NTPC Ramagundam | RSTPS:NTPC: 29/08/2025 19:02:06: Completed | Complied | Complied
132/VI/3 | 400KV/220KV RAMAGUNDAM-ICT-2 | 21-05-2025 16:14 | Station at which DR time synchronisation was not observed - RAMAGUNDAM - 400KV | NTPC Ramagundam to furnish the reasons for DR Time sync Issues | NTPC Ramagundam | RSTPS:NTPC: 29/08/2025 19:02:06: Completed | Complied | Complied
132/VI/2 | 400KV/220KV RAMAGUNDAM-ICT- | 21-05-2025 16:14 | Station at which DR time synchronisation was not observed - RAMAGUNDAM - 400KV | NTPC Ramagundam to furnish the reasons for DR Time sync Issues | NTPC Ramagundam | RSTPS:NTPC: 29/08/2025 19:02:06: Completed | Complied | Complied
133/I/3 | complete outage of 220kV RSRPL_GadagPS | 11-07-2025 09:08 | As per the reports submitted, the triggering incident was RY-N fault in 220kV Gadag RSRPL line-1 and the line tripped at both ends. Tripping of the only connected line led to complete outage of 220kV RSRPL_GadagPS. | M/s Renew to ensure that DR signals are mapped as per FOLD recommendations.. | M/s Renew |  | Pending | Pending
133/I/4 | Complete Outage of 220kV Serentica_RI1PL_Koppal_S | 11-07-2025 15:08 | As per the reports submitted, the triggering incident was R-N fault in 220KV-KOPPAL-Serentica_RI1PL_Koppal_S-1 and the line tripped. Tripping of the only connected line led to complete outage of 220kV Serentica_RI1PL_Koppal_S | M/s Serentica to submit a detailed report for this incident to SRPC & SRLDC. | M/s Serentica |  | Pending | Pending
133/II/1 | Tripping of 400kV Bus-1 and Bus-2 of 400kV SEIL P2 | 24-06-2025 10:47 | During antecedent conditions, SEIL P2 Bus Reactor was under shutdown for maintenance. As per the reports submitted, the triggering incident was inadvertant closing of isolator of Bus reactor at SEIL P2. Since the earth switch was in closed condition, bus bar was feeding the current through bus isolator and earth switch causing an RYB-N fault. Subsequently, Bus-1 BBP failed to operate and remote ends of 400kV lines connected to 400kV Bus-1 and Bus-2 tripped. This led to loss of power supply to 400kV Bus-1 and Bus-2. 400kV Bus-3 and Bus-4 were in service during the event. Subsequently, it is reported that SEIL P2 Generator 1 tripped on composite voltage over current protection with delay of 1.5 sec. | SEIL to ensure appropriate Electrical/Mechanical interlock between isolator and earthswitch. | SEIL | YuvarajLoganathan:SEIL Energy India Limited: 07/11/2025 14:46:41: interlocks reviewed and implemented | Complied | Complied
133/II/1 | Tripping of 400kV Bus-1 and Bus-2 of 400kV SEIL P2 | 24-06-2025 10:47 | During antecedent conditions, SEIL P2 Bus Reactor was under shutdown for maintenance. As per the reports submitted, the triggering incident was inadvertant closing of isolator of Bus reactor at SEIL P2. Since the earth switch was in closed condition, bus bar was feeding the current through bus isolator and earth switch causing an RYB-N fault. Subsequently, Bus-1 BBP failed to operate and remote ends of 400kV lines connected to 400kV Bus-1 and Bus-2 tripped. This led to loss of power supply to 400kV Bus-1 and Bus-2. 400kV Bus-3 and Bus-4 were in service during the event. Subsequently, it is reported that SEIL P2 Generator 1 tripped on composite voltage over current protection with delay of 1.5 sec. | SEIL to ensure duplication in BUSBAR protection. | SEIL | YuvarajLoganathan:SEIL Energy India Limited: 07/11/2025 14:46:41: High impedance circuit faulty resistance replaced, and protection checked and kept in service | Complied | Complied
133/II/1 | Tripping of 400kV Bus-1 and Bus-2 of 400kV SEIL P2 | 24-06-2025 10:47 | During antecedent conditions, SEIL P2 Bus Reactor was under shutdown for maintenance. As per the reports submitted, the triggering incident was inadvertant closing of isolator of Bus reactor at SEIL P2. Since the earth switch was in closed condition, bus bar was feeding the current through bus isolator and earth switch causing an RYB-N fault. Subsequently, Bus-1 BBP failed to operate and remote ends of 400kV lines connected to 400kV Bus-1 and Bus-2 tripped. This led to loss of power supply to 400kV Bus-1 and Bus-2. 400kV Bus-3 and Bus-4 were in service during the event. Subsequently, it is reported that SEIL P2 Generator 1 tripped on composite voltage over current protection with delay of 1.5 sec. | SEIL to follow SOP during Maintainence activities. | SEIL | YuvarajLoganathan:SEIL Energy India Limited: 07/11/2025 14:46:41: SOP reviewed and implemented | Complied | Complied
133/II/2 | Tripping of 400kV Bus 2 of 400kV Ramagundam Generating station | 26-06-2025 00:22 | As per the reports submitted, the triggering incident was B-phase CT failure in 400V Ramagundam causing fault in 400kV Bus-2. Immeditely, 400kV Bus-2 BBP operated and all main breakers connected to 400kV Bus-2 tripped. | NTPC-Ramagundum to furnish CT failure report to CEA | NTPC-Ramagundum | RSTPS:NTPC: 04/12/2025 19:40:24: submitted report to CEA | Complied | Complied
134/I/4 | Complete Outage of 220kV Veena_GadagPS of Vena Energy | 11-08-2025 08:23 | 220kV Vena_GadagPS is radially connected to 220kV Gadag through 220KV-GADAG_PSS-Vena_GadagPS-1. The triggering incident is the Y-G fault in the line. The tripping of the only connected line to the station led to Complete outage of 220kV Vena_GadagPS | M/s Veena Gadag to furnish the reasons for non operation of A/r | M/s Veena Gadag | VEVPL160:VENA ENERGY: 14/10/2025 15:30:54: Due to carrier RECEPTION Channel 1&2 signal continues ON, and due to three phase fault AR block also ON. | Complied | Complied
134/I/4 | Complete Outage of 220kV Veena_GadagPS of Vena Energy | 11-08-2025 08:23 | 220kV Vena_GadagPS is radially connected to 220kV Gadag through 220KV-GADAG_PSS-Vena_GadagPS-1. The triggering incident is the Y-G fault in the line. The tripping of the only connected line to the station led to Complete outage of 220kV Vena_GadagPS | M/s Veena Gadag to furnish the reasons for non reporting of PMU during the event | M/s Veena Gadag | VEVPL160:VENA ENERGY: 16/10/2025 14:36:48: There was GPS timing miss match, corrected and now its reporting | Complied | Complied
134/I/9 | Complete Outage of 400kV CEPL Generating Station of Coastal | 18-08-2025 06:51 | During antecedent conditions, CEPL GT-1 and 400KV-CEPL-TUTICORIN_PS-1 are in shutdown condition for various maintenance activity. As per the reports submitted, the triggering incident was failure of DC Charger-1&2 causing 400KV-CEPL-TUTICORIN_PS-2 to trip on SF6 interlock at CEPL end. Tripping of the only connected line led to Complete outage of CEPL Generating Stat | CEPL to furnish the detailed report based on OEM report/recomendations. | M/s Moxie Power |  | Pending | Pending
134/I/9 | Complete Outage of 400kV CEPL Generating Station of Coastal | 18-08-2025 06:51 | During antecedent conditions, CEPL GT-1 and 400KV-CEPL-TUTICORIN_PS-1 are in shutdown condition for various maintenance activity. As per the reports submitted, the triggering incident was failure of DC Charger-1&2 causing 400KV-CEPL-TUTICORIN_PS-2 to trip on SF6 interlock at CEPL end. Tripping of the only connected line led to Complete outage of CEPL Generating Stat | CEPL to rectify the DR time sync issue at 400kV CEPL SS | M/s Moxie Power | ChetanShete:MPGL: 07/11/2025 17:31:46: Relay time synch checked and found ok, Now, all relays are time synchronized with GPS. | Complied | Pending
134/III/3 | Multiple Trippings at 400kV Koppal SS and 220kV RSOPL SS | 30-07-2025 12:45 | During antecedent conditions, the 400 kV Koppal Bus2 was under shutdown from 09:45 hrs for Primary Busbar Stability and Relay Testing. 400kV/220kV Koppal ICT3, which is connected to 400kV Bus-2, was being charged through Tie Bay (408), as its Main Bay (407) was isolated. This bay arrangement was in the same dia as the 400 kV KoppalNew Kudgi_PG Line1. As per the reports submitted, the triggering incident was a YN fault on the 400 kV KoppalNew Kudgi_PG Line1 due to an insulator failure Tower No.9 from Koppal end . At the Kudgi end, the fault was also detected in Zone1, and the line tripped. At the Koppal end, the fault was detected in Zone1, A/R operated, but the line tripped due to the persisting fault | M/s Indigrid to furnish a detailed report of the event in consultation with the OEM | M/s Indigrid |  | Pending | Pending
134/V/3 | 400KV-NEYVELI_TS_II-NEYVELI_TS2_EXP-1 | 12-08-2025 06:50 | As per the reports submitted, the triggering incident is the suspected PLCC maloperation at NLC TS2EXP and the Direct trip received from NLC TS2EXP to NEYVELI_TS_II end. However, no DRs/FIR/EL were uploaded for establishing the event. | NLCIL TS-II to furnish detailed report on PLCC maloperation | NLCIL TS-II | NLCI/TS2:NLCIL: 07/11/2025 10:27:40: DT has been received at TPS-II end and PLCC counter also increased. PLCC has not maloperated at TPS-II | Complied | Complied
134/VI/5 | KSPPL - 220KV | 31-07-2025 21:13 | DR Time sync issue | M/s Kleio Solar to furnish detailed report on DR time sync issue | M/s Kleio Solar |  | Pending | Pending
135/I/4 | Complete Outage 220kV Green Infra Generating Station | 04-09-2025 05:45 | As per the reports submitted, the triggering incident was B-N fault in 220kV Gadag GreenInfra line. At both ends, differential protection operated and the line tripped. At Green Infra end, A/R operated and the line was holding. At gadag end, A/R did not operate and the line tripped. Tripping of only connected line led ot complete outage of 220kV Green Infra Generating station. | 220kV Gadag to submit the detailed report on non operation of Auto Reclosure. | M/s Gadag |  | Pending | Pending
135/I/8 | Complete Outage of 230kV JSW Vilathikulam of JSW_RE | 11-09-2025 06:48 | 230kV JSW Vilathikulam is only connected to TTGS through 230kV JSW Vilathikulam-TTGS line. As per the reports submitted, the triggering incident was B-G fault in the line. At TTGS end, differential protection operated and A/R operated and tripped due to persisting fault. At JSW Vilathikulam end, differential protection operated and AR operated and the line was in closed condition. Tripping of the only line connected to 230kV JSW Vilathikulam led to the complete outage at 230kV JSW Vilathikulam. | 1.JSW to review the Auto Reclosure logic at JSW end and TTGS end. 2.JSW to enable the single pole operation in Auto recloser. | M/s JSW | jeganraj:JSW Vilathikulam: 07/11/2025 13:39:09: our team is planning to verify the above functionality at Both Ends with support of Relay OEM team.completion by 15th Dec-25 | Pending | Pending
135/I/9 | Complete outage of 220kV SAEL of SAEL | 11-09-2025 18:00 | 220kV SAEL station is connected to Kurnool_PG_III through only 220kV SAEL Kurnool_PG_III line. As per the reports submitted, the triggering incident was R-Y-B fault in the 220kV SAEL Kurnool_PG_III line. At both ends, differential protection operated and the line tripped. Tripping of the only connected line led to complete outage of 220kV SAEL. | SAEL to check the CT star point of all the CTs at MHP2 and connected lines. | M/s SAEL |  | Pending | Pending
135/II/6 | Tripping of 400kV Bus-1 at CEPL of Moxie Power Generation Limited | 09-09-2025 14:45 | The triggering incident was tripping of 400kV Bus-1 at CEPL due to suspected LBB operation during the charging of the GT-1. The LBB initiation was already high due to wiring issue (as per Coastal) and once the GT-1 was charged, the required current threshold has reached and after around 200ms LBB operated and tripped all the connected elements to 400KV Bus-1. This led to the Tripping of 400kV Bus-1 at CEPL. | Moxie Power to furnish the detailed report of the incident. | M/s Moxie Power | ChetanShete:MPGL: 07/11/2025 17:26:39: The issue was related to wrong wiring of the LBB initiation to static relay (RAICA) of GT 1 bay which has been corrected as per the scheme drawing. | Complied | Complied
135/III/13 | 765KV-MAHESHWARAM_PG-WARANGAL(NEW)-1 | 11-09-2025 15:16 | As per the reports submitted, the triggering incident was R-N fault in the line. At Maheshwaram end, the fault was sensed in zone-1 and R-pole opened. Y-N fault was observed during A/R dead time and the line tripped. The fault distance from Maheshwaram end was 106.02kms. Tripping at Warangal end could not be verified due to non-submission of DR. | WKTL to furnish a detailed report on the incident. | M/s WKTL |  | Pending | Pending
135/IV/7 | 400KV-KOPPAL-KUDGI_PG-2 | 19-09-2025 09:36 | As per the reports submitted, the triggering incident was B-N fault. The fault distance from Koppal end was 30.82kms and from Kudgi end it was 31.7kms. At Koppal end, the fault was sensed in Zone-1 and A/R did not operate and 3ph tripped. At Kudgi end,the fault was sensed in Zone-1, carrier was sent and SOTF trip was operated. | INDIGRID to furnish detailed report regarding non operation of A/r | M/s INDIGRID |  | Pending | Pending
136/I/11 | Complete Outage of 230kV Karur_JSW_Dharapuram_2, TP Vardaman and Tripping of 230kV Bus-1 &2 at Karur PS | 08-10-2025 12:12 | JSW_Dharapuram_1, JSW_Dharapuram_2 and TP Vardaman are radially connected to Karur PS which is inturn connected to 400kV via 400/230kV ICT-1&2 Karur PS. In the antecedent conditions 230kV Karur_JSW_Dharapuram_1 was under shutdown and 400/230kV Karur PS ICT-2 was under shut down condition. The triggering incident is the R-B phase Bus fault (as per PMU) in Bus-1 due to human error (as per user FIR) leading to Bus-1 BBP operation and tripping of all the elements connected to Bus-1 including the Bus Coupler. Bus-2 did not have any evacuation led tripping the Bus-2 at Karur PS. This led to the Complete Outage of Karur_JSW_Dharapuram_2, TP Vardaman and Tripping of 220kV Bus-1 &2 at Karur PS. | 1.ATL to furnish a detailed report for the event. 2.SOP to be followed during any activites to avoid human error. 3.Direct Trip (DT) to be configured for BBP operation. | M/s ATL |  | Pending | Pending
136/III/2 | 230KV/33KV TP Vardhaman Surya TPRELICT- 1 | 28-09-2025 10:41 | As per the reports submitted, the triggering incident was REF Relay Maloperation during suspected 33kV line fault leading to operation of REF protection due to double earthing on the secondary side of the CT and tripping of 230KV/33KV TP Vardhaman Surya TPREL-ICT-1 | TATA to check the REF stability at 230KV/33KV TP Vardhaman Surya TPREL-ICT-2. | M/S TATA | bhargavupadhyay:TPREL: 11/12/2025 11:37:44: Post this ICT-1 Transformer Trip Occurrence, TATA investigated and conducted the following: 1. Visual Inspection of Transformer LV Terminal is done 2. All Cables from LV Side the Transformer checked and IR test completed. 3. Relay Setting, DR, EL checking done 4. IR Testing for Transformer carried out 5. REF Stability Test Repeated after removing the Double earthing. Transformer charged at 20.16 Hrs | Pending | Pending
136/III/7 | 400KVNEYVELI_ TS2_EXPPUGALUR- 1 | 08-10-2025 09:05 | As per the reports submitted, the triggering incident was B-N fault in the line. The fault distance from Neyveli end was 1.5kms and from Pugalur end it was 190.2kms. At Neyveli end, the fault was sensed in Z1, A/R operated and blocked subsequently 3phase SOTF was operated. At Pugalur end, the fault was sensed in Z1 and DT was received. | 400kV NLCIL TPS2 Exp to check the SOTF settings of all lines. | NLCIL TPS2 Exp | NLCI/TS2EXPN:NLCIL: 30/01/2026 12:31:37: 400kV PUGALUR MAIN-2 relay (7SA522) SOTF activation was over-current based instead of closing command based. On 08-10-2025 fault current was very high 26kA, so SOTF got activated in Main-2 relay leading to 3-ph lockout & non-operation of AR Now Main2 relay SOTF activation now has been changed from current based to only closing command based. Closing command wired for initiation of SOTF & necessary setting changes in Main-2 relay completed. In Main-1 relay of Pugalur & other line (TIE line to TS2) SOTF activation is already closing command based. Hence all recommendations have been implemented. | Complied | Complied
136/IV/11 | 220KV-NP_KUNTAGALIVVEDU- 1 | 10-10-2025 21:59 | As per the reports submitted, the triggering incident was R-N fault in the line. The fault distance from NP Kunta end was 1.92kms and from Galiveedu end it was 5.9kms. At NP Kunta end, the fault was sensed in Differential protection. At Galiveedu end, the line got tripped on R-Ph Differential & Distance Protection Operated due to Heavy Rain & Thunderstorms. | APSPCL to rectify the non-operation of A/R at Galiveedu end. | APSPCL |  | Pending | Pending
136/VI/21 | 400KV-KALVENDAPATTU-VALLUR-2 | 07-10-2025 13:55 | VALLUR - 400KV | NTECL Vallur to rectify the DR Time Synchronization issue at VALLUR - 400KV. | NTECL Vallur |  | Pending | Pending
137/I/1 | Complete Outage 220kV RSOPL_Koppal of RENEW | 23-09-2025 14:18 | 220kV RSOPL is connected to Koppal through 220kV RSOPL-Koppal line. As per the reports submitted, the triggering incident was Y-G fault in 220kV Koppal RSOPL_Koppal line and the line tripped. Tripping of the only connected led to complete outage of 220kV RSOPL_Koppal. | M/s Indigrid to submit a detailed report. | M/s Indigrid |  | Pending | Pending
137/I/2 | Complete Outage of 230kV Karur_JSW_Dharapuram_2, TP Vardaman and Tripping of 230kV Bus-1 &2 at Karur PS | 08-10-2025 12:12 | JSW_Dharapuram_1, JSW_Dharapuram_2 and TP Vardaman are radially connected to Karur PS which is inturn connected to 400kV via 400/230kV ICT-1&2 Karur PS. In the antecedent conditions 230kV Karur_JSW_Dharapuram_1 was under shutdown and 400/230kV Karur PS ICT-2 was under shut down condition. The triggering incident is the R-B phase Bus fault (as per PMU) in Bus-1 due to human error (as per user FIR) leading to Bus-1 BBP operation and tripping of all the elements connected to Bus-1 including the Bus Coupler. Bus-2 did not have any evacuation led tripping the Bus-2 at Karur PS. This led to the Complete Outage of Karur_JSW_Dharapuram_2, TP Vardaman and Tripping of 220kV Bus-1 &2 at Karur PS. | Karur PS to follow SOP during testing and Maintenance activities. | M/S Karur |  | Pending | Pending
137/III/4 | 220KV-NP_KUNTA-NP_KUNTA PSS1-1 | 25-10-2025 11:14 | As per the reports submitted, 220KV-NP_KUNTA-NP_KUNTA PSS1-1 only tripped at NP_KUNTA PSS end and the line was holding at NP_KUNTA. APSPCL reported that the line tripped on zone-1 in FIR, However, no fault and zone-1 operation is observed in the DR | 1.NP_ Kunta to provide the detailed report on the incident. 2.NP_ Kunta to rectify Time synch issue at NP_KUNTA PSS1 | APSPCL |  | Pending | Pending
137/III/6 | 400KV/11KV GREENKO_PSP-ST-2 | 25-10-2025 16:00 | As per the reports submitted, the triggering incident was PLCC Maloperation. At GREENKO_PSP-ST-2 end, backup impedance protection operated and ST-2 tripped for no fault. | Greenko is advised to enable the VT fuse failure settings in all the protection relays. | M/S GREENKO | kvchenchaiah:GREENKO: 21/01/2026 10:24:52: VT fuse failure settings in all the protection relays at PSP is enabled. | Complied | Complied
137/IV/5 | 20KV-NP_KUNTA-SBENERGY_NPK-1 | 25-10-2025 13:39 | As per the reports submitted, the triggering incident was B-N fault. The fault distance from NP Kunta was 5.37kms. At both ends, differential protection operated. At NP Kunta end, AR operated and the line tripped on persistent fault. At SB Energy end, AR did not operate and the line got tripped. | APSPCL to rectify the A/R issue at SB Energy end | APSPCL |  | Pending | Pending
137/IV/8 | 765KV-WARANGAL(NEW)-WARORA-1 | 02-11-2025 23:52 | As per the reports submitted, the triggering incident was B-N fault in the line. The fault distance from Warangal end was 287kms. At Warangal end, the fault was sensed in Zone-1. and AR did not operated a and 3-phase tripped | WKTL to rectify the A/R issue at Warangal end (New) | M/S WKTL | amarnaththiyagarajan:ADANI: 28/01/2026 16:36:56: We had mistakenly uploaded the wrong file earlier. The correct DR files were checked and sent mail to SRLDC Protection team on 18 December 2025. In which there was no Auto-Reclose (AR) issue. | Complied | Complied
137/IV/11 | 220KV-NP_KUNTA PSS3-NP_KUNTA-2 | 19-11-2025 05:50 | As per the reports submitted, the triggering incident was B-N fault in the line. The fault distance from NP_KUNTA PSS3 end was 0.9kms and from NP_KUNTA end it was 2.215kms. At NP_KUNTA PSS3 end, the fault was sensed in Zone-1 differential M1&M2 Relay acted. At NP_KUNTA end, the fault was sensed in Zone-1, A/R operated and the line was holding. | APSPCL to rectify the A/R issue at NP Kunta PSS end | APSPCL |  | Pending | Pending
137/VI/3 | 400KV-NCTPS_STAGE_II-SUNGAVARACHATRAM-2 | 24-10-2025 01:56 | 400KV-NCTPS_STAGE_II-SUNGAVARACHATRAM-2 | NCTPS to rectify the DR time synchronization issue at NCTPS_STAGE_II - 400KV. | NCTPS | aeswydmrtnctps2:TNPGCL: 07/03/2026 09:58:16: NEW GPS CLOCK HAS BEEN COMMISSIONED ON 04.11.2025 AND SUCCESSFULLY SYNCHRONIZED WITH EXISTING SCADA SYSTEM(SERVERS AND RELAYS). NOW ALL RELAYS ARE SYNCHRONIZED WITH GPS CLOCK. | Complied | Complied
137VI/6 | 220KV-NP_KUNTA-SBENERGY_NPK-1 | 25-10-2025 13:39 | 220KV-NP_KUNTA-SBENERGY_NPK-1 | APSPCL to rectify the DR time synchronization issue at SBENERGY_NPK - 220KV. | APSPCL |  | Pending | Pending
137/VI/14 | 400KV-LKPPL_STG2-VIJAYAWADA-1 | 02-11-2025 18:25 | 400KV-LKPPL_STG2-VIJAYAWADA-1 | LKPPL to rectify the DR time synchronization issue at LKPPL_STG2 - 400KV. | M/S LKPPL to rectify the DR time synchronization issue at LKPPL_STG2 - 400KV. |  | Pending | Pending
137/VI/15 | 765KV-WARANGAL(NEW)-WARORA-1 | 02-11-2025 23:52 | 765KV-WARANGAL(NEW)-WARORA-1 | WKTL to rectify the DR time synchronization issue at WARANGAL(NEW) - 765KV. | M/S WKTL | amarnaththiyagarajan:ADANI: 28/01/2026 16:31:25: The time synchronization issue observed in the DR has been successfully rectified. The DR time synchronization was checked and aligned with the substation master clock/GPS time source. Necessary configuration corrections were carried out, and the system has been verified for correct time stamping | Complied | Complied
138/I/2 | Complete outage of 230kV Spring_Pugalur of Spring_Pugalur | 26-11-2025 05:33 | 230kV Spring_Pugalur is radially connected through 230KV-PUGALUR-SPRING_PUGALUR-1. The triggering incident was Y-G fault in the line. The fault distance from Pugalur end was 3.7kms. At Pugalur end, the fault was sensed in Zone-1 and auto reclose operated and was successful and line was holding. At Spring Pugalur end, the fault was sensed in Zone-1 and AR did not get operated and 3ph tripped. Tripping of only one line connected to Spring_Pugalur led to the Complete outage of 230kV Spring_Pugalur of Spring_Pugalur. There was no generation at Spring_Pugalur during the event. | 1.Spring Pugalur to rectify the AR relay logics at their substation. 2.Insulator replacement to be completed | M/s Spring Pugalur | ramakrishnang:Sprng Energy Ltd(Pugalur): 24/02/2026 10:51:20: 1.) AR Logic Rectification completed in MAIN-01 Relay. 2.) 230KV Line Weak Insulator Replacement work completed on 04th and 5th Feb 2026 | Complied | Complied
138/III/9 | Tripping of Bhavini Siruseri | 03-12-2025 04:25 | As per the reports submitted, the triggering incident was YG fault in 230KV SHOLINGANALLUR-SIRUSERI 1 due to insulator failure in Loc. No41. At both ends, the fault was sensed in zone1. At Sholinganallur end, A/R operated and the line tripped on persistent fault. At Siruseri end, AR did not operate and the line tripped. At the same time, the same fault was sensed in zone1 in 220kV Bhavini Siruseri Line1 and B pole opened and all other poles tripped after 1200ms. The line was holding at Siruseri end. | BHAVINI to submit all relay settings to the PSSG forum for approval. | BHAVINI |  | Pending | Pending
138/III/14 | 400KV/33KV AMGEPL_SOLAR-ICT-2 | 12-12-2025 19:40 | As per the reports submitted, the triggering incident was Relay Maloperation. At AMGEPL end, ICT2 Tripped on Over flux trip. As per DR the phase voltages observed are Vr-411kV, Vy236kV, and Vb237.9kV. R-phase voltage is higher than other voltages in ICT but the same thing was not observed in PMU. | AMGEPL to submit the OEM report on the over flux tripping of the 400KV/33KV AMGEPL_SOLAR-ICT-2. | M/S AMGEPL |  | Pending | Pending
138/VI/11 | 220KV-RAICHUR_KA-UPPER_JURALA-1 | 14-12-2025 02:19 | DR time synchronization issue at RAICHUR_KA - 220KV | KPCL to rectify the DR time synchronization issue at RAICHUR_KA - 220KV | KPCL |  | Pending | Pending
139/I/5 | Spring Pugalur complete outage | 13-01-2026 06:17 | The triggering incident was R-G fault in 230KV-PUGALUR-SPRING_PUGALUR-1 line due to suspected R-phase insulator flash over. At Pugalur end, the fault was sensed in zone-1, A/R operated and the line was holding. At Sprng_Pugalur end, the fault was sensed in carrier aided zone-2 and the line tripped. A/R did not operate at Pugalur end. Tripping of only connected line led to loss of power supply to 230kV Sprng_Pugalur Wind plant. | Spring Pugalur to rectify the A/r logic at their end. | M/s Spring Pugalur |  | Pending | Pending
139/IV/5 | 400KV-KUDANKULAM-TUTICORIN_PS-2 | 12-01-2026 06:21 | As per the reports submitted, the triggering incident was R-N fault in the line. The fault distance from Kudankulam end was 27kms and from Tuticorin end it was 112.4kms. At Kudankulam end, the fault was sensed in Z1 and A/R did not operated and 3ph tripped. At Tuticorin end, the fault was sensed in Z1 and A/R operated but tripped due to persistent fault. | KKNPP advised to review the A/R operation in 400KV-KUDANKULAM-TUTICORIN_PS-2 line. | KKNPP | purvabhoj:NPCIL: 07/03/2026 13:40:05: Non operation of auto reclose during single phase trip was referred to OEM and A/R block logic modified as their recommendation. | Complied | Complied
139/VI/2 | 400KV-VALLUR-ALAMATHY-1 | 24-12-2025 03:49 | 400KV-VALLUR-ALAMATHY-1 | NTECL Vallur to rectify the DR time synchronization issue at 400kV Vallur | NTECL Vallur | cepc:TANTRANSCO: 04/03/2026 15:31:58: Bay owned by PGCIL. PGCIL has proposed to replace the relays | Pending | Pending
140/I/1 | Complete Outage of 220kV Kadra, Kodasalli and Karwar of KPTCL | 21-01-2026 09:23 | 220kV Kaiga Bus-1 and Bus-2 was planned to be under shutdown from 1000 hrs to 1600 hrs where in both the 220 kV Kaiga- Kadra and 220 kV Kaiga - Kodasalli had to be opened. In the antecedent condition 220kV Naghjeri-Kodasalli-1&2 were in idle charged condition. After the receipt of code for planned activity, the lines (220 kV Kaiga- Kadra and 220 kV Kaiga - Kodasalli) were opened (not in coordination) leading to the Complete Outage of 220kV Kadra, Kodasalli and Karwar of KPTCL | Kaiga GS to obtain codes from SRLDC and KAR SLDC while taking outages. | NPCIL Kaiga |  | Pending | Pending
140/I/1 | Complete Outage of 220kV Kadra, Kodasalli and Karwar of KPTCL | 21-01-2026 09:23 | 220kV Kaiga Bus-1 and Bus-2 was planned to be under shutdown from 1000 hrs to 1600 hrs where in both the 220 kV Kaiga- Kadra and 220 kV Kaiga - Kodasalli had to be opened. In the antecedent condition 220kV Naghjeri-Kodasalli-1&2 were in idle charged condition. After the receipt of code for planned activity, the lines (220 kV Kaiga- Kadra and 220 kV Kaiga - Kodasalli) were opened (not in coordination) leading to the Complete Outage of 220kV Kadra, Kodasalli and Karwar of KPTCL | SRLDC to bifurcate the Grid occurances into Protectional and operational issues, while furnishing the agenda. | SRLDC | ArthiV~1776856274:SRLDC: 04/04/2026 17:45:08: The Grid Disturbances classification is being done based on Grid standards. Any protection or operational issues are being mentioned in the points for review. | Pending | Pending
140/I/2 | Complete Outage of 230kV M/s Spring Pugalur Pugalur Wind station | 23-01-2026 00:35 | As per the reports submitted, at M/s Spring Pugalur Pugalur Wind Station, SVG lost communication at 00:29hrs causing SVG-1,2 &3 to inject reactive power causing voltage to shoot up to around 1.1PU. Immediately, Over voltage protection that was supposed to trigger only the DR has extended trip signal from Main-2(ABB REL 670 ) relay and the line tripped at M/s Spring Pugalur Pugalur end. DT was sent to Pugalur end and the line tripped at both ends. Tripping of only connected line led to loss of power supply to 230kV M/s Spring Pugalur Pugalur Wind station. | 1. M/s SPRNG Pugalur to rectify the MPPC logic in coordination with OEM. 2. M/s SPRNG Pugalur to disable the Over Voltage / Under voltage and Under frequency tripping of lines. | M/s SPRNG Pugalur |  | Pending | Pending
140/I/7 | Complete Outage of 220kV Vizag Steel SS of APTRANSCO | 06-02-2026 11:31 | 220kV Vizag Steel SS is connected to Vizag Switching Station through 220kV Vizag Steel-Vizag Switching Station-1&2 only. As per the reports submitted, the triggering incident was R-G fault in 220kV Bus of 220kV Vizag Steel SS. Immedeately, 220kV BBP operated and all elements connected to 220kV Bus tripped. However, the lines were holding from the remote ends. This led to complete outage of 220kV Vizag Steel SS. | 1. RINL VSP to submit complete DR files of the event to SRPC & SRLDC. 2. RINL VSP to periodically check and ensure proper CT connections in the switchyard. 3. RINL VSP to expedite the retroffiting of static relays with Numerical relays in the switchyard. 4. RINL VSP to rectify the DR time sync issue 5. RINL VSP to ensure double bus operation | M/s RINL VSP | dee2sp:APTRANSCO: 07/04/2026 14:53:22: PCSC/SRPC recommendations were communicated to M/s. RINL by OMC circle/Vizag and requested for pointwise compliance report from M/s. RINL. dee2sp:APTRANSCO: 09/04/2026 11:48:48: Remarks received from M/s RINL in response to the PCSC -140 recommendations is forwarded to SRPC by email on 09-04-2026 at 11:52 AM. | Pending | Pending
140/II/3 | Tripping of 400kV Bus-1 at Simhadri TPS of NTPC | 31-01-2026 18:04 | The triggering incident is the testing activity of CT after replacement of CT in 412 Bay at Simhadri TPS. Due to human error of testing activities, inadvertently current injection in the secondary side led to the operation BBP operation due to the imbalance and tripping of 400kV Bus-1 at Simhadri TPS. During the same time due to outage of tie breaker led to the tripping of Unit-1 at Simhadri leading to a generation loss of 450MW | NTPC Simhadri to strictly enforce SOP for CT secondary handling during testing activities. | NTPC Simhadri |  | Pending | Pending
140/III/7 | 400KV-NEYVELI_TS2_EXP-PUGALUR-1 | 28-01-2026 06:26 | As per the reports submitted, the triggering incident was B-G fault in the line. The fault distance from Neyveli end was 130.2 kms and from Pugalur end was 130 kms. At Neyveli end, both Main-1 and 2 relays sensed in Z1 fault. But in Main-2 relay CB R-ph pole was already sensed as open status. When B-ph pole was opened due to transient fault (Z1), the M2 relay sensed it as both pole (R & B) open. So M2 relay issued A/R block & A/R Lock out due to which 3-ph lock out operated and DT was sent to remote end. At Pugalur end, B phase single pole tripped but before operation of AR DT received from remote end causing 3 pole trip. | 1. NLC TS-2 EXP is advised to provide detailed report on the incident. 2. NLC TS-2 EXP to rectify the DR Time synch | NLC TS-2 EXP |  | Pending | Pending
140/VI/4 | 400KV-NEYVELI_TS2_EXP-PUGALUR-1 | 28-01-2026 06:26 | 400KV-NEYVELI_TS2_EXP-PUGALUR-1 | NEYVELI_TS2_EXP to rectify the DR time synchronization issue at NEYVELI_TS2_EXP - 400KV | NEYVELI_TS2_EXP |  | Pending | Pending
140/VI/7 | SIMHADRI - 400KV | 30-01-2026 11:08 | SIMHADRI - 400KV | NTPC SIMHADRI to rectify the DR time synchronization issue at SIMHADRI - 400KV | NTPC SIMHADRI |  | Pending | Pending
141/I/5 | Complete Outage 220kV Renew_Surya_Koppal of RENEW | 08-03-2026 05:49 | 220kV Renew_Surya_Koppal is connected radially to KOPPAL through 220KV-KOPPAL-Renew_Surya_Koppal-1. The triggering incident is the B-G fault in the 220KV-KOPPAL-Renew_Surya_Koppal-1 line and tripping of the only line connected to 220kV Renew_Surya_Koppal led to the Complete Outage 220kV Renew_Surya_Koppal of RENEW | 1.M/s Renew to submit detailed report for the event. 2.M/s Renew to Enable Auto reclosure for 220kV Koppal Renew Surya line. | M/s Renew |  | Pending | Pending
141/I/6 | Complete outage of 220kV SPRING_PUGALUR of SPRING | 11-03-2026 14:17 | 220kV SPRING_PUGALUR is connected radially to PUGALUR through 230KV-PUGALUR-SPRING_PUGALUR-1. The triggering incident is the B-G fault in the 230KV-PUGALUR-SPRING_PUGALUR-1 line and tripping of the only line connected to 220kV SPRING_PUGALUR led to the Complete outage of 220kV SPRING_PUGALUR of SPRING | Spring Pugalur to submit detailed report regarding non operation of AR in consulattion with OEM. | M/s Spring Pugalur |  | Pending | Pending
141/I/7 | Complete Outage of 220kV TP SAURYA of TATA POWER | 13-03-2026 15:07 | 220kV TP SAURYA is connected radially to KOPPAL through 220KV-TP SAURYA LIMITED-KOPPAL-1. The triggering incident is the B-G fault in the 220KV-TP SAURYA LIMITED-KOPPAL-1 line and tripping of the only line connected to 220kV TP SAURYA led to the Complete Outage of 220kV TP SAURYA of TATA POWER | 1.TATAPOWER to verify healthiness of the jumpers at all tower locations. 2.TATAPOWER to install pilot insulators for angle towers. 3.TATAPOWER to enable AR in coordination with Indigrid. 4.TATAPOWER to follow the IEGC mentioned timeline for furnish FIR, EL & DR to SRLDC | M/s TATAPOWER |  | Pending | Pending
141/III/8 | 220KV/33KV KSPPL-ICT-2 | 08-03-2026 10:24 | As per the reports submitted, the triggering incident is the 33kV downstream fault, during which 220KV/33KV KSPPL-ICT-2 tripped on Earth Fault Protection. | KLEIO Solar IS advised to conduct a detailed inspection of all isolator clamps and associated conductors in the switchyard to identify any loose connections, mechanical wear or deterioration. Necessary corrective actions shall be undertaken. | M/s KLEIO Solar |  | Pending | Pending
141/VI/12 | 400KV/230KV NTPL-ICT-1 | 04-03-2026 16:38 | Station at which DR time synchronisation was not observed NTPL - 400KV | NTPL to rectify the DR time synchronization issue at NTPL - 400KV | NTPL |  | Pending | Pending
141/VI/13 | 400KV-KAIGA-GUTTUR-2 | 13-03-2026 05:27 | Station at which DR time synchronisation was not observed KAIGA - 400KV | NPCIL KAIGA to rectify the DR time synchronization issue at KAIGA - 400KV | NPCIL KAIGA |  | Pending | Pending