BATTERY ENERGY STORAGE SYSTEMS (BESS)

# As per IEGC 2023 Part 6, hybrid RE and storage resources require special consideration due to their dynamic operational characteristics, fast ramping capability and interaction with grid voltage/reactive power.

# Therefore, before issuing connectivity approval, certain technical, operational, protection and compliance requirements must be validated to ensure grid safety, voltage stability, power quality and protection coordination in accordance with CEA & IEGC provisions.

# 2. Key Regulatory-Based Concerns Prior to Granting Grid Connectivity

# a) Grid Security, Stability & Ramp Control

# As per IEGC 2023 Part 6, Clauses on Active Power Control & Ramp Rate:

# Hybrid RE + BESS plants shall comply with mandated active power ramp limits, frequency control requirements, and must avoid sudden power surges or absorption.

# BESS operation shall not cause frequency excursion, uncoordinated charging or uncontrolled swings in output.

# As per CEA Grid Standards (2013), generating plants must operate without causing voltage fluctuations or disturbances.

# b) Protection Coordination Requirements

# As per CEA Connectivity Standards (2013 & amendments):

# The fault contribution and inverter-based protection settings of Wind/Solar/BESS inverters must comply with LVRT/HVRT, anti-islanding, O/V–U/V, and O/F–U/F protection norms.

# Hybrid developers must furnish:

# Fault-level calculations at 110/230 kV interface

# Relay coordination and grading study

# Islanding prevention scheme as per CEA Grid Safety Regulations.

# c) Voltage Regulation & Reactive Power Support

# As per IEGC 2023 Part 6 (Voltage & Reactive Power Requirements) and CEA Connectivity Standards:

# All inverter-based resources must operate within ±0.95 power factor at the interconnection point.

# Plants must provide dynamic reactive power support, including night/SVC/STATCOM capability, as applicable.

# Inverter/IBR must support grid voltage during disturbances (LVRT/HVRT).

# Hybrid developer shall furnish:

# VAR sizing study

# Capability curves of Solar, Wind and BESS inverters

# Details of external VAR compensators

# d) BESS SoC Management & Charge/Discharge Control

# In line with MoP Draft BESS Standards 2023/24 and IEGC 2023 Part 6:

# SoC control logic, charge/discharge limits and operational philosophy must be declared in advance.

# BESS in charge mode must not draw power during low-voltage or contingency events, in accordance with the general grid-safety requirement under CEA Grid Standards.

# EMS/HPC must restrict injection to approved capacity and follow SLDC scheduling instructions.

# e) Scheduling, Metering & Energy Accounting

# As per IEGC 2023 Chapter on Scheduling & CEA Metering Regulations:

# Hybrid + ESS must adhere to 15-minute scheduling, QCA-based aggregation, and RE forecasting requirements.

# Separate meters are required for:

# Solar Generation

# Wind Generation

# BESS Charging

# BESS Discharging

# Net Injection

# AMR/SCADA must comply with CEA Communication Standards 2020.

# COD certificate must confirm compliance with CEA Connectivity, Communication and Safety Standards.

# f) Transmission Infrastructure Adequacy

# As per CEA Connectivity & Grid Standards:

# Load flow studies must consider simultaneous Wind + Solar + BESS discharge.

# Transformer, bay equipment, CT/PT burden and STU substation ratings must be verified.

# g) SCADA, Telemetry & Cybersecurity

# As per CEA Communication Standards (2020) & IEGC 2023:

# Real-time data (MW, MVAR, SoC, inverter status, node voltages, alarms) must be provided to SLDC.

# BESS controller and HPC must comply with time-synchronization, redundancy & cybersecurity provisions.

# 3. Recommendations Prior to Issuing Grid Connectivity

# The following documents and studies are obtained:

# Hybrid plant design package

# SLD, capability curves, VAR study, protection study, metering arrangement

# Compliance report

# IEGC 2023 Part 6

# CEA Connectivity Standards

# CEA Safety & Communication Regulations

# SCADA/Telemetry readiness with SLDC

# Installation of harmonic filters, STATCOM/VAR support and HPC

# Load flow study demonstrating no overloading or voltage violation

# Developer undertaking confirming that:

# BESS will not charge without RLDC/SLDC approval

# All SLDC instructions will be followed in real time

# Battery Storage Support to Grid and DISCOM and recommendation of Best type of Battery in lieu with long life cycle and disposal mechanism shall be included in the Bid Document.

# 1. BESS Control & Communication Architecture

The BESS operates through a four-level hierarchical control architecture:

| Level | Layer | Key Functions |
| --- | --- | --- |
| Level 4 | Grid / SLDC Control | Real-time monitoring, dispatch & scheduling, BESS optimisation, ACE/frequency control, reserve management, congestion management |
| Level 3 | Control Centre (SCADA/EMS) | SCADA: Data acquisition, alarms, event records. EMS: Forecasting, optimisation, dispatch. FEP: Protocol conversion, time sync. Cyber security. |
| Level 2 | Plant Supervisory Layer | Central optimiser, SoC/SoH management, power dispatch, mode management (charge/discharge/standby), ramp rate, alarms, data logging |
| Level 1 | Unit Control Layer | BMS: Cell monitoring, SoC/SoH estimation, cell balancing. PCS: Active/reactive power control, FFR/PFR, grid-forming/following. Protection IEDs. |
| Field | Equipment / Power System | Battery racks/modules, DC combiner, PCS/inverter, step-up transformer, MV switchgear, grid interconnection point |

Communication protocols: IEC 60870-5-104 (SLDC/WAN), IEC 61850 / Modbus TCP (plant level), IEC 61850 (high-speed field level).

Key feedback signals include SoC, SoH, cell voltage/temperature, DC voltage/current, PCS P/Q/V/I, breaker status, alarms and weather/forecast inputs.

# 2. BESS Frequency Response – PFR & FFR

## 2.1 Operating Band and Deadband

- Nominal grid frequency: 50.000 Hz; Allowable operating band: 49.900 – 50.050 Hz.

- Deadband: ±0.03 Hz (49.97 – 50.03 Hz) — BESS does not respond within this band.

- Droop setting (R): 3–5%; Deadband: ±0.03 Hz; response symmetrical for over and under frequency.

## 2.2 Primary Frequency Response (PFR) – Droop Control

- Once frequency moves outside the deadband, droop control activates proportionally.

- Formula: P_droop(f) = 50 × (49.97 − f) for f < 49.97; P_droop(f) = −50 × (f − 50.03) for f > 50.03 (for 5% droop on 125 MW BESS → slope = 50 MW/Hz).

- BESS injects power (discharges) for low frequency; absorbs power (charges) for high frequency.

- PFR responds within 1–10 seconds after the disturbance.

## 2.3 Fast Frequency Response (FFR)

- FFR acts almost instantaneously (100 ms – 1 s) to arrest frequency decline or rise.

- Triggered when |df/dt| exceeds the RoCoF threshold (typically 0.5 Hz/s).

- Provides a fixed additional boost (approx. 18.75 MW on a 125 MW BESS) beyond the droop response.

- FFR is mandatory for Inverter-Based Resources (IBRs) as per CEA Connectivity Regulations.

## 2.4 Ancillary Service Timeline

- FFR: Fast arrest of frequency — 100 ms to 1 s.

- PFR (PRAS): Primary response to arrest & support — 1 to 10 s.

- SRAS: Restore frequency and reduce ACE — up to 15 min.

- TRAS: Replace secondary reserve support — up to 60 min.

## 2.5 SoC Window for Frequency Response

- Recommended operating SoC window: 20% – 80%.

- Ideal SoC for maximum flexibility: 40% – 60% (normal operating range).

- Above 80% SoC: Insufficient headroom to absorb power (high-frequency support unavailable).

- Below 20% SoC: Insufficient energy to inject power (low-frequency support unavailable).

- Reserve allocations (typical): PRAS 10–15%, SRAS 15–25%, TRAS 20–30% of BESS rated power.

## 2.6 Active Power Controller Block Diagram (Droop + FFR)

- Droop (PFR) Path: Measured frequency → Low Pass Filter → Deadband (±0.03 Hz) → Droop Gain (Kp = Pmax / (R × fnom)) → Droop PI Controller → P_droop.

- FFR Path: d/dt (High Pass Filter) → RoCoF computation → FFR Trigger (|df/dt| > Threshold) → FFR Shaping (Fast Ramp – Hold – Ramp) → FFR Gain (Kffr) → P_ffr.

- Combined output (P_droop + P_ffr) → Active Power PI (Plant Level) → Saturation Limiter (±Pmax) → Rate Limiter → SoC Limiter → P_ref.

# 3. Automatic Generation Control (AGC) for BESS

- BESS receives AGC setpoint (ΔPAGC) from SLDC EMS via SCADA/EMS interface (IEC 60870-5-104 / TCP-IP).

- BESS adjusts active power (charge or discharge) based on the AGC signal.

- Fast response: < 2 seconds; supports both up-regulation and down-regulation.

- AGC architecture uses Area Control Error (ACE) calculation: ACE = (P_actual − P_schedule) + B × (f − 50).

- Two-area model: SLDC/AGC controller manages tie-line dynamics (ΔPtie,12) and frequency deviation (Δf).

- BESS as AGC participant provides fast, precise regulation and improves frequency stability and reliability.

# 4. Reserve Management

## 4.1 Concept

- Up Reserve: Additional capacity available above scheduled generation to handle demand increase or generation trip.

- Down Reserve: Absorption capacity available below scheduled generation to handle generation surplus.

- BESS reserves should not be normally scheduled for routine operations; reserved only for contingencies.

## 4.2 Normal Condition (Reserves Adequate)

- Available Up Reserve ≥ Mandated Up Reserve Requirement → system is secure.

- Available Down Reserve ≥ Mandated Down Reserve Requirement → system is secure.

- BESS is NOT obligated for reserve and can be used for DSM, market operations, peak support, etc.

## 4.3 Reserve Shortfall Condition (Example: Mylatti 125 MW BESS)

- Up Reserve Shortfall: Mandated 300 MW; Generators provide 240 MW → Shortfall = 60 MW.

- SLDC instructs BESS to keep 60 MW earmarked as Up Reserve. Remaining BESS capacity for other uses = 65 MW.

- Down Reserve Shortfall: Mandated 200 MW; Generators provide 150 MW → Shortfall = 50 MW.

- SLDC instructs BESS to keep 50 MW charging headroom (absorption capability) as Down Reserve. BESS SoC maintained at 40–60%.

## 4.4 Combined Reserve Margin Example

- BESS capacity = 125 MW. Total reserve margin (Up + Down) required = 80 MW. Remaining for energy operations = 45 MW.

- SoC must be maintained in mid-range (40–60%) for bi-directional readiness.

- Reserved capacity released ONLY for real-time contingency events (FFR/Droop/Contingency).

# 5. DSM (Deviation Settlement Mechanism) / ACE Management

## 5.1 Key Concepts

- DSM: Financial penalty for deviating from schedule. ACE: Real-time control signal.

- ACE = (P_actual − P_schedule) + B × (f − 50). ACE > 0 → excess generation (BESS charges); ACE < 0 → deficit (BESS discharges).

# 6. Peak Demand Management

- Concept: Charge BESS during off-peak / low demand; discharge during peak / high demand.

- Charging Energy Requirement: To deliver 500 MWh during peak, total input energy = 500 / 0.90 × 1.02 ≈ 567 MWh.

- Charging Schedule (off-peak 6 hours): Required charging power = 567 / 6 ≈ 94.5 MW → Charge C-rate = 0.19C (within limit).

- Discharge Schedule (peak 4 hours, 18:00–22:00): Discharge power = 500 / 4 = 125 MW → C-rate = 0.25C (within limit).

- Result: Peak demand reduced by 125 MW; load curve flattened; DSM penalty avoided.

- SLDC finalises block-wise (15-min interval) input/output energy schedules considering RTE, C-rate and Aux Consumption.

# 7. Market Operation (DSM Rate-Based Economic Dispatch)

- During the first volume limit of DSM (small ACE), BESS can operate based on DSM rates for economic optimisation.

- Deficit + High DSM price → BESS discharges (injects power) to reduce deviation and avoid penalty.

- Deficit + Low DSM price → BESS may conserve SoC for critical events.

- Surplus + Low/Negative DSM price → BESS charges (absorbs power) economically.

- Layered strategy: Small deviation → Economic operation (DSM rate-based); Moderate → Partial correction; Large → Full correction (system security priority).

# 8. Congestion Deployment by SLDC

## 8.1 Congestion due to Excess Power Flow (Over-generation)

- BESS charges (absorbs power) at highest C-rate to reduce flow on the congested corridor.

## 8.2 Congestion due to Power Deficit / Reverse Flow

- BESS discharges (injects power) at highest C-rate to reduce dependency on the congested corridor.

## 8.3 Evacuation / Transmission Constraint

- BESS deployed for evacuation/transmission constraint must prioritise handling the constraint.

- If no constraint exists in real time, BESS can be re-purposed for peak shaving, market operations, reserve provision, or DSM support.

- Constraint status continuously monitored in real time by SLDC/RLDC.

# 9. Phasor Measurement Unit (PMU) Integration

- PMU installed at Point of Interconnection (POI); provides high-speed (25/50 samples/sec), time-synchronized measurements.

- Measured parameters: 3-phase voltage, 3-phase current, frequency, RoCoF, voltage/current phasor angle (δ), active power (P), reactive power (Q), UTC time.

- PMU data stream (IEEE C37.118 / IEC 61850-90-5) transmitted to PDC/Phasor Data Concentrator → SLDC/WAMS.

- Applications: Real-time grid monitoring, frequency & RoCoF monitoring, oscillation detection & damping, voltage stability assessment, dynamic state estimation, event detection & post-event analysis.

- Time synchronization via GPS / IRNSS.

# 10. Fault Ride Through (FRT) and Black Start

## 10.1 LVRT and HVRT Compliance

- BESS must comply with CEA 2019 Fault Ride Through (VRT) standards.

- LVRT: BESS must remain connected and support grid during voltage dips down to ~0.2 p.u. for up to ~0.625 seconds, then recover.

- HVRT: BESS must withstand over-voltage (up to ~1.3 p.u.) without tripping.

- BESS response must remain within the CEA Continuous Operation Zone during and after the fault.

## 10.2 Black Start – Grid-Forming (GFM) Capability

- GFM-capable BESS can perform black start restoration from 'cold start' (0 p.u. voltage).

- Sequence: Cold Start → GFM Voltage Source established → Bus Pressurize → Load Step (Steady State) → Grid Sync.

- Internal voltage rises rapidly to ~0.6 p.u. at cold start; system frequency stabilises at ~50 Hz throughout the sequence.

- Black start is enabled only where specified in the contract and required by the System Operator.

# 11. System Operation – Centralised BESS Optimisation at SLDC

- BESS can be operated by manual entry by System Operator (charge/discharge power MW, schedule, mode, priority) or through centralised dispatch via BESS Optimiser at SLDC.

- With multiple BESS at various locations, centralised optimisation is essential to avoid counter-dispatches among BESS units.

- SLDC BESS Optimiser: Aggregates data from all BESS, runs optimisation engine, handles constraints, generates coordinated schedules.

- Objectives may include: Peak Demand Management + ACE; Peak Demand Management + Market-Based; Congestion Management + Reserve Provision; or other combinations.

- Limiting constraints in optimisation: BESS technical limits (MW/MWh/SoC/ramp/C-rate), operational constraints (min/max SoC, efficiency/losses), time & schedule constraints, grid constraints (transmission/congestion/security), policy/market constraints (DSM rules, reserve requirements, regulatory directives).

# 12. Communication Architecture

- IEC 60870-5-104 (IEC 104): Between Control Centre (SCADA) and remote BESS Station (RTU) — via WAN or dedicated link.

- TCP/IP Protocol: Between RTU, PPC (Power Plant Controller), PCS and BESS equipment at the site.

- Data flow: Telemetry / Status / Alarms / Measurements from BESS to Control Centre; Control Commands / Setpoints / Dispatch from Control Centre to BESS.

- Firewall and cyber security at both Control Centre and BESS Station ends.

- Architecture enables secure bi-directional communication between SLDC and all BESS stations.