## Sheet 1
Reference Number | OCC Number | Name of Requesting Agency | Element Name | Owner | Daily/ Continous | Reason | From Date | From Time | To Date | To Time | Requester Remarks | Availing Status | RLDC Status | RLDC Remarks | Element Type | Availing Request Date | Availing Request Time | RLDC Action Date | RLDC Action Time
RQ106949 | OCC_237 | TGTRANSCO | 132KV-MADIRA-CHILLAKALLU-1 | APTRANSCO,TGTRANSCO | C | for bay Quarterly & Yearly maintenance work and MRT Testings | 2026-05-30 | 10:00 | 2026-05-30 | 13:00 |  | Yes | Approved | Load Management need to be done by AP and TG. | Line Circuits | 26-May-2026 | 17:47 | 27-May-2026 | 11:26
RQ106926 | OCC_237 | PGCIL SR-1 | RAICHUR_PG - 765KV - BUS 2 | PGCIL SR-1 | C | For 765KV Raichur-Koppal line construction works | 2026-05-30 | 07:00 | 2026-05-31 | 19:00 | Construction works | Yes | Rejected | Due to Multiple Inter regional shutdowns and overlapping 765kV elements having impact on N-1 contingency. other elements planned are as follows: 765KV-WARANGAL(NEW)-WARORA-2 765kV-KURNOOL - NPS -2. Element already under shutdown: 400kV-GAZUWAKA - JEYPIRE D/C | Bus | 26-May-2026 | 16:21 | 27-May-2026 | 12:43
RQ106810 | OCC_237 | kptcl | 400KV/220KV DEVANAHALLI-ICT-3 | KPTCL | D | quarterly maintenance work | 2026-05-30 | 08:00 | 2026-05-30 | 18:00 |  | Yes | Approved | Load Management need to be done by KPTCL. N-1 limit for DEVANAHALLI and HOODY ICTs is 333 MW each. Subject to ICT loadings of HOODY ICTs and DEVANAHALLI ICTs shall be within their N-1 limits. HOODY ICTs are loading near to their N-1 limits on weekends. 400KV/220KV DEVANAHALLI-ICT-1,2 33% each 400KV/220KV HOODY-ICT-1,2,3 6% each 400KV-DEVANAHALLI-HOODY D/C 10% each shall be in service. | Transformer | 26-May-2026 | 13:36 | 27-May-2026 | 12:37
RQ108954 | PNOCC | KSPDCL | PAVAGADA_PG - 220KV - BUS 4 | PGCIL SR-2 | C | For Jumper Connection from BUS-4 to Newly constructed Bay 230 isolator(89B) terminals | 2026-05-26 | 18:00 | 2026-05-27 | 02:00 |  | Yes | Approved | Remaining all elements shall be in service. | Bus | 16-May-2026 | 16:43 | 23-May-2026 | 16:29
RQ106532 | OCC_237 | kseb | 400KV/220KV MADAKKATHARA-ICT-1 | KSEB | D | For conducting RLA study of ICT No.1 | 2026-05-30 | 08:00 | 2026-05-30 | 17:00 | For conducting RLA study of ICT No.1 | No | Rejected | Deferred by requester. | Transformer | 26-May-2026 | 11:39 | 27-May-2026 | 11:12
RQ106517 | OCC_237 | TANTRANSCO | VELLALAVIDUTHI - 400KV B/R 1 | TAMILNADU | D | Monthly Maintenance work | 2026-05-30 | 09:00 | 2026-05-30 | 17:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Bus Reactor | 26-May-2026 | 11:08 | 27-May-2026 | 11:21
RQ106465 | OCC_237 | WKTL | 765KV-WARANGAL(NEW)-WARORA-2 | WKTL | C | For 24Hrs. Trail Run of NGR Bypass at Warora end | 2026-05-30 | 08:00 | 2026-05-31 | 08:00 | For 24Hrs. Trail Run of NGR Bypass at Warora end | Yes | Approved | TTC reduction of 700 MW / 150 MW in NEW-SR Import / Export. Healthiness of other circuit need to be ensured prior to the shutdown in view of frequent tripping of the line in recent past. 765kV-WARANGAL-WARORA-1 tripped on R-B fault on 25.05.2026 at 14:51 HRS and charged back at 18:55 HRS on the same day. Subject to NLDC approval and real time grid conditions. 765KV-WARANGAL(NEW)-WARORA-1 35% 765kV-SOLAPUR - RAICHUR_PG D/C 12% each 765kV-WARDHA - NIZAMABAAD D/C 12% each 765kV-RAICHUR - KURNOOL_PG D/C 9% each 765kV-NIZAMABAAD - MAHESHWARAM D/C 8% each All 765kV/400kV WARANGAL and RAICHUR and NIZAMABAAD ICTs shall be in service. | Line Circuits | 26-May-2026 | 10:27 | 27-May-2026 | 12:43
RQ109339 | PNOCC | aptransco | A/R of 400KV-NARNOOR-GHANI-1 | APTRANSCO | D | for hotline stringing of 400 KV TMSC Line from Nagaluti Solar PSS to Central Pooling Switching Station (CPSS) by M/s Greenko Pvt Ltd across 400KV Narnoor-Ghani QMDC Line between locations 37-38 | 2026-05-30 | 08:00 | 2026-05-30 | 18:00 |  | Yes | Rejected | Details of work, No of days for A/R off along with all other relevant details need to be shared. Feasibility for availing the A/R off after 12:30 HRS also need to be shared. | Auto Reclosure | 25-May-2026 | 18:55 | 27-May-2026 | 11:29
RQ109342 | PNOCC | aptransco | A/R of 400KV-NARNOOR-GHANI-2 | APTRANSCO | D | for hotline stringing of 400 KV TMSC Line from Nagaluti Solar PSS to Central Pooling Switching Station (CPSS) by M/s Greenko Pvt Ltd across 400KV Narnoor-Ghani QMDC Line between locations 37-38 | 2026-05-30 | 08:00 | 2026-05-30 | 18:00 |  | Yes | Rejected | Details of work, No of days for A/R off along with all other relevant details need to be shared. Feasibility for availing the A/R off after 12:30 HRS also need to be shared. | Auto Reclosure | 25-May-2026 | 18:55 | 27-May-2026 | 11:29
RQ109338 | PNOCC | aptransco | A/R of 400KV-NARNOOR-GHANI-1 | APTRANSCO | D | for hotline stringing of 400 KV TMSC Line from Nagaluti Solar PSS to Central Pooling Switching Station (CPSS) by M/s Greenko Pvt Ltd across 400KV Narnoor-Ghani QMDC Line between locations 37-38 | 2026-05-29 | 08:00 | 2026-05-29 | 18:00 |  | Yes | Rejected | Details of work, No of days for A/R off along with all other relevant details need to be shared. Feasibility for availing the A/R off after 12:30 HRS also need to be shared. | Auto Reclosure | 25-May-2026 | 18:55 | 26-May-2026 | 17:34
RQ109340 | PNOCC | aptransco | A/R of 400KV-NARNOOR-GHANI-1 | APTRANSCO | D | for hotline stringing of 400 KV TMSC Line from Nagaluti Solar PSS to Central Pooling Switching Station (CPSS) by M/s Greenko Pvt Ltd across 400KV Narnoor-Ghani QMDC Line between locations 37-38 | 2026-05-31 | 08:00 | 2026-05-31 | 18:00 |  | Yes | Rejected | Details of work, No of days for A/R off along with all other relevant details need to be shared. Feasibility for availing the A/R off after 12:30 HRS also need to be shared. | Auto Reclosure | 25-May-2026 | 18:55 | 28-May-2026 | 10:29
RQ109341 | PNOCC | aptransco | A/R of 400KV-NARNOOR-GHANI-2 | APTRANSCO | D | for hotline stringing of 400 KV TMSC Line from Nagaluti Solar PSS to Central Pooling Switching Station (CPSS) by M/s Greenko Pvt Ltd across 400KV Narnoor-Ghani QMDC Line between locations 37-38 | 2026-05-29 | 08:00 | 2026-05-29 | 18:00 |  | Yes | Rejected | Details of work, No of days for A/R off along with all other relevant details need to be shared. Feasibility for availing the A/R off after 12:30 HRS also need to be shared. | Auto Reclosure | 25-May-2026 | 18:55 | 26-May-2026 | 17:34
RQ109343 | PNOCC | aptransco | A/R of 400KV-NARNOOR-GHANI-2 | APTRANSCO | D | for hotline stringing of 400 KV TMSC Line from Nagaluti Solar PSS to Central Pooling Switching Station (CPSS) by M/s Greenko Pvt Ltd across 400KV Narnoor-Ghani QMDC Line between locations 37-38 | 2026-05-31 | 08:00 | 2026-05-31 | 18:00 |  | Yes | Rejected | Details of work, No of days for A/R off along with all other relevant details need to be shared. Feasibility for availing the A/R off after 12:30 HRS also need to be shared. | Auto Reclosure | 25-May-2026 | 18:55 | 28-May-2026 | 10:29
RQ106444 | OCC_237 | TANTRANSCO | 230KV-KARAIKUDI-PUDUKKOTTAI | TANTRANSCO | D | Monthly Maintenance and Line Maintenance work | 2026-05-29 | 16:30 | 2026-05-29 | 20:00 |  | Yes | Approved | Shutdown to be availed after 16:30 HRS. 400KV-VELLALAVIDUTHI-KARAIKUDI-1 20% 400KV-KARAIKUDI-TRICHY-1 18% 230KV-TRICHY-ALUNDUR-2 15% 230KV-TRICHY-ALUNDUR-3 15% 230KV-KARAMBAYAM-KARAIKUDI(TN)-1 13% 230KV-KARAMBAYAM-KARAIKUDI(TN)-2 12% 400KV-KANARPATTI-TIRUNELVELI-1 9% 400KV-PUGALUR-KARAIKUDI-1 8% All VELLALVIDUTHI and TRICHY ICTs shall be in service. | Line Circuits | 25-May-2026 | 18:46 | 26-May-2026 | 17:19
RQ106824 | OCC_237 | TANTRANSCO | KAYATHAR - 400KV - BUS 2 | TANTRANSCO | D | For providing jumper from 400KV BUS 2 to 400KV Isolator [420-89A] of New ICT5 bay | 2026-05-29 | 10:00 | 2026-05-29 | 14:00 | There will be no interruption to ICT2&ICT4 , 400KV Karaikudi #1, 400KV Kanarpatti #2 & 400KV Thennampatti # as the load will be fed by concerned Tie Breakers[411-52] for ICT2, [405-52] for ICT4, [408-52] for 400 KV Karaikudi #2, [402-52] for 400KV Kanarpatti #1, [417-52] for 400KV Thennampatti#. The 400KV Isolator [420-89A] will be kept opened after providing jumper from 400KV BUS 2 | Yes | Rejected | May be availed after peak wind season of SR. | Bus | 25-May-2026 | 18:46 | 26-May-2026 | 17:19
RQ106480 | OCC_237 | TANTRANSCO | 400KV/110KV KANARPATTI-ICT-5 | TANTRANSCO | D | Monthly Maintenance work | 2026-05-29 | 17:00 | 2026-05-29 | 20:00 |  | Yes | Approved | Load Management need to be done by TN. Shutdown to be given only after 17:00 HRS. N-1 limit for 400KV/110KV KANARPATTI ICTs is 144 MW each. | Transformer | 25-May-2026 | 18:46 | 26-May-2026 | 17:00
RQ106487 | OCC_237 | TANTRANSCO | 400KV/110KV KAYATHAR-ICT-4 | TANTRANSCO | D | Monthly Maintenance work | 2026-05-29 | 14:00 | 2026-05-29 | 20:00 |  | Yes | Rejected | Shutdown already facilitated on 25.05.2026 for parallel operation testing of 400kV/110kV KAYATHAR ICT-5. | Transformer | 25-May-2026 | 18:46 | 26-May-2026 | 10:42
RQ106508 | OCC_237 | TANTRANSCO | 400KV/110KV THENNAMPATTY-ICT-4 | TANTRANSCO | D | Monthly Maintenance Work | 2026-05-29 | 17:00 | 2026-05-29 | 20:00 |  | Yes | Approved | Load Management need to be done by TN. Shutdown to be given only after 17:00 HRS. N-1 limit for 400KV/110KV THENNAMAPATTY ICTs is 95 MW each. | Transformer | 25-May-2026 | 18:46 | 26-May-2026 | 17:00
RQ106518 | OCC_237 | TANTRANSCO | 400KV-PUGALUR-VELLALAVIDUTHI-1 L/R@ VELLALAVIDUTHI - 400KV | TANTRANSCO | D | Monthly Maintenance work | 2026-05-29 | 09:00 | 2026-05-29 | 17:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Line Reactor | 25-May-2026 | 18:46 | 26-May-2026 | 10:46
RQ109302 | PNOCC | PGCIL SR-2 | MAIN BAY (401) OF 400KV-KARAIKUDI-TRICHY-1 AND KARAIKUDI - 400KV - BUS 1 @KARAIKUDI - 400KV | PGCIL SR-2 | C | for AMP works. | 2026-05-29 | 09:00 | 2026-05-29 | 18:00 | NIL | Yes | Approved | Remaining bays shall be in service. | Bay | 24-May-2026 | 20:51 | 25-May-2026 | 10:13
RQ106959 | OCC_237 | TGTRANSCO | 400KV-YADADRI TPP-CHOUTUPPAL-2 | TGTRANSCO | C | For periodical testing and general maintenance | 2026-05-29 | 10:00 | 2026-05-29 | 18:00 |  | Yes | Approved | 400KV-CHOUTUPPAL-YADADRI TPP-1 55% 400KV-YADADRI TPP-DINDI D/C 18% each 400KV-MAHESHWARAM_TG-MAMIDAPALLI D/C 10% each shall be in service. | Line Circuits | 25-May-2026 | 15:06 | 26-May-2026 | 17:12
RQ107062 | OCC_237 | PGCIL SR-2 | PAVAGADA_PG - 220KV - BUS 4 | PGCIL SR-2 | C | Connection of Jumpers with new Bay and Carrying out 220 kV Bus Bar-4 Stability Tests under ICT‑07 construction works. | 2026-05-29 | 17:00 | 2026-05-29 | 23:59 |  | No | Rejected | Deferred by requester. | Bus | 25-May-2026 | 14:08 | 26-May-2026 | 10:37
RQ106627 | OCC_237 | kseb | 220KV-KADAKOLA-KANIYAMPETTA | KPTCL,KSEB | D | Routine Maintenance, Relay & PET Testing | 2026-05-29 | 09:00 | 2026-05-29 | 17:00 | Routine Maintenance, Relay & PET Testing | Yes | Approved | Load Management to be done by KA and KL, Subject to real time voltage conditions near Mysore Area. No N-1 for 220kV KANIYAMPETA S/S. 220kV-MYSORE-KADAKOLA D/C 400kV-MYSORE-KOZHIKODE D/C 220kV-HOOTAGALLY - VAJAMANGALA 220kV-MYSORE-HOOTAGALLY D/C All MYSORE and BIDADI ICTs shall be in service. voltage dip of around 2kV is expected at 220kV-BEGUR, CHAMARAJANAGAR, ADAKANAHALLI, MADUVANAHALLI, HEBBANI, TK HALLI, VAJAMANGALA S/S. | Line Circuits | 25-May-2026 | 11:14 | 26-May-2026 | 18:02
RQ106585 | OCC_237 | aptransco | 132KV-PAMMY-CHILLAKALLU-1 | TGTRANSCO | D | Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | 2026-05-29 | 08:00 | 2026-05-29 | 18:00 | Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | Yes | Approved | Load management to be done by AP & TG for multiple outages | Line Circuits | 25-May-2026 | 10:59 | 26-May-2026 | 10:37
RQ106595 | OCC_237 | aptransco | 132KV-CHILLAKALLU-PEDAGOPATHI-1 | APTRANSCO,TGTRANSCO | D | D/C line Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | 2026-05-29 | 08:00 | 2026-05-29 | 18:00 | D/C line Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | Yes | Approved | Load management to be done by AP & TG for multiple outages | Line Circuits | 25-May-2026 | 10:59 | 26-May-2026 | 10:37
RQ106551 | OCC_237 | aptransco | 400KV-KRISHNAPATNAM-RACHAGUNNERI-1 | APTRANSCO | D | Tightening of spacer dampers and providing of missing keepers to dampers between locno:87 to 90, arranging repair sleeves to conductor damages between loc. No:87- 88 bottom phase in 400KV KrishnapatnamRachagunneri-1 feeder. | 2026-05-29 | 07:00 | 2026-05-29 | 17:00 | During the LC period there will be no interruption to loads as 400KV Krishnapatnam TPP - Manubolu feeder, 400KV SEIL – Manubolu feeder, 400KV Krishnapatnam-SEIL feeder and 400KV Krishnapatnam TPP – Rachagunneri - 2 feeders will be in Service. | Yes | Approved | 400KV-RACHAGUNNERI-KRISHNAPATNAM-2 44% 400KV-KRISHNAPATNAM-NELLORE_AP-1 30% 400KV-SEILU2_AP-NELLORE_AP-1 26% 400KV-TVLM-CHITTOOR D/C 11% each All NELLORE_AP ICTs shall be in service. | Line Circuits | 25-May-2026 | 10:59 | 26-May-2026 | 16:51
RQ106704 | OCC_237 | aptransco | 400KV-GUDDIGUDEM-KV_KOTA-2 | APTRANSCO | D | For periodical testing of equipment and relays by MRT | 2026-05-29 | 09:00 | 2026-05-29 | 17:00 | Annual maintenance works | Yes | Approved | 400KV-GUDDIGUDEM-KV_KOTA-1 71% 400KV-GUDDIGUDEM-HINDUJA D/C 8% each 400KV-VTPS_IV-VIJAYAWADA-1 3% All K V KOTA ICTs shall be in service. | Line Circuits | 25-May-2026 | 10:59 | 26-May-2026 | 17:02
RQ106646 | OCC_237 | aptransco | 400KV/220KV SATTENPALLY-ICT-2 | APTRANSCO | D | For Bays maintenance works and MRT works | 2026-05-29 | 09:00 | 2026-05-29 | 17:00 | Annual maintenance works | Yes | Rejected | Multiple shutdowns at the same station. | Transformer | 25-May-2026 | 10:59 | 26-May-2026 | 10:46
RQ106672 | OCC_237 | aptransco | KALPAKKA - 400KV - BUS 6 | APTRANSCO | D | For general maintenance of yard equipment and for periodical bay equipment and relay testing. | 2026-05-29 | 09:00 | 2026-05-29 | 17:00 | Annual maintenance works | Yes | Approved | All other elements shall be in service except ongoing shutdown of 400kV-KALPAKKA-KHAMMAM, and 400kV-KALPAKKA-ASUPAKA. | Bus | 25-May-2026 | 10:59 | 26-May-2026 | 17:28
RQ109305 | PNOCC | WKTL | KUDGI_PG - 400KV - BUS 2 | PGCIL SR-2 | C | Extension/Interconnection of400kv Main Bus-2 from existing PGCIL Kudgi to WRSR New Narendra. | 2026-05-29 | 00:00 | 2026-05-30 | 18:00 | Outage of 400kV Bus-2 approved from 11.05.26 to 16.05.26, not avail due to on going 400kV Bus 1 outage. Hence reschedule from 25.05.26 to 30.05.26 | Yes | Approved | Concurred for ICT-3 and ICT-4 Interconnection works. All elements shall be in service. | Bus | 25-May-2026 | 10:02 | 26-May-2026 | 10:40
RQ109306 | PNOCC | WKTL | TIE BAY (420) OF 400KV-KOPPAL-KUDGI_PG-1 AND 400KV/220KV KUDGI_PG-ICT-3 @KUDGI_PG - 400KV | KNTL | C | Extension/Interconnection of 400kv Main Bus-2 from existing PGCIL Kudgi to WRSR New Narendra. | 2026-05-29 | 00:00 | 2026-05-30 | 18:00 | Outage of 400kV Bus-2 approved from 11.05.26 to 16.05.26, not avail due to on going 400kV Bus 1 outage. Hence reschedule from 25.05.26 to 30.05.26 | Yes | Approved | CEA safety approval submitted. Remaining bays shall be in service. ICT-3 is a future element. | Bay | 25-May-2026 | 10:22 | 26-May-2026 | 10:40
RQ109307 | PNOCC | WKTL | MAIN BAY (421) OF 400KV/220KV KUDGI_PG-ICT-3 AND KUDGI_PG - 400KV - BUS 2 @KUDGI_PG - 400KV | KNTL | C | Extension/Interconnection of 400kv Main Bus-2 from existing PGCIL Kudgi to WRSR New Narendra. | 2026-05-29 | 00:00 | 2026-05-30 | 18:00 | Outage of 400kV Bus-2 approved from 11.05.26 to 16.05.26, not avail due to on going 400kV Bus 1 outage. Hence reschedule from 25.05.26 to 30.05.26 | Yes | Approved | CEA safety approval submitted. Remaining bays shall be in service. ICT-3 is a future element. | Bay | 25-May-2026 | 10:22 | 26-May-2026 | 10:40
RQ109308 | PNOCC | WKTL | TIE BAY (423) OF 400KV-KOPPAL-KUDGI_PG-2 AND 400KV/220KV KUDGI_PG-ICT-4 @KUDGI_PG - 400KV | KTL | C | Extension/Interconnection of 400kv Main Bus-2 from existing PGCIL Kudgi to WRSR New Narendra. | 2026-05-29 | 00:00 | 2026-05-30 | 18:00 | Outage of 400kV Bus-2 approved from 11.05.26 to 16.05.26, not avail due to on going 400kV Bus 1 outage. Hence reschedule from 25.05.26 to 30.05.26 | Yes | Approved | CEA safety approval submitted. Remaining bays shall be in service. ICT-4 is a future element. | Bay | 25-May-2026 | 10:22 | 26-May-2026 | 10:40
RQ109309 | PNOCC | WKTL | MAIN BAY (424) OF 400KV/220KV KUDGI_PG-ICT-4 AND KUDGI_PG - 400KV - BUS 2 @KUDGI_PG - 400KV | KTL | C | Extension/Interconnection of 400kv Main Bus-2 from existing PGCIL Kudgi to WRSR New Narendra. | 2026-05-29 | 00:00 | 2026-05-30 | 18:00 | Outage of 400kV Bus-2 approved from 11.05.26 to 16.05.26, not avail due to on going 400kV Bus 1 outage. Hence reschedule from 25.05.26 to 30.05.26 | Yes | Approved | CEA safety approval submitted. Remaining bays shall be in service. ICT-4 is a future element. | Bay | 25-May-2026 | 10:22 | 26-May-2026 | 10:40
RQ106894 | OCC_237 | PGCIL SR-1 | 400KV-NARNOOR-MAHESHWARAM_PG-1 | POWERGRID | C | Construction of 765kV Bidar-Maheshwaram Line at AP128-AP129 location | 2026-05-28 | 06:00 | 2026-05-31 | 18:00 | Construction works | No | Rejected | Deferred by requester. | Line Circuits | 24-May-2026 | 18:45 | 25-May-2026 | 10:03
RQ106659 | OCC_237 | aptransco | 400KV/220KV URAVAKONDA-ICT-4 | APTRANSCO | D | "1. Half yearly Maintenance works 2. Periodical Relay testing of ICT *Note : ICT-1,2&3 Will be in service" | 2026-05-28 | 09:00 | 2026-05-28 | 15:00 | Annual maintenance works | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. Load Management need to be done by AP. Timelines to be strictly adhered. N-1 limit for URAVAKONDA ICTs is 207 MW for 315 MVA ICT each and 329 MW for 500 MVA ICT each. 400KV/220KV URAVAKONDA-ICT-3 38% 400KV/220KV URAVAKONDA-ICT-1,2 24% each All CUDDAPAH ICTs shall be in service. | Transformer | 24-May-2026 | 10:44 | 25-May-2026 | 10:48
RQ106584 | OCC_237 | aptransco | 132KV-PAMMY-CHILLAKALLU-1 | TGTRANSCO | D | Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | 2026-05-28 | 08:00 | 2026-05-28 | 18:00 | Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | Yes | Approved | Load management to be done by AP & TG for multiple outages | Line Circuits | 24-May-2026 | 10:44 | 25-May-2026 | 10:03
RQ106594 | OCC_237 | aptransco | 132KV-CHILLAKALLU-PEDAGOPATHI-1 | APTRANSCO,TGTRANSCO | D | D/C line Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | 2026-05-28 | 08:00 | 2026-05-28 | 18:00 | D/C line Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | Yes | Approved | Load management to be done by AP & TG for multiple outages | Line Circuits | 24-May-2026 | 10:44 | 25-May-2026 | 10:03
RQ106725 | OCC_237 | TANTRANSCO | 230KV-KAYATHAR(TN)-TIRUNELVELI-1 | TANTRANSCO | D | Monthly Maintenance Work | 2026-05-27 | 09:00 | 2026-05-27 | 17:00 |  | Yes | Rejected | Due to very high line loadings. In case of shutdown the same will burden already loaded 400KV-KANARPATTI-TIRUNELVELI-1 30%. May be availed after peak wind season of SR. | Line Circuits | 23-May-2026 | 23:14 | 24-May-2026 | 11:32
RQ106477 | OCC_237 | TANTRANSCO | 400KV/110KV KANARPATTI-ICT-4 | TANTRANSCO | D | Monthly Maintenance work | 2026-05-27 | 14:00 | 2026-05-27 | 18:00 |  | Yes | Approved | Load Management need to be done by TN. N-1 limit for 400KV/110KV KANARPATTI-ICTs is 140 MW each. Timelines to be adhered. | Transformer | 23-May-2026 | 23:14 | 24-May-2026 | 10:57
RQ106814 | OCC_237 | kptcl | GUTTUR - 400KV B/R 2 | KPTCL | D | 1st Quarter Maintenance | 2026-05-27 | 10:00 | 2026-05-27 | 17:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Bus Reactor | 23-May-2026 | 22:39 | 24-May-2026 | 10:44
RQ106923 | OCC_237 | PGCIL SR-1 | NAGARJUNASAGAR_PG - 400KV - BUS 2 | PGCIL SR-1 | C | Bus Bar Relay testing works | 2026-05-27 | 09:00 | 2026-05-28 | 18:00 | Circular compliance/Scheme Modification works. | No | Rejected | Deferred by requester. | Bus | 23-May-2026 | 16:32 | 24-May-2026 | 10:15
RQ107061 | OCC_237 | PGCIL SR-2 | PAVAGADA_PG - 220KV - BUS 3 | PGCIL SR-2 | C | Connection of Jumpers with new Bay and Carrying out 220 kV Bus Bar-3 Stability Tests under ICT‑07 construction works. | 2026-05-27 | 17:00 | 2026-05-27 | 23:59 |  | No | Rejected | Deferred by requester. | Bus | 23-May-2026 | 16:27 | 24-May-2026 | 10:15
RQ107524 | OCC_2371 | PGCIL SR-2 | 400KV-KOPPAL-KUDGI_PG-1 | KNTL | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 9/0 - 10/0 | 2026-05-27 | 08:00 | 2026-05-27 | 19:00 | 400KV-KOPPAL-KUDGI_PG- D/C Outage is required to carry out powerline crossing works. Concurrence from connected IPPs will be submitted on D-4 basis. | Yes | Rejected | Due to Multiple shutdowns at the same station. 400kV-KOPPAL-GADAG D/C is out due to tower collapse. | Line Circuits | 23-May-2026 | 16:27 | 24-May-2026 | 10:17
RQ107526 | OCC_2371 | PGCIL SR-2 | 400KV-KOPPAL-KUDGI_PG-2 | KNTL | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 9/0 - 10/0 | 2026-05-27 | 08:00 | 2026-05-27 | 19:00 | 400KV-KOPPAL-KUDGI_PG- D/C Outage is required to carry out powerline crossing works. Concurrence from connected IPPs will be submitted on D-4 basis. | Yes | Rejected | Due to Multiple shutdowns at the same station. 400kV-KOPPAL-GADAG D/C is out due to tower collapse. | Line Circuits | 23-May-2026 | 16:27 | 24-May-2026 | 10:17
RQ107060 | OCC_237 | PGCIL SR-2 | KOZHIKODE - 400KV - BUS 1 | PGCIL SR-2 | D | AMP works of 400 kV Bus-1 | 2026-05-27 | 09:00 | 2026-05-27 | 17:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Bus | 23-May-2026 | 16:27 | 24-May-2026 | 10:44
RQ106408 | OCC_237 | TANTRANSCO | 400KV-PALAVADI-RASIPALYAM-2 L/R@ RASIPALYAM - 400KV | TANTRANSCO | D | Preventive maintenance for bay equipments, Reactor maintenance and P&C testing work. | 2026-05-27 | 09:00 | 2026-05-27 | 17:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Line Reactor | 23-May-2026 | 14:29 | 24-May-2026 | 10:20
RQ106593 | OCC_237 | aptransco | 132KV-CHILLAKALLU-PEDAGOPATHI-1 | APTRANSCO,TGTRANSCO | D | D/C line Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | 2026-05-27 | 08:00 | 2026-05-27 | 18:00 | D/C line Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | Yes | Approved | Load management to be done by AP & TG for multiple outages | Line Circuits | 23-May-2026 | 13:26 | 24-May-2026 | 10:17
RQ106648 | OCC_237 | aptransco | 400KV/220KV NARNOOR-ICT-1 | APTRANSCO | D | For Annualy and Quarterly maintenance works(for ICT Testings) | 2026-05-27 | 10:00 | 2026-05-27 | 16:00 | Annual maintenance works | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. Load Management need to be done by AP. N-1 limit for NARNOOR ICTs is 200 MW for 315 MVA ICT each and 316 MW for 500 MVA ICT. 400KV/220KV NARNOOR-ICT-2 34% 400KV/220KV NARNOOR-ICT-3 34% All GOOTY ICTs 400KV-KURNOOL_PG-NARNOOR D/C shall be in service. | Transformer | 23-May-2026 | 13:26 | 24-May-2026 | 10:57
RQ106583 | OCC_237 | aptransco | 132KV-PAMMY-CHILLAKALLU-1 | TGTRANSCO | D | Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | 2026-05-27 | 08:00 | 2026-05-27 | 18:00 | Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | Yes | Approved | Load management to be done by AP & TG for multiple outages | Line Circuits | 23-May-2026 | 13:18 | 24-May-2026 | 10:17
RQ106536 | OCC_237 | kseb | 400KV/220KV MADAKKATHARA-ICT-2 | KSEB | D | For conducting RLA study ICT No.2 | 2026-05-27 | 08:00 | 2026-05-27 | 17:00 | For conducting RLA study ICT No.2 | Yes | Approved | Load Management need to be done by KSEB. S3- 300 MW import ATC reduction. N-1 limit for MADAKKATHARA ICTs is 235 MW each. 400KV/220KV MADAKATHARA-ICT-1,3 25% each All PALAKKAD and KOZHIKODE ICTs shall be in service along with 220KV-ELANKUR-AREACODE-1 10% 220KV-ELAPULLY-MADAKATHARA-1 9% 220KV-PALAKKAD(KL)-MADAKATHARA-1 9% 220KV-MADAKATHARA-LOWER PERIYAR-1 8% 400KV-KOZHIKODE-MADAKKATHARA D/C 7% each 220KV-KOZHIKODE-AREACODE D/C 4% each. | Transformer | 23-May-2026 | 10:43 | 24-May-2026 | 10:18
RQ106980 | OCC_237 | TGTRANSCO | JANAGAON - 400KV B/R 1 | TGTRANSCO | C | Yearly MAINTENANCE & Testing of REACTOR,Relays & BAY equipment. | 2026-05-26 | 07:00 | 2026-05-26 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Bus Reactor | 22-May-2026 | 19:19 | 23-May-2026 | 16:29
RQ106996 | OCC_237 | TGTRANSCO | 400KV-RAMADUGU-TIPPAPUR-2 | TGTRANSCO | C | Periodical testing of bay equipment | 2026-05-26 | 10:00 | 2026-05-26 | 18:00 |  | Yes | Approved | 400KV-TIPPAPUR-RAMADUGU-1 53% 400KV-RAMADUGU-GAJWEL D/C 10% each 400KV-TELANGANA_STPP-NARSAPUR D/C 6% each All RAMADUGU ICTs shall be in service. | Line Circuits | 22-May-2026 | 19:19 | 23-May-2026 | 17:10
RQ109263 | PNOCC | aptransco | 220KV-DOMALAPENTA-SRISAILAM_RIGHT_BANK-1 | TGTRANSCO | D | Heavy damages occurred on conductors and require to be take up the works immediately. The stipulated dates given are in the merge of the monsoons and it is very difficult to arrange man power and also to complete the work in the stipulated duration | 2026-05-31 | 05:00 | 2026-05-31 | 12:00 | Date change request due to man power issue | Yes | Rejected | Planned Activities to be taken as per approved timelines of Main OCC. | Line Circuits | 22-May-2026 | 16:55 | 28-May-2026 | 10:33
RQ106409 | OCC_237 | TANTRANSCO | TIE BAY (409) OF 400KV/110KV SALEM_TN-ICT-3 AND 400KV/110KV SALEM_TN-ICT-4 @SALEM_TN - 400KV | TANTRANSCO | D | Preventive maintenance for bay equipments ( Breaker, CT) and P&C testing works. | 2026-05-26 | 09:00 | 2026-05-26 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 22-May-2026 | 15:59 | 23-May-2026 | 16:40
RQ106406 | OCC_237 | TANTRANSCO | PALAVADI - 400KV B/R 2 | TANTRANSCO | D | Preventive maintenance for bay equipments, Reactor maintenance and P&C testing work. | 2026-05-26 | 09:00 | 2026-05-26 | 17:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Bus Reactor | 22-May-2026 | 15:53 | 23-May-2026 | 16:46
RQ106898 | OCC_237 | PGCIL SR-1 | 765KV-KURNOOL_PG-NPS-2 | POWERGRID | D | Jumper guy work anchoring work | 2026-05-26 | 07:00 | 2026-05-26 | 18:00 | AMP works. | No | Rejected | Deferred by requester. | Line Circuits | 22-May-2026 | 15:51 | 23-May-2026 | 16:29
RQ107523 | OCC_2371 | PGCIL SR-2 | 400KV-KOPPAL-KUDGI_PG-1 | KNTL | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 9/0 - 10/0 | 2026-05-26 | 08:00 | 2026-05-26 | 19:00 | 400KV-KOPPAL-KUDGI_PG- D/C Outage is required to carry out powerline crossing works. Concurrence from connected IPPs will be submitted on D-4 basis. | Yes | Rejected | Due to Multiple shutdowns at the same station. 400kV-KOPPAL-GADAG D/C is out due to tower collapse. | Line Circuits | 22-May-2026 | 14:07 | 23-May-2026 | 18:37
RQ107525 | OCC_2371 | PGCIL SR-2 | 400KV-KOPPAL-KUDGI_PG-2 | KNTL | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 9/0 - 10/0 | 2026-05-26 | 08:00 | 2026-05-26 | 19:00 | 400KV-KOPPAL-KUDGI_PG- D/C Outage is required to carry out powerline crossing works. Concurrence from connected IPPs will be submitted on D-4 basis. | Yes | Rejected | Due to Multiple shutdowns at the same station. 400kV-KOPPAL-GADAG D/C is out due to tower collapse. | Line Circuits | 22-May-2026 | 14:07 | 23-May-2026 | 18:37
RQ106533 | OCC_237 | kseb | 400KV/220KV MADAKKATHARA-ICT-2 | KSEB | D | For conducting RLA study of ICT No.2 | 2026-05-26 | 08:00 | 2026-05-26 | 17:00 | For conducting RLA study of ICT No.2 | Yes | Approved | Load Management need to be done by KSEB. S3- 300 MW import ATC reduction. N-1 limit for MADAKKATHARA ICTs is 235 MW each. 400KV/220KV MADAKATHARA-ICT-1,3 25% each All PALAKKAD and KOZHIKODE ICTs shall be in service along with 220KV-ELANKUR-AREACODE-1 10% 220KV-ELAPULLY-MADAKATHARA-1 9% 220KV-PALAKKAD(KL)-MADAKATHARA-1 9% 220KV-MADAKATHARA-LOWER PERIYAR-1 8% 400KV-KOZHIKODE-MADAKKATHARA D/C 7% each 220KV-KOZHIKODE-AREACODE D/C 4% each. | Transformer | 22-May-2026 | 13:03 | 23-May-2026 | 16:49
RQ106582 | OCC_237 | aptransco | 132KV-PAMMY-CHILLAKALLU-1 | TGTRANSCO | D | Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | 2026-05-26 | 08:00 | 2026-05-26 | 18:00 | Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | Yes | Approved | Load management to be done by AP & TG for multiple outages | Line Circuits | 22-May-2026 | 11:44 | 23-May-2026 | 16:29
RQ106592 | OCC_237 | aptransco | 132KV-CHILLAKALLU-PEDAGOPATHI-1 | APTRANSCO,TGTRANSCO | D | D/C line Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | 2026-05-26 | 08:00 | 2026-05-26 | 18:00 | D/C line Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | Yes | Approved | Load management to be done by AP & TG for multiple outages | Line Circuits | 22-May-2026 | 11:44 | 23-May-2026 | 16:29
RQ106550 | OCC_237 | aptransco | 400KV-KRISHNAPATNAM-RACHAGUNNERI-1 | APTRANSCO | D | Tightening of spacer dampers and providing of missing keepers to dampers between locno:91 to 94 , arranging repair sleeves to conductor damages between loc. No:91- 92 bottom phase in 400KV KrishnapatnamRachagunneri-1 feeder. | 2026-05-26 | 07:00 | 2026-05-26 | 17:00 | During the LC period there will be no interruption to loads as 400KV Krishnapatnam TPP - Manubolu feeder, 400KV SEIL – Manubolu feeder, 400KV Krishnapatnam-SEIL feeder and 400KV Krishnapatnam TPP – Rachagunneri - 2 feeders will be in Service. | Yes | Approved | 400KV-RACHAGUNNERI-KRISHNAPATNAM-2 44% 400KV-KRISHNAPATNAM-NELLORE_AP-1 30% 400KV-SEILU2_AP-NELLORE_AP-1 26% 400KV-TVLM-CHITTOOR D/C 11% each shall be in service. | Line Circuits | 22-May-2026 | 11:44 | 23-May-2026 | 17:47
RQ106682 | OCC_237 | aptransco | 400KV-VEMAGIRI_AP-KV_KOTA-2 | APTRANSCO | D | General maintenance works as per schedule. | 2026-05-26 | 09:00 | 2026-05-26 | 17:00 | Annual maintenance works | Yes | Approved | 400KV-KV_KOTA-VEMAGIRI_AP-1 32% 400KV-SURYAPET-KV_KOTA D/C 13% each 400KV-GUDDIGUDEM-HINDUJA D/C 10% each 400KV-SURYAPET-VTPS_IV D/C 7% each All VEMAGIRI_AP ICTs shall be in service | Line Circuits | 22-May-2026 | 11:44 | 23-May-2026 | 17:10
RQ106707 | OCC_237 | aptransco | 400KV-SATTENPALLY-PODILI-2 | APTRANSCO | D | For periodical Line Maintenance works | 2026-05-26 | 09:00 | 2026-05-26 | 17:00 | Annual maintenance works | Yes | Rejected | Due to Multiple shutdowns at the same station. | Line Circuits | 22-May-2026 | 11:44 | 23-May-2026 | 17:47
RQ106451 | OCC_237 | TANTRANSCO | 400KV-KARAIKUDI-KAMUDHI-2 | TANTRANSCO | D | Monthly Maintenance Work | 2026-05-26 | 16:00 | 2026-05-26 | 21:00 |  | Yes | Approved | 400KV-KAMUDHI-KARAIKUDI-1 52% 400KV-THENNAMPATTY-KAYATHAR-1 20% 400KV-OTTAPIDARAM-THENNAMPATTY D/C 18% each 400KV-KANARPATTI-TIRUNELVELI-1 13% 400KV-VIRUDHUNAGAR-THENNAMPATTY-1 12% 400KV-VIRUDHUNAGAR-KAYATHAR-1 12% 400KV-KAYATHAR-KARAIKUDI-1 10% shall be in service. | Line Circuits | 22-May-2026 | 10:50 | 23-May-2026 | 17:10
RQ106507 | OCC_237 | TANTRANSCO | 400KV/110KV THENNAMPATTY-ICT-3 | TANTRANSCO | D | Monthly Maintenance Work | 2026-05-26 | 16:00 | 2026-05-26 | 20:00 |  | Yes | Approved | Load Management need to be done by TN. N-1 limit for 400KV/110KV THENNAMPATTY-ICTs is 95 MW each. | Transformer | 22-May-2026 | 10:50 | 23-May-2026 | 17:47
RQ106516 | OCC_237 | TANTRANSCO | VELLALAVIDUTHI - 400KV - BUS 2 | TANTRANSCO | D | Monthly Maintenance work | 2026-05-26 | 09:00 | 2026-05-26 | 17:00 |  | Yes | Approved | Remaining all elements shall be in service. | Bus | 22-May-2026 | 10:50 | 23-May-2026 | 16:46
RQ106825 | OCC_237 | TANTRANSCO | KAYATHAR - 400KV - BUS 1 | TANTRANSCO | D | For providing jumper from 400KVBUS1 to 400KV Isolator [422-89A]of New ICT 5 Bay | 2026-05-26 | 10:00 | 2026-05-26 | 14:00 | There will be no interruption to ICT1,400KV Karaikudi #2, 400KV Kanarpatti #1 & 400KV Virudhunagar# as the load will be fed by concerned Tie Breakers[405-52] for ICT1, [408-52] for 400 KV Karaikudi #1, [402-52] for 400KV Kanarpatti #1, [417-52] for 400KV Virudhunagar#. The 400KV Isolator [422-89A] will be kept opened after providing jumper from 400KV BUS1 | Yes | Rejected | In view of high RE injection. May be availed after peak wind season of SR. | Bus | 22-May-2026 | 10:50 | 23-May-2026 | 16:40
RQ106526 | OCC_237 | TANTRANSCO | RASIPALYAM - 400KV B/R 1 | TANTRANSCO | D | Preventive maintenance for bay equipments, Reactor and P&C testing works | 2026-05-25 | 09:00 | 2026-05-25 | 17:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Bus Reactor | 21-May-2026 | 19:49 | 22-May-2026 | 12:42
RQ106901 | OCC_237 | PGCIL SR-1 | 765KV-KURNOOL_PG-NPS-1 | POWERGRID | D | Jumper guy work anchoring work | 2026-05-25 | 07:00 | 2026-05-25 | 19:00 | AMP works. | No | Rejected | Deferred by requester. | Line Circuits | 21-May-2026 | 18:05 | 22-May-2026 | 10:40
RQ107476 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-KURNOOL_PG-MAHESHWARAM_PG-1 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP146-AP147 | 2026-05-25 | 06:00 | 2026-05-25 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 21-May-2026 | 18:05 | 22-May-2026 | 10:40
RQ107487 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-KURNOOL_PG-MAHESHWARAM_PG-2 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP146-AP147 | 2026-05-25 | 06:00 | 2026-05-25 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 21-May-2026 | 18:05 | 22-May-2026 | 10:40
RQ107498 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-NIZAMABAD-MAHESHWARAM_PG-1 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP147-AP148 | 2026-05-25 | 06:00 | 2026-05-25 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 21-May-2026 | 18:05 | 22-May-2026 | 10:40
RQ107509 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-NIZAMABAD-MAHESHWARAM_PG-2 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP147-AP148 | 2026-05-25 | 06:00 | 2026-05-25 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 21-May-2026 | 18:05 | 22-May-2026 | 10:40
RQ106476 | OCC_237 | TANTRANSCO | 400KV/110KV KANARPATTI-ICT-3 | TANTRANSCO | D | Monthly Maintenance work | 2026-05-25 | 14:00 | 2026-05-25 | 20:00 |  | Yes | Approved | N-1 limit for 400KV/110KV KANARPATTI-ICTs is 140 MW each. ICT loadings to be below N-1 limit. S/D to be availed only after 15:30 HRS. | Transformer | 21-May-2026 | 15:26 | 22-May-2026 | 13:17
RQ106515 | OCC_237 | TANTRANSCO | VELLALAVIDUTHI - 400KV - BUS 1 | TANTRANSCO | D | Monthly Maintenance work | 2026-05-25 | 09:00 | 2026-05-25 | 17:00 |  | Yes | Approved | Remaining all elements shall be in service. | Bus | 21-May-2026 | 15:26 | 22-May-2026 | 12:42
RQ106502 | OCC_237 | NPCIL | 230KV-KUDANKULAM-TTPS | TANTRANSCO | C | Line insulator cleaning work. Wave trap top side connectors CRM measurements. SF6 gas properties checking in the compartments. SF6 Density meters calibration to be done. | 2026-05-25 | 07:00 | 2026-05-25 | 18:00 |  | Yes | Approved | 230KV-TTPS-MEELAVITTAN-1 27% 230KV-KUDANKULAM-S R PUDUR-1 26% 230KV-S R PUDUR-SANGANERI-1 26% 400KV-KUDANKULAM-TIRUNELVELI all lines shall be in service. Load management need to be done by TN in case of any contingency. | Line Circuits | 21-May-2026 | 11:15 | 22-May-2026 | 15:15
RQ106813 | OCC_237 | kptcl | GUTTUR - 400KV B/R 1 | KPTCL | D | 1st Quarter Maintenance. C isolator allignment issue to be attended. | 2026-05-25 | 10:00 | 2026-05-25 | 17:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Bus Reactor | 21-May-2026 | 10:45 | 22-May-2026 | 12:42
RQ106535 | OCC_237 | kseb | 400KV/220KV MADAKKATHARA-ICT-1 | KSEB | D | For conducting RLA study ICT No.1 | 2026-05-25 | 08:00 | 2026-05-25 | 17:00 | For conducting RLA study ICT No.1 | Yes | Approved | Load Management need to be done by KSEB. S3- 300 MW import ATC reduction. N-1 limit for MADAKKATHARA ICTs is 235 MW each. 400KV/220KV MADAKATHARA-ICT-2,3 25% each All PALAKKAD and KOZHIKODE ICTs shall be in service along with 220KV-ELANKUR-AREACODE-1 10% 220KV-ELAPULLY-MADAKATHARA-1 9% 220KV-PALAKKAD(KL)-MADAKATHARA-1 9% 220KV-MADAKATHARA-LOWER PERIYAR-1 8% 400KV-KOZHIKODE-MADAKKATHARA D/C 7% each 220KV-KOZHIKODE-AREACODE D/C 4% each. | Transformer | 21-May-2026 | 10:28 | 22-May-2026 | 12:44
RQ109234 | PNOCC | aptransco | 132KV-NAGARJUNASAGAR-NS_RIGHT_CANEL_PH-1 | APTRANSCO,TGTRANSCO | D | Dismantling od existiong CT's of NSR feeder& erection of new CT's | 2026-05-28 | 06:00 | 2026-05-28 | 18:00 |  | Yes | Rejected | Planned Activities to be taken into Main OCC. TG concurrence is required as well. | Line Circuits | 21-May-2026 | 10:17 | 25-May-2026 | 10:44
RQ109232 | PNOCC | aptransco | 132KV-NAGARJUNASAGAR-NS_RIGHT_CANEL_PH-1 | APTRANSCO,TGTRANSCO | D | Dismantling od existiong CT's of NSR feeder& erection of new CT's | 2026-05-26 | 06:00 | 2026-05-26 | 18:00 |  | Yes | Rejected | Planned Activities to be taken into Main OCC. TG concurrence is required as well. | Line Circuits | 21-May-2026 | 10:17 | 23-May-2026 | 16:46
RQ109233 | PNOCC | aptransco | 132KV-NAGARJUNASAGAR-NS_RIGHT_CANEL_PH-1 | APTRANSCO,TGTRANSCO | D | Dismantling od existiong CT's of NSR feeder& erection of new CT's | 2026-05-27 | 06:00 | 2026-05-27 | 18:00 |  | Yes | Rejected | Planned Activities to be taken into Main OCC. TG concurrence is required as well. | Line Circuits | 21-May-2026 | 10:17 | 24-May-2026 | 10:44
RQ106581 | OCC_237 | aptransco | 132KV-PAMMY-CHILLAKALLU-1 | TGTRANSCO | D | Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | 2026-05-25 | 08:00 | 2026-05-25 | 18:00 | Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | Yes | Approved | Load management to be done by AP & TG for multiple outages | Line Circuits | 21-May-2026 | 10:11 | 22-May-2026 | 12:42
RQ106591 | OCC_237 | aptransco | 132KV-CHILLAKALLU-PEDAGOPATHI-1 | APTRANSCO,TGTRANSCO | D | D/C line Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | 2026-05-25 | 08:00 | 2026-05-25 | 18:00 | D/C line Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | Yes | Approved | Load management to be done by AP & TG for multiple outages | Line Circuits | 21-May-2026 | 10:11 | 22-May-2026 | 12:42
RQ106811 | OCC_237 | aptransco | KALPAKKA - 400KV B/R 2 | APTRANSCO | C | For replacement of old 1no Nos CB( Make: M/s ABB) with newly supplied 1 nos CB (Make : M/s CG power) at 400kv SS Kalapaka under RMI | 2026-05-25 | 09:00 | 2026-05-30 | 17:00 | For replacement of old 1no Nos CB( Make: M/s ABB) with newly supplied 1 nos CB (Make : M/s CG power) at 400kv SS Kalapaka under RMI | Yes | Approved | Concurred, subject to real time grid conditions. | Bus Reactor | 21-May-2026 | 10:11 | 22-May-2026 | 15:07
RQ106417 | OCC_237 | TANTRANSCO | 230KV-KALVENDAPATTU-THARAMANI | TANTRANSCO | D | QUARTERLY MAINTENANCE WORKS | 2026-05-24 | 09:00 | 2026-05-24 | 17:00 |  | No | Rejected | Deferred by requester. | Line Circuits | 21-May-2026 | 08:49 | 21-May-2026 | 10:04
RQ109208 | PNOCC | TANTRANSCO | 230KV-ARASUR_PG-ARASUR-1 | TANTRANSCO | D | for replacement of the snapped 24 OPGW between Loc. 6-7 in 230KV Arasur- Arasur PGCIL Link I & II DC feeder with 48 OPGW between loc 5 to 8. (the snapped OPGW earth wire was removed on 02.05.2026 due to heavy wind) | 2026-05-24 | 06:00 | 2026-05-24 | 18:00 | For load management, LC programmed based on Sunday load relief. Around 60 MW(110KV Karamadai 1 & 2#) load will be transferred to Karamadai 400KV SS, around 30 MW(110KV Karuvalur 1 & 2) load will be transferred to Karuvalur 230KV SS, around 20MW(Poomalur 110V SS) load will be transferred to Kalivelampatty 230 KV SS and wind generation connected 110KV SS either 110KV Kethanur SS or 110KV Sulthanpet SS may be taken to Arasur 230KV SS to avail wind generation import. Further load will be managed by increasing the Kundah PH2 and PUSHEP hydro generation please. | Yes | Approved | Load Management details submitted by TN: 1. Around 70MW load relief by making 110KV Arasur- Karamadai I# and 110KV Arasur-Karamadai II # will be kept radial from 400KV Karamadai SS end. 2. Around 20MW load relief by making 110KV Arasur- Karuvalur I# and 110KV Arasur-Karuvalur II # will be kept radial from 230KV Karuvalur SS end. 3. Around 20MW load relief, 110KV Poomalur SS load will be transferred from Arasur 230KV SS to 230KV Kalivellmapatty SS. 4. Based on WInd Generation on 23.05.2026, either 110KV Kethanur SS or 110KV Sulthanpet SS may be taken into Arasur 230KV SS for wind generation import. 5. Balance load such as Local 110kV Arasur SS (15MW), 110KV Kalivellampatty # (Sulur load: 25MW), 110KV Somanur # (35MW), 110KV Kaniyur # (28MW), total load around 103MW will be managed by increasing the Kundah PH2 and PUSHEP hydro generation and 230KV other tie feeders. The same need to be adhered by TN. Post load shifting, following sensitivities are observed on each line of 230kV-ARASUR_PG - ARASUR_TN D/C: Kundah PH2 generation (-10%) PUSHEP generation (-16%) Sensitivities on other lines post D/C shutdown: 230kV-KARAMADAI-SHENBAGPUDUR 24% 230kV-ARASUR-KARUVALUR 21% 230kV-ARASUR-GOBI 19% 230kV-ARASUR-PUSHEP 18% 400kV-KARAMADAI-ARASUR D/C 15% each 230kV-ARASUR-KALIVELAMPATTY-INGUR All KARAMADAI, SALEM and MTPS ICTs shall be in service. Along with this, voltage management need to be taken care by TN. | Line Circuits | 20-May-2026 | 18:26 | 22-May-2026 | 12:26
RQ109209 | PNOCC | TANTRANSCO | 230KV-ARASUR_PG-ARASUR-2 | TANTRANSCO | D | for replacement of the snapped 24 OPGW between Loc. 6-7 in 230KV Arasur- Arasur PGCIL Link I & II DC feeder with 48 OPGW between loc 5 to 8. (the snapped OPGW earth wire was removed on 02.05.2026 due to heavy wind) | 2026-05-24 | 06:00 | 2026-05-24 | 18:00 | For load management, LC programmed based on Sunday load relief. Around 60 MW(110KV Karamadai 1 & 2#) load will be transferred to Karamadai 400KV SS, around 30 MW(110KV Karuvalur 1 & 2) load will be transferred to Karuvalur 230KV SS, around 20MW(Poomalur 110V SS) load will be transferred to Kalivelampatty 230 KV SS and wind generation connected 110KV SS either 110KV Kethanur SS or 110KV Sulthanpet SS may be taken to Arasur 230KV SS to avail wind generation import. Further load will be managed by increasing the Kundah PH2 and PUSHEP hydro generation please. | Yes | Approved | Load Management details submitted by TN: 1. Around 70MW load relief by making 110KV Arasur- Karamadai I# and 110KV Arasur-Karamadai II # will be kept radial from 400KV Karamadai SS end. 2. Around 20MW load relief by making 110KV Arasur- Karuvalur I# and 110KV Arasur-Karuvalur II # will be kept radial from 230KV Karuvalur SS end. 3. Around 20MW load relief, 110KV Poomalur SS load will be transferred from Arasur 230KV SS to 230KV Kalivellmapatty SS. 4. Based on WInd Generation on 23.05.2026, either 110KV Kethanur SS or 110KV Sulthanpet SS may be taken into Arasur 230KV SS for wind generation import. 5. Balance load such as Local 110kV Arasur SS (15MW), 110KV Kalivellampatty # (Sulur load: 25MW), 110KV Somanur # (35MW), 110KV Kaniyur # (28MW), total load around 103MW will be managed by increasing the Kundah PH2 and PUSHEP hydro generation and 230KV other tie feeders. The same need to be adhered by TN. Post load shifting, following sensitivities are observed on each line of 230kV-ARASUR_PG - ARASUR_TN D/C: Kundah PH2 generation (-10%) PUSHEP generation (-16%) Sensitivities on other lines post D/C shutdown: 230kV-KARAMADAI-SHENBAGPUDUR 24% 230kV-ARASUR-KARUVALUR 21% 230kV-ARASUR-GOBI 19% 230kV-ARASUR-PUSHEP 18% 400kV-KARAMADAI-ARASUR D/C 15% each 230kV-ARASUR-KALIVELAMPATTY-INGUR All KARAMADAI, SALEM and MTPS ICTs shall be in service. Along with this, voltage management need to be taken care by TN. | Line Circuits | 20-May-2026 | 18:26 | 22-May-2026 | 12:26
RQ106922 | OCC_237 | PGCIL SR-1 | NAGARJUNASAGAR_PG - 400KV - BUS 1 | PGCIL SR-1 | C | Bus Bar Relay testing works | 2026-05-24 | 09:00 | 2026-05-25 | 18:00 | Circular compliance/Scheme Modification works. | Yes | Rejected | Deferred by PGCIL SR-1 as per mail communication received dated 21.05.2026. | Bus | 20-May-2026 | 15:33 | 21-May-2026 | 12:48
RQ107475 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-KURNOOL_PG-MAHESHWARAM_PG-1 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP146-AP147 | 2026-05-24 | 06:00 | 2026-05-24 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 20-May-2026 | 15:33 | 21-May-2026 | 10:04
RQ107486 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-KURNOOL_PG-MAHESHWARAM_PG-2 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP146-AP147 | 2026-05-24 | 06:00 | 2026-05-24 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 20-May-2026 | 15:33 | 21-May-2026 | 10:04
RQ107497 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-NIZAMABAD-MAHESHWARAM_PG-1 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP147-AP148 | 2026-05-24 | 06:00 | 2026-05-24 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 20-May-2026 | 15:33 | 21-May-2026 | 10:04
RQ107508 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-NIZAMABAD-MAHESHWARAM_PG-2 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP147-AP148 | 2026-05-24 | 06:00 | 2026-05-24 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 20-May-2026 | 15:33 | 21-May-2026 | 10:04
RQ109190 | PNOCC | aptransco | 400KV-GUDIWADA-SATTENPALLY-2 | APTRANSCO | C | To rectify the auto reclosure functions of main & TIE breakers | 2026-05-25 | 00:00 | 2026-05-25 | 18:00 | For checking of mal operation of AR functions | Yes | Rejected | Planned Activities to be taken into Main OCC. | Line Circuits | 20-May-2026 | 12:38 | 22-May-2026 | 13:14
RQ109193 | PNOCC | aptransco | 400KV-NARNOOR-JAMMALAMADUGU-2 | APTRANSCO | C | For checking of AR operations of the breakers | 2026-05-25 | 10:00 | 2026-05-25 | 14:00 |  | Yes | Rejected | Planned Activities to be taken into Main OCC. | Line Circuits | 20-May-2026 | 12:44 | 22-May-2026 | 13:14
RQ109197 | PNOCC | kseb | 132KV-KUZHITHURAI-PARASSALA-1 | KSEB,TANTRANSCO | D | Sir, As part of the 110kV Bus renewal work at 110kV Kuzhithuri Substation of KSEBL, shutdown of the 110kV Kuzhithuri–Parassala feeder is required on 24.05.2026 (Sunday). Since the work involves total substation bus permit work, the activity has also been coordinated with the Distribution Wing. Hence, you are requested to kindly concur the shutdown. | 2026-05-24 | 07:00 | 2026-05-24 | 17:00 | 110kV Bus renewal works at Kuzhithuri SS | Yes | Rejected | TNEB concurrence need to be submitted. Planned Activities to be taken into Main OCC. | Line Circuits | 20-May-2026 | 13:30 | 21-May-2026 | 12:55
RQ109179 | PNOCC | aptransco | 220KV-SRISAILAM_RIGHT_BANK-DINDI-1 | APTRANSCO,TGTRANSCO | D | 238th OCC approved shutdowns. Date change requested due to these feeder’s heavy damages occurred on conductors and require to be take up the works immediately. The stipulated dates given are in the merge of the monsoons and it is very difficult to arrange man power and also to complete the work in the stipulated duration. | 2026-05-28 | 05:00 | 2026-05-28 | 12:00 | Due to manpower issue Date change requested | Yes | Rejected | Planned Activities to be availed as per approved timelines of OCC. | Line Circuits | 20-May-2026 | 10:26 | 25-May-2026 | 10:44
RQ109176 | PNOCC | aptransco | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1 | APTRANSCO,TGTRANSCO | D | 238th OCC approved shutdowns. Date change requested due to these feeder’s heavy damages occurred on conductors and require to be take up the works immediately. The stipulated dates given are in the merge of the monsoons and it is very difficult to arrange man power and also to complete the work in the stipulated duration. | 2026-05-25 | 05:00 | 2026-05-25 | 12:00 | Due to manpower issue Date change requested | Yes | Rejected | Planned Activities to be availed as per the stipulated approved timelines. | Line Circuits | 20-May-2026 | 10:26 | 22-May-2026 | 13:56
RQ109177 | PNOCC | aptransco | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1 | APTRANSCO,TGTRANSCO | D | 238th OCC approved shutdowns. Date change requested due to these feeder’s heavy damages occurred on conductors and require to be take up the works immediately. The stipulated dates given are in the merge of the monsoons and it is very difficult to arrange man power and also to complete the work in the stipulated duration. | 2026-05-26 | 05:00 | 2026-05-26 | 12:00 | Due to manpower issue Date change requested | Yes | Rejected | Planned Activities to be taken as per approved OCC timelines. | Line Circuits | 20-May-2026 | 10:26 | 23-May-2026 | 16:46
RQ109178 | PNOCC | aptransco | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1 | APTRANSCO,TGTRANSCO | D | 238th OCC approved shutdowns. Date change requested due to these feeder’s heavy damages occurred on conductors and require to be take up the works immediately. The stipulated dates given are in the merge of the monsoons and it is very difficult to arrange man power and also to complete the work in the stipulated duration. | 2026-05-27 | 05:00 | 2026-05-27 | 12:00 | Due to manpower issue Date change requested | Yes | Rejected | Planned Activities to be availed as per approved timelines in Main OCC. | Line Circuits | 20-May-2026 | 10:26 | 24-May-2026 | 10:26
RQ109180 | PNOCC | aptransco | 220KV-SRISAILAM_RIGHT_BANK-DINDI-1 | APTRANSCO,TGTRANSCO | D | 238th OCC approved shutdowns. Date change requested due to these feeder’s heavy damages occurred on conductors and require to be take up the works immediately. The stipulated dates given are in the merge of the monsoons and it is very difficult to arrange man power and also to complete the work in the stipulated duration. | 2026-05-29 | 05:00 | 2026-05-29 | 12:00 | Due to manpower issue Date change requested | Yes | Rejected | Planned Activities to be taken as per approved timelines in Main OCC. | Line Circuits | 20-May-2026 | 10:26 | 26-May-2026 | 16:50
RQ109181 | PNOCC | aptransco | 220KV-SRISAILAM_RIGHT_BANK-DINDI-1 | APTRANSCO,TGTRANSCO | D | 238th OCC approved shutdowns. Date change requested due to these feeder’s heavy damages occurred on conductors and require to be take up the works immediately. The stipulated dates given are in the merge of the monsoons and it is very difficult to arrange man power and also to complete the work in the stipulated duration. | 2026-05-30 | 05:00 | 2026-05-30 | 12:00 | Due to manpower issue Date change requested | Yes | Rejected | Planned Activities to be taken as per approved timelines of OCC. | Line Circuits | 20-May-2026 | 10:26 | 27-May-2026 | 11:21
RQ106580 | OCC_237 | aptransco | 132KV-PAMMY-CHILLAKALLU-1 | TGTRANSCO | D | Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | 2026-05-24 | 08:00 | 2026-05-24 | 18:00 | Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | Yes | Approved | Load management to be done by AP & TG for multiple outages | Line Circuits | 20-May-2026 | 10:14 | 21-May-2026 | 12:48
RQ106590 | OCC_237 | aptransco | 132KV-CHILLAKALLU-PEDAGOPATHI-1 | APTRANSCO,TGTRANSCO | D | D/C line Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | 2026-05-24 | 08:00 | 2026-05-24 | 18:00 | D/C line Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | Yes | Approved | Load management to be done by AP & TG for multiple outages | Line Circuits | 20-May-2026 | 10:14 | 21-May-2026 | 12:48
RQ106760 | OCC_237 | KNTL | KOPPAL - 220KV - BUS 4 | INDIGRID | D | Yearly Bay equipment testing and preventive maintenance. | 2026-05-23 | 09:00 | 2026-05-23 | 17:00 |  | Yes | Approved | Remaining all elements shall be in service. | Bus | 20-May-2026 | 08:49 | 20-May-2026 | 23:18
RQ106429 | OCC_237 | TANTRANSCO | MAIN BAY (405) OF 400KV/230KV SRIPERUMBADUR_TN-ICT-3 AND SRIPERUMBADUR_TN - 400KV - BUS 2 @SRIPERUMBADUR_TN - 400KV | TANTRANSCO | D | QUARTERLY MAINTENANCE WORKS | 2026-05-23 | 09:00 | 2026-05-23 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 19-May-2026 | 15:45 | 20-May-2026 | 11:18
RQ107079 | OCC_237 | PGCIL SR-2 | 400KV/220KV KOCHI-ICT-3 | PGCIL SR-2 | D | AMP works of ICT-3 | 2026-05-23 | 09:00 | 2026-05-23 | 13:00 |  | Yes | Rejected | S3 - 200MW reduction. Subject to revival of 400kV/220kV KOZHIKODE ICT-3. Load Management need to be done by KSEB. N-1 limit for KOCHI ICTs is 208 MW for 315 MVA ICT each and 330 MW for 500 MVA ICT. 400KV/220KV KOCHI-ICT-1,2 28% each All KOTTAYAM and MADAKKATHARA ICTs shall be in service along with 400KV-KOCHI-THRISSUR HVDC D/C and 400KV-THRISSUR HVDC-TRICHUR D/C. | Transformer | 19-May-2026 | 15:45 | 20-May-2026 | 23:25
RQ107080 | OCC_237 | PGCIL SR-2 | 400KV/230KV HOSUR_PG-ICT-4 | PGCIL SR-2 | D | AMP works of ICT-4 | 2026-05-23 | 09:00 | 2026-05-23 | 13:00 |  | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. N-1 limit for Remaining HOSUR ICTs is 219 MW each. Load Management need to be done by TN. 400KV/230KV HOSUR_PG-ICT-1,2,3 23% each All PALAVADI and SALEM ICTs shall be in service. | Transformer | 19-May-2026 | 15:45 | 20-May-2026 | 23:25
RQ107511 | OCC_2371 | PGCIL SR-1 | KURNOOL_PG - 400KV - BUS 1 | PGCIL SR-1 | C | Construction works: AMGEPL line integration (416-418 bays at Kurnool SS): Busbar stability , protection testing and integration | 2026-05-23 | 07:30 | 2026-05-24 | 20:00 | Construction works | No | Rejected | Deferred by requester. | Bus | 19-May-2026 | 15:37 | 20-May-2026 | 10:27
RQ107474 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-KURNOOL_PG-MAHESHWARAM_PG-1 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP146-AP147 | 2026-05-23 | 06:00 | 2026-05-23 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 19-May-2026 | 15:16 | 20-May-2026 | 10:27
RQ107485 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-KURNOOL_PG-MAHESHWARAM_PG-2 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP146-AP147 | 2026-05-23 | 06:00 | 2026-05-23 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 19-May-2026 | 15:16 | 20-May-2026 | 10:27
RQ107496 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-NIZAMABAD-MAHESHWARAM_PG-1 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP147-AP148 | 2026-05-23 | 06:00 | 2026-05-23 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 19-May-2026 | 15:16 | 20-May-2026 | 10:27
RQ107507 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-NIZAMABAD-MAHESHWARAM_PG-2 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP147-AP148 | 2026-05-23 | 06:00 | 2026-05-23 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 19-May-2026 | 15:16 | 20-May-2026 | 10:27
RQ107007 | OCC_237 | TGTRANSCO | 400KV-YEDULA-MEHBOOBNAGAR-1 | TGTRANSCO | C | For carrying out periodical equipment Maintenance and Testing works by O&m and MRT wings. | 2026-05-23 | 09:00 | 2026-05-23 | 17:00 |  | Yes | Approved | 400KV-YEDULA-MEHBOOBNAGAR-2 68% 400KV-MAHESHWARAM_TG-MAHESHWARAM_PG D/C 8% each 400KV-MAHESHWARAM_TG-DINDI D/C each shall be in service. | Line Circuits | 19-May-2026 | 13:50 | 20-May-2026 | 23:18
RQ109066 | PNOCC | kseb | 400KV/220KV MADAKKATHARA-ICT-1 | KSEB | D | Sir/Madam, The RLA study is proposed for seven 105 MVA transformer units (ICT#1 and ICT#2, including spare) and 7nos 66.67MVA transformer units (200MVA#1 and 200MVA#2, including spare) at 400kV Substation Madakkathara during May 2026. The study is being carried out by Central Power Research Institute, Bangalore. They tentatively requested two days to complete testing on one transformer bank. OCC approval for the shutdown of 440/220kV ICT#1 was requested for 23.05.2026 & 25.05.2026, and approved for 25.05.2026 & 30.05.2026 due to Kochi ICT 3 shutdown on 23.05.26. OCC approval for the shutdown of ICT#2 was requested for 26.05.2026 & 27.05.2026, and approved for the same dates. It may please be noted that since CPRI officials are coming for testing hence it will be convenient if consecutive days are approved for one bank.Hence it is requested approve shutdown of Madakkathara 400/220kV ICT#1 on 24.05.26 instead of 30.05.26 as ICT#1 shutdown is already sanctioned on 25.05.26. | 2026-05-24 | 08:00 | 2026-05-24 | 17:00 | Sir, the PW is sanctioned on 30.05.2026, but this work is carried out by CPRI hence it is requested to change the date of sanction to 24.05.2026. | Yes | Approved | Load Management need to be done by KSEB. S3- 300 MW import ATC reduction. N-1 limit for MADAKKATHARA ICTs is 235 MW each. 400KV/220KV MADAKATHARA-ICT-2,3 25% each All PALAKKAD and KOZHIKODE ICTs shall be in service along with 220KV-ELANKUR-AREACODE-1 10% 220KV-ELAPULLY-MADAKATHARA-1 9% 220KV-PALAKKAD(KL)-MADAKATHARA-1 9% 220KV-MADAKATHARA-LOWER PERIYAR-1 8% 400KV-KOZHIKODE-MADAKKATHARA D/C 7% each 220KV-KOZHIKODE-AREACODE D/C 4% each. | Transformer | 18-May-2026 | 17:41 | 21-May-2026 | 13:03
RQ106579 | OCC_237 | aptransco | 132KV-PAMMY-CHILLAKALLU-1 | TGTRANSCO | D | Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | 2026-05-23 | 08:00 | 2026-05-23 | 18:00 | Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | Yes | Approved | Load management to be done by AP & TG for multiple outages | Line Circuits | 19-May-2026 | 10:33 | 20-May-2026 | 10:27
RQ106589 | OCC_237 | aptransco | 132KV-CHILLAKALLU-PEDAGOPATHI-1 | APTRANSCO,TGTRANSCO | D | D/C line Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | 2026-05-23 | 08:00 | 2026-05-23 | 18:00 | D/C line Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | Yes | Approved | Load management to be done by AP & TG for multiple outages | Line Circuits | 19-May-2026 | 10:33 | 20-May-2026 | 10:27
RQ106464 | OCC_237 | WKTL | 765KV-WARANGAL(NEW)-WARORA-1 | WKTL | C | For 24Hrs. Trail Run of NGR Bypass at Warora end | 2026-05-23 | 08:00 | 2026-05-24 | 08:00 | For 24Hrs. Trail Run of NGR Bypass at Warora end | Yes | Approved | Subject to NLDC approval and real time grid conditions. TTC reduction of 700 MW / 150 MW in NEW-SR Import / Export. 765KV-WARANGAL(NEW)-WARORA-2 35% 765kV-SOLAPUR - RAICHUR_PG D/C 12% each 765kV-WARDHA - NIZAMABAAD D/C 12% each 765kV-RAICHUR - KURNOOL_PG D/C 9% each 765kV-NIZAMABAAD - MAHESHWARAM D/C 8% each All 765kV/400kV WARANGAL and RAICHUR and NIZAMABAAD ICTs shall be in service. | Line Circuits | 19-May-2026 | 10:20 | 20-May-2026 | 11:00
RQ109061 | PNOCC | aptransco | 400KV/220KV URAVAKONDA-ICT-1 | APTRANSCO | C | for replacement of 220kV IV Bushings due to critical Tan Delta values | 2026-05-25 | 07:00 | 2026-05-25 | 16:00 | To avert any potential equipment failure &in view of the upcoming wind generation season, it is imperative to ensure the maximum reliability and healthiness of both ICTs to handle the anticipated load without interruption | Yes | Approved | Load Management need to be done by AP. N-1 limit for URAVAKONDA ICTs is 207 MW for 315 MVA ICT each and 329 MW for 500 MVA ICT each. 400KV/220KV URAVAKONDA-ICT-3 33% 400KV/220KV URAVAKONDA-ICT-4 33% 400KV/220KV URAVAKONDA-ICT-2 21% All CUDDAPAH ICTs shall be in service. | Transformer | 18-May-2026 | 16:47 | 22-May-2026 | 14:59
RQ109063 | PNOCC | aptransco | 400KV/220KV URAVAKONDA-ICT-2 | APTRANSCO | C | for replacement of 220kV IV Bushings due to critical Tan Delta values | 2026-05-26 | 07:00 | 2026-05-26 | 16:00 | To avert any potential equipment failure &in view of the upcoming wind generation season, it is imperative to ensure the maximum reliability and healthiness of both ICTs to handle the anticipated load without interruption | Yes | Approved | Load Management need to be done by AP. N-1 limit for URAVAKONDA ICTs is 207 MW for 315 MVA ICT each and 329 MW for 500 MVA ICT each. 400KV/220KV URAVAKONDA-ICT-3 33% 400KV/220KV URAVAKONDA-ICT-4 33% 400KV/220KV URAVAKONDA-ICT-1 21% All CUDDAPAH ICTs shall be in service. | Transformer | 18-May-2026 | 16:49 | 23-May-2026 | 16:49
RQ106756 | OCC_237 | KNTL | KOPPAL - 220KV - BUS 3 | INDIGRID | D | Yearly Bay equipment testing and preventive maintenance. | 2026-05-22 | 09:00 | 2026-05-22 | 17:00 |  | Yes | Rejected | As per mail forwarded by PGCIL SR-2 for the concurrence from KNTL not to avail the bus shutdown. | Bus | 19-May-2026 | 08:20 | 19-May-2026 | 10:37
RQ107473 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-KURNOOL_PG-MAHESHWARAM_PG-1 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP146-AP147 | 2026-05-22 | 06:00 | 2026-05-22 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 18-May-2026 | 17:40 | 19-May-2026 | 10:09
RQ107484 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-KURNOOL_PG-MAHESHWARAM_PG-2 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP146-AP147 | 2026-05-22 | 06:00 | 2026-05-22 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 18-May-2026 | 17:40 | 19-May-2026 | 10:09
RQ107495 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-NIZAMABAD-MAHESHWARAM_PG-1 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP147-AP148 | 2026-05-22 | 06:00 | 2026-05-22 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 18-May-2026 | 17:40 | 19-May-2026 | 10:09
RQ107506 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-NIZAMABAD-MAHESHWARAM_PG-2 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP147-AP148 | 2026-05-22 | 06:00 | 2026-05-22 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 18-May-2026 | 17:40 | 19-May-2026 | 10:09
RQ106902 | OCC_237 | PGCIL SR-1 | 400KV-NAGARJUNASAGAR_PG-MEHBOOBNAGAR-1 | POWERGRID | D | amp works | 2026-05-22 | 09:00 | 2026-05-22 | 18:00 | AMP WORKS | Yes | Approved | 400KV-YEDULA-DINDI-2 25% 400KV-YEDULA-MEHBOOBNAGAR D/C 13% each 400KV-KHAMMAM_PG-NAGARJUNASAGAR_PG-1,2,3 11% each 400KV-KURNOOL_PG-NAGARJUNASAGAR_PG-1 10% 400KV-MAHESHWARAM_PG-GHANAPUR-1 9% shall be in service. | Line Circuits | 18-May-2026 | 17:40 | 19-May-2026 | 15:16
RQ106958 | OCC_237 | TGTRANSCO | 400KV-YADADRI TPP-CHOUTUPPAL-1 | TGTRANSCO | C | For periodical testing and general maintenance | 2026-05-22 | 10:00 | 2026-05-22 | 18:00 |  | Yes | Rejected | Due to Multiple shutdowns in near vicinity having sensitivity overlapping. | Line Circuits | 18-May-2026 | 15:35 | 19-May-2026 | 15:21
RQ106968 | OCC_237 | TGTRANSCO | 400KV-MAHESHWARAM_TG-DINDI-1 | TGTRANSCO | C | General and periodical maintenance works to be done by both maintenance and MRT wings | 2026-05-22 | 10:00 | 2026-05-22 | 17:00 |  | Yes | Approved | 400KV-MAHESHWARAM_TG-DINDI-2 31% 400KV-YEDULA-DINDI-2 18% 400KV-YADADRI TPP-DINDI D/C 14% each 400KV-MAHESHWARAM_TG-MAMIDAPALLI D/C 10% each shall be in service. | Line Circuits | 18-May-2026 | 15:35 | 19-May-2026 | 15:16
RQ107054 | OCC_237 | PGCIL SR-2 | A/R of 400KV-HOSUR_PG-KOLAR_AC-1 | POWERGRID | D | Attending shutdown nature defects in a D/C Tower during Line-2 shutdown. | 2026-05-22 | 09:00 | 2026-05-22 | 17:00 |  | No | Rejected | Deferred by requester. | Auto Reclosure | 18-May-2026 | 14:24 | 19-May-2026 | 10:09
RQ107057 | OCC_237 | PGCIL SR-2 | PUGALUR - 400KV - BUS 2 | PGCIL SR-2 | D | AMP works of 400 kV Bus-2 | 2026-05-22 | 09:00 | 2026-05-22 | 17:00 |  | Yes | Approved | Remaining all elements shall be in service. | Bus | 18-May-2026 | 14:16 | 19-May-2026 | 10:37
RQ106631 | OCC_237 | aptransco | GHANI - 400KV B/R 2 | APTRANSCO | D | For Relay& Equipment testing works | 2026-05-22 | 10:00 | 2026-05-22 | 17:00 | Annual maintenance works | Yes | Approved | Concurred, subject to real time grid conditions. | Bus Reactor | 18-May-2026 | 11:34 | 19-May-2026 | 10:09
RQ106547 | OCC_237 | aptransco | 400KV-KRISHNAPATNAM-RACHAGUNNERI-1 | APTRANSCO | D | Tightening of spacer dampers and providing of missing keepers to dampers between loc. No:85 to 83 , arranging repair sleeves to conductor damages between loc.No:85 to 83 Top phase in 400KV KrishnapatnamRachagunneri-1 feeder. | 2026-05-22 | 07:00 | 2026-05-22 | 17:00 | During the LC period there will be no interruption to loads as 400KV Krishnapatnam TPP - Manubolu feeder, 400KV SEIL – Manubolu feeder, 400KV Krishnapatnam-SEIL feeder and 400KV Krishnapatnam TPP – Rachagunneri - 2 feeders will be in Service. | Yes | Approved | 400KV-RACHAGUNNERI-KRISHNAPATNAM-2 44% 400KV-KRISHNAPATNAM-NELLORE_AP-1 30% 400KV-SEILU2_AP-NELLORE_AP-1 26% 400KV-NELLORE_AP-NELLORE_PG-1 21% 400KV-TVLM-CHITTOOR D/C 11% each 400KV-SRIPERUMBADUR-NELLORE_PG-1 10% All NELLORE_AP ICTs shall be in service. | Line Circuits | 18-May-2026 | 11:32 | 19-May-2026 | 10:31
RQ106578 | OCC_237 | aptransco | 132KV-PAMMY-CHILLAKALLU-1 | TGTRANSCO | D | Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | 2026-05-22 | 08:00 | 2026-05-22 | 18:00 | Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | Yes | Approved | Load management to be done by AP & TG for multiple outages | Line Circuits | 18-May-2026 | 11:32 | 19-May-2026 | 10:24
RQ106588 | OCC_237 | aptransco | 132KV-CHILLAKALLU-PEDAGOPATHI-1 | APTRANSCO,TGTRANSCO | D | D/C line Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | 2026-05-22 | 08:00 | 2026-05-22 | 18:00 | D/C line Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | Yes | Approved | Load management to be done by AP & TG for multiple outages | Line Circuits | 18-May-2026 | 11:32 | 19-May-2026 | 10:24
RQ106522 | OCC_237 | kseb | A/R of 220KV-KOCHI-KALAMASSERY-2 | KSEB | D | Disc replacement work | 2026-05-22 | 09:00 | 2026-05-22 | 17:00 | Disc replacement work | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 18-May-2026 | 11:07 | 19-May-2026 | 10:18
RQ106538 | OCC_237 | NTPC | 400KV-KUDGI_PG-KUDGI_NTPC-3 | KTL | C | yearly line side equipment maintenance | 2026-05-22 | 07:00 | 2026-05-23 | 19:00 |  | Yes | Approved | 400KV-KUDGI_PG-KUDGI_NTPC-1,2,4 33% each shall be in service. Subject to real time weather condition and line loadings. | Line Circuits | 18-May-2026 | 10:25 | 19-May-2026 | 10:24
RQ106458 | OCC_237 | ILFS | 400KV-ILFS-NAGAPATTNAM_PS-2 | ILFS | D | Spacer Repair Maintenance/Replacement. | 2026-05-22 | 09:00 | 2026-05-22 | 17:00 | Non- Continuous, Line will be charged at evening. | Yes | Approved | No N-1 for ILFS, Subject to at least one unit outage and real time grid conditions. 400KV-ILFS-NAGAPATTNAM_PS-1 100% shall be in service. | Line Circuits | 18-May-2026 | 10:15 | 19-May-2026 | 10:18
RQ106755 | OCC_237 | KNTL | KOPPAL - 220KV - BUS 2 | INDIGRID | D | Yearly Bay equipment testing and preventive maintenance. | 2026-05-21 | 09:00 | 2026-05-21 | 17:00 |  | Yes | Approved | Remaining all elements shall be in service. | Bus | 18-May-2026 | 08:31 | 18-May-2026 | 11:55
RQ106513 | OCC_237 | TANTRANSCO | KAMUDHI - 400KV - BUS 2 | TANTRANSCO | D | Monthly Maintenance work | 2026-05-21 | 16:00 | 2026-05-21 | 21:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Bus | 17-May-2026 | 20:26 | 18-May-2026 | 11:51
RQ106514 | OCC_237 | TANTRANSCO | KAMUDHI - 400KV B/R 2 | TANTRANSCO | D | Monthly Maintenance work | 2026-05-21 | 16:00 | 2026-05-21 | 21:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Bus Reactor | 17-May-2026 | 20:26 | 18-May-2026 | 11:51
RQ106719 | OCC_237 | TANTRANSCO | 400KV-KAYATHAR-THENNAMPATTY-1 | TANTRANSCO | D | Monthly Maintenance Work | 2026-05-21 | 10:00 | 2026-05-21 | 17:00 |  | Yes | Approved | 400KV-VIRUDHUNAGAR-THENNAMPATTY-1 40% 400KV-VIRUDHUNAGAR-KAYATHAR-1 39% 400KV-OTTAPIDARAM-KAMUDHI D/C 17% each 400KV-KAMUDHI-KARAIKUDI D/C 17% each shall be in service along with All OTTAPIDARAM and THENNAMPATTY ICTs. | Line Circuits | 17-May-2026 | 20:26 | 18-May-2026 | 13:18
RQ106577 | OCC_237 | aptransco | 132KV-PAMMY-CHILLAKALLU-1 | TGTRANSCO | D | Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | 2026-05-21 | 08:00 | 2026-05-21 | 18:00 | Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | Yes | Approved | Load management to be done by AP & TG for multiple outages | Line Circuits | 17-May-2026 | 18:54 | 18-May-2026 | 11:55
RQ106587 | OCC_237 | aptransco | 132KV-CHILLAKALLU-PEDAGOPATHI-1 | APTRANSCO,TGTRANSCO | D | D/C line Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | 2026-05-21 | 08:00 | 2026-05-21 | 18:00 | D/C line Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | Yes | Approved | Load management to be done by AP & TG for multiple outages | Line Circuits | 17-May-2026 | 18:54 | 18-May-2026 | 11:55
RQ106635 | OCC_237 | aptransco | PODILI - 400KV B/R 1 | APTRANSCO | D | FOR PERIODICAL MAINTENANCE AND MRT WORKS | 2026-05-21 | 09:00 | 2026-05-21 | 17:00 | Annual maintenance works | Yes | Approved | Concurred, subject to real time grid conditions. | Bus Reactor | 17-May-2026 | 18:54 | 18-May-2026 | 13:18
RQ106654 | OCC_237 | aptransco | 400KV/220KV HINDUPUR-ICT-4 | APTRANSCO | D | "1. Half yearly Maintenance works 2. Periodical Relay testing of ICT *Note : ICT-1,2&3 Will be in service" | 2026-05-21 | 10:00 | 2026-05-21 | 16:00 | Annual maintenance works | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. Load Management need to be done by AP. N-1 limit for HINDUPUR ICTs is 220 MW each. ICT-2 is under long shutdown for diversion to Gudiwada. 400KV/220KV HINDUPUR-ICT-1 36% 400KV/220KV HINDUPUR-ICT-3 36% All GOOTY ICTs shall be in service. | Transformer | 17-May-2026 | 18:54 | 18-May-2026 | 13:03
RQ106658 | OCC_237 | aptransco | 400KV/220KV URAVAKONDA-ICT-3 | APTRANSCO | D | "1. Half yearly Maintenance works 2. Periodical Relay testing of ICT *Note : ICT-1,2&4 Will be in service" | 2026-05-21 | 09:00 | 2026-05-21 | 15:00 | Annual maintenance works | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. Load Management need to be done by AP. N-1 limit for URAVAKONDA ICTs is 207 MW for 315 MVA ICT each and 329 MW for 500 MVA ICT each. 400KV/220KV URAVAKONDA-ICT-4 38% 400KV/220KV URAVAKONDA-ICT-1 24% 400KV/220KV URAVAKONDA-ICT-2 24% All CUDDAPAH ICTs shall be in service. | Transformer | 17-May-2026 | 18:54 | 18-May-2026 | 13:03
RQ106706 | OCC_237 | aptransco | 400KV-SATTENPALLY-PODILI-1 | APTRANSCO | D | For periodical Line Maintenance works | 2026-05-21 | 09:00 | 2026-05-21 | 17:00 | Annual maintenance works | Yes | Rejected | Multiple shutdowns at the same station. | Line Circuits | 17-May-2026 | 18:54 | 18-May-2026 | 13:18
RQ106957 | OCC_237 | TGTRANSCO | 220KV-RAMAGUNDAM-MALYALAPALLI-4 | NTPC | C | For Isolator Overhauling works and Bay Maintenance works | 2026-05-21 | 09:00 | 2026-05-21 | 19:00 |  | Yes | Approved | 220KV-RAMAGUNDAM-MALYALAPALLI-3 42% 220KV-RAMAGUNDAM-MALYALAPALLI-1 28% 220KV-RAMAGUNDAM-MALYALAPALLI-2 28% shall be in service. | Line Circuits | 17-May-2026 | 15:54 | 18-May-2026 | 11:55
RQ107016 | OCC_237 | TGTRANSCO | SRISAILAM_LEFT_BANK - 400KV - BUS 2 | TGGENCO | C | Annual Maintenance works at 400KV GIS- Reconditioning of SF6 gas, repalcement of molecular absorbents in the BUS Ducts of 15 Bays | 2026-05-21 | 06:00 | 2026-05-31 | 23:59 | [From:21/05/2026 06:00 To 09/06/2026 17:00] | Yes | Approved | Approved along with 400kV-SRISAILAM_LEFT_BANK - SATTENPALLY-1. Remaining elements shall be in service. Reason submitted by TG for simultaneously availing the bus and line shutdown: "It is to submit that in order to carry out the Reconditioning of SF6 gas and Replacement of Adsorbents in BUS-B Isolator Section of corresponding Feeder, there must be LC on BUS-B and Corresponding Feeder also. Otherwise the Reconditioning of SF6 gas and Replacement of Adsorbents cannot be carried out on BUS-B Isolator Section of Corresponding Feeder." | Bus | 17-May-2026 | 15:54 | 18-May-2026 | 13:48
RQ107472 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-KURNOOL_PG-MAHESHWARAM_PG-1 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP146-AP147 | 2026-05-21 | 06:00 | 2026-05-21 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 17-May-2026 | 15:19 | 18-May-2026 | 10:13
RQ107483 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-KURNOOL_PG-MAHESHWARAM_PG-2 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP146-AP147 | 2026-05-21 | 06:00 | 2026-05-21 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 17-May-2026 | 15:19 | 18-May-2026 | 10:13
RQ107494 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-NIZAMABAD-MAHESHWARAM_PG-1 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP147-AP148 | 2026-05-21 | 06:00 | 2026-05-21 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 17-May-2026 | 15:19 | 18-May-2026 | 10:13
RQ107505 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-NIZAMABAD-MAHESHWARAM_PG-2 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP147-AP148 | 2026-05-21 | 06:00 | 2026-05-21 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 17-May-2026 | 15:19 | 18-May-2026 | 10:13
RQ107510 | OCC_2371 | PGCIL SR-1 | KURNOOL_PG - 400KV - BUS 2 | PGCIL SR-1 | C | Construction works: AMGEPL line integration (416-418 bays at Kurnool SS): Busbar stability , protection testing and integration | 2026-05-21 | 07:30 | 2026-05-22 | 20:00 | Construction works | No | Rejected | Deferred by requester. | Bus | 17-May-2026 | 15:19 | 18-May-2026 | 10:13
RQ106382 | OCC_237 | TANTRANSCO | 400KV-PALAVADI-RASIPALYAM-4 | TANTRANSCO | D | Preventive maintenance for bay equipments ( Breaker, CT, Isolator, LAS, Line maintenance and tree clearance) and P&C testing works. | 2026-05-21 | 09:00 | 2026-05-21 | 17:00 |  | Yes | Approved | 400KV-PALAVADI-RASIPALYAM-1,2,3 33% each shall be in service. | Line Circuits | 17-May-2026 | 14:50 | 18-May-2026 | 11:51
RQ106848 | OCC_237 | kptcl | 400KV-GUTTUR-HIRIYUR-2 | KPTCL | D | submitting proposal to attend Bus2 R phase PG isolator issue & & 1st Quarterly maintenance | 2026-05-21 | 10:00 | 2026-05-21 | 17:00 |  | Yes | Rejected | Due to 400kV-KAIGA-GUTTUR tower collapse. | Line Circuits | 17-May-2026 | 12:24 | 18-May-2026 | 13:05
RQ106455 | OCC_237 | ILFS | 400KV-ILFS-NAGAPATTNAM_PS-1 | ILFS | D | Spacer Repair Maintenance/Replacement. | 2026-05-19 | 09:00 | 2026-05-19 | 17:00 | Non- Continuous, Line will be charged at evening | Yes | Approved | No N-1 for ILFS, Subject to at least one unit outage and real time grid conditions. 400KV-ILFS-NAGAPATTNAM_PS-2 100% shall be in service. | Line Circuits | 17-May-2026 | 10:16 | 16-May-2026 | 11:00
RQ106662 | OCC_237 | aptransco | 400KV/220KV NELLORE_AP-ICT-4 | APTRANSCO | D | For maintenance Works & MRT Works | 2026-05-21 | 10:00 | 2026-05-21 | 17:00 | Annual maintenance works | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. Load Management need to be done by AP. N-1 limit for NELLORE AP ICTs is 220 MW for 315 MVA ICT each and 376 MW for 500 MVA ICT. 400KV/220KV NELLORE_AP-ICT-1,2,3 22% each All RACHAGUNNERI ICTs 400KV-RACHAGUNNERI-KRISHNAPATNAM D/C shall be in service. SDSTPS generation need to be managed by AP in order to keep remaining NELLORE_AP ICTs within their N-1 limit. | Transformer | 17-May-2026 | 10:13 | 18-May-2026 | 13:03
RQ106457 | OCC_237 | ILFS | 400KV-ILFS-NAGAPATTNAM_PS-2 | ILFS | D | Spacer Repair Maintenance/Replacement. | 2026-05-21 | 09:00 | 2026-05-21 | 17:00 | Non- Continuous, Line will be charged at evening. | Yes | Approved | No N-1 for ILFS, Subject to at least one unit outage and real time grid conditions. 400KV-ILFS-NAGAPATTNAM_PS-1 100% shall be in service. | Line Circuits | 17-May-2026 | 10:01 | 18-May-2026 | 11:51
RQ106456 | OCC_237 | ILFS | 400KV-ILFS-NAGAPATTNAM_PS-1 | ILFS | D | Spacer Repair Maintenance/Replacement. | 2026-05-20 | 09:00 | 2026-05-20 | 17:00 | Non- Continuous, Line will be charged at evening | Yes | Approved | No N-1 for ILFS, Subject to at least one unit outage and real time grid conditions. 400KV-ILFS-NAGAPATTNAM_PS-2 100% shall be in service. | Line Circuits | 17-May-2026 | 06:18 | 17-May-2026 | 10:21
RQ108948 | PNOCC | aptransco | 400KV-GUDIWADA-SATTENPALLY-2 | APTRANSCO | C | rectification of Auto Reclosure function which is observed as the line tripped on 02-05-2026 @12:47 Hrs. | 2026-05-20 | 10:00 | 2026-05-20 | 18:00 |  | Yes | Rejected | Planned Activities to be taken into Main OCC. | Line Circuits | 16-May-2026 | 15:33 | 17-May-2026 | 15:38
RQ106977 | OCC_237 | TGTRANSCO | 400KV/220KV JANAGAON-ICT-1 | TGTRANSCO | C | Yearly MAINTENANCE & Testing OF ICT,Relays & BAY equipment. | 2026-05-20 | 08:00 | 2026-05-20 | 18:00 |  | Yes | Approved | Load Management need to be done by TG. Subject to ICT loadings to be within their N-1 limit. N-1 limit for JANAGAON ICTs is 364 MW each. 400KV/220KV JANAGAON-ICT-2 28% 400KV/220KV JANAGAON-ICT-3 28% All KHAMMAM and MALKARAM ICTs 400KV-TIPPAPUR-CHANDALAPUR D/C shall be in service. | Transformer | 16-May-2026 | 16:23 | 17-May-2026 | 15:33
RQ106994 | OCC_237 | TGTRANSCO | 400KV-VTPS_IV-SURYAPET-2 | APTRANSCO,TGTRANSCO | C | General maintenance works and MRT wing testing works | 2026-05-20 | 10:00 | 2026-05-20 | 17:00 |  | Yes | Approved | 400KV-SURYAPET-VTPS_IV-1 46% 400KV-KHAMMAM_PG-VIJAYAWADA-1 11% 400KV-SURYAPET-MALKARAM D/C 7% each 220KV-SURYAPET-CHILLAKALLU-1 6% 400KV-KETHIREDDYPALLY-SURYAPET-1 5% | Line Circuits | 16-May-2026 | 16:23 | 17-May-2026 | 15:33
RQ106956 | OCC_237 | TGTRANSCO | 220KV-RAMAGUNDAM-MALYALAPALLI-3 | NTPC | C | For Isolator Overhauling works and Bay Maintenance works | 2026-05-20 | 09:00 | 2026-05-20 | 19:00 |  | Yes | Approved | 220KV-RAMAGUNDAM-MALYALAPALLI-4 42% 220KV-RAMAGUNDAM-MALYALAPALLI-1 28% 220KV-RAMAGUNDAM-MALYALAPALLI-2 28% shall be in service. | Line Circuits | 16-May-2026 | 16:23 | 17-May-2026 | 10:29
RQ106945 | OCC_237 | PGCIL SR-1 | A/R of 400KV-GOOTY-KURNOOL_PG-1 | POWERGRID | D | Hot line stringing works 400kV D/C Peddapodilla to Bethapalle Line at Existing 400kV S/C Gooty – Kurnool (PG) Line, tower no. 746 & 747 - Auto reclosure to be kept in non auto mode | 2026-05-20 | 09:00 | 2026-05-20 | 18:00 | Construction works | Yes | Rejected | Multiple shutdowns at the same station. PGCIL requested to avail the shutdown of 400kV-KURNOOL-BUS-1. | Auto Reclosure | 16-May-2026 | 16:09 | 17-May-2026 | 10:29
RQ107482 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-KURNOOL_PG-MAHESHWARAM_PG-2 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP146-AP147 | 2026-05-20 | 06:00 | 2026-05-20 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 16-May-2026 | 16:06 | 17-May-2026 | 10:24
RQ107493 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-NIZAMABAD-MAHESHWARAM_PG-1 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP147-AP148 | 2026-05-20 | 06:00 | 2026-05-20 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 16-May-2026 | 16:06 | 17-May-2026 | 10:24
RQ107056 | OCC_237 | PGCIL SR-2 | PUGALUR - 400KV - BUS 1 | PGCIL SR-2 | D | AMP works of 400 kV Bus-1 | 2026-05-20 | 09:00 | 2026-05-20 | 17:00 |  | Yes | Approved | Remaining all elements shall be in service. | Bus | 16-May-2026 | 15:39 | 17-May-2026 | 15:33
RQ107528 | OCC_2371 | PGCIL SR-2 | 400KV-GADAG_PSS-KOPPAL-1 | GADAG_II_A | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 11/0 - 12/0 | 2026-05-20 | 08:00 | 2026-05-20 | 19:00 | 400KV-GADAG_PSS-KOPPAL- D/C Outage is required to carry out powerline crossing works. Concurrence from connected IPPs will be submitted on D-4 basis. | Yes | Approved | PGCIL SR-2 submitted the RE developer concurrence through mail dated 07-05-2026. 400kV-KUDGI_PG - KOPPAL D/C 50% 400kV-KUDGI_PG - GADAG D/C each shall be in service. Subject to real time RE generation and line loadings. Subject to adherence of proper RE schedules. | Line Circuits | 16-May-2026 | 15:39 | 17-May-2026 | 10:36
RQ107530 | OCC_2371 | PGCIL SR-2 | 400KV-GADAG_PSS-KOPPAL-2 | GADAG_II_A | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 11/0 - 12/0 | 2026-05-20 | 08:00 | 2026-05-20 | 19:00 | 400KV-GADAG_PSS-KOPPAL- D/C Outage is required to carry out powerline crossing works. Concurrence from connected IPPs will be submitted on D-4 basis. | Yes | Approved | PGCIL SR-2 submitted the RE developer concurrence through mail dated 07-05-2026. 400kV-KUDGI_PG - KOPPAL D/C 50% 400kV-KUDGI_PG - GADAG D/C each shall be in service. Subject to real time RE generation and line loadings. Subject to adherence of proper RE schedules. | Line Circuits | 16-May-2026 | 15:39 | 17-May-2026 | 10:36
RQ107471 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-KURNOOL_PG-MAHESHWARAM_PG-1 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP146-AP147 | 2026-05-20 | 06:00 | 2026-05-20 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 16-May-2026 | 15:34 | 17-May-2026 | 10:24
RQ107504 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-NIZAMABAD-MAHESHWARAM_PG-2 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP147-AP148 | 2026-05-20 | 06:00 | 2026-05-20 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 16-May-2026 | 15:34 | 17-May-2026 | 10:24
RQ108942 | PNOCC | NPCIL | 220KV-KAIGA-KADRA-1 | KPTCL | C | Preventive maintenance work of bay equipment | 2026-05-23 | 08:00 | 2026-05-24 | 20:00 | Earlier 3 requests since April were differed, to complete PM before monsoon, Line outage is essential. 3Days (up to 25/05/26) outage required to complete all PM and Testing | Yes | Approved | Concurrence received from KPTCL regarding load and hydro generation management to avoid overloading of 220kV Kodsalli-Kaiga line. No N-1 for 220kV-KODASALLI-KAIGA. 220kV-KADRA-KODASALLY 220kV-KODASALLI-KAIGA shall be in service. | Line Circuits | 16-May-2026 | 14:58 | 21-May-2026 | 12:24
RQ106853 | OCC_237 | kptcl | 400KV-MYSORE-NELAMANGALA-1 | POWERGRID | C | The Erection and line stringing work of the proposed Huliyurudurga 400/220/66KV Sub Station is in the verge of completion and it is planned for 2 No's of (DD+0 and DD+3 ) LILO towers erection in between Tower No. 160 and 161 of the 400kV Nelamangala-Bastipura( Mysore )DC Twin moose lineand 390 Mtrs of conductor stringing in the month of May 2026 | 2026-05-20 | 09:00 | 2026-05-29 | 18:00 | line clear of 400kV Nelamangala-Bastipura( Mysore )DC Twin moose line for the period of 10Days (20.05.2026 to 29.05.2026). | No | Rejected | Deferred by requester. | Line Circuits | 16-May-2026 | 14:20 | 17-May-2026 | 10:24
RQ106854 | OCC_237 | kptcl | 400KV-MYSORE-NELAMANGALA-2 | POWERGRID | C | The Erection and line stringing work of the proposed Huliyurudurga 400/220/66KV Sub Station is in the verge of completion and it is planned for 2 No's of (DD+0 and DD+3 ) LILO towers erection in between Tower No. 160 and 161 of the 400kV Nelamangala-Bastipura( Mysore )DC Twin moose lineand 390 Mtrs of conductor stringing in the month of May 2026 | 2026-05-20 | 09:00 | 2026-05-29 | 18:00 | line clear of 400kV Nelamangala-Bastipura( Mysore )DC Twin moose line for the period of 10Days (20.05.2026 to 29.05.2026). | No | Rejected | Deferred by requester. | Line Circuits | 16-May-2026 | 14:20 | 17-May-2026 | 10:24
RQ106520 | OCC_237 | kseb | A/R of 220KV-KOCHI-KALAMASSERY-2 | KSEB | D | Disc replacement work | 2026-05-20 | 09:00 | 2026-05-20 | 17:00 | Disc replacement work | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 16-May-2026 | 13:30 | 17-May-2026 | 10:29
RQ106452 | OCC_237 | TANTRANSCO | 400KV-KAYATHAR-VIRUDHUNAGAR-1 | TANTRANSCO | D | Monthly Maintenance Work | 2026-05-20 | 09:00 | 2026-05-20 | 17:00 |  | Yes | Approved | 400KV-THENNAMPATTY-KAYATHAR-1 52% 400KV-OTTAPIDARAM-KAMUDHI D/C 14% each 400KV-KAMUDHI-KARAIKUDI D/C 14% each All OTTAPIDARAM and THENNAMAPATTY ICTs shall be in service. | Line Circuits | 16-May-2026 | 13:03 | 17-May-2026 | 15:36
RQ106479 | OCC_237 | TANTRANSCO | 400KV/230KV KANARPATTI-ICT-2 | TANTRANSCO | D | Monthly Maintenance work | 2026-05-20 | 14:00 | 2026-05-20 | 20:00 |  | Yes | Approved | subject to real time grid conditions. N-1 limit for KANARPATTI ICTs is 238 MW each. 400KV/230KV KANARPATTI-ICT-1 100% shall be in service. ICT loadings to be within their N-1 limit. | Transformer | 16-May-2026 | 13:03 | 17-May-2026 | 15:36
RQ106519 | OCC_237 | kseb | A/R of 220KV-KOCHI-KALAMASSERY-2 | KSEB | D | Disc replacement work | 2026-05-18 | 09:00 | 2026-05-18 | 17:00 | Disc replacement work | Yes | Approved | Concurred, subject to real time grid conditions. Availing status received as yes through mail communication. | Auto Reclosure | 16-May-2026 | 10:56 | 15-May-2026 | 10:24
RQ106531 | OCC_237 | kseb | 400KV-KOZHIKODE-MADAKKATHARA-1 | KSEB | D | Annual Maintenance work | 2026-05-18 | 08:00 | 2026-05-18 | 17:00 | Annual Maintenance work | Yes | Rejected | Availing status received as yes through mail communication. Due to multiple overlapping shutdowns at the same station and sensitivity overlapping on other highly loaded elements. 400KV/220KV THRISSUR HVDC-ICT-1,2 6% each 400KV/220KV MADAKATHARA-ICT-1,2,3 4% each. | Line Circuits | 16-May-2026 | 10:56 | 15-May-2026 | 10:24
RQ106576 | OCC_237 | aptransco | 132KV-PAMMY-CHILLAKALLU-1 | TGTRANSCO | D | Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | 2026-05-20 | 08:00 | 2026-05-20 | 18:00 | Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | Yes | Approved | Load management to be done by AP & TG for multiple outages | Line Circuits | 16-May-2026 | 10:20 | 17-May-2026 | 10:33
RQ106586 | OCC_237 | aptransco | 132KV-CHILLAKALLU-PEDAGOPATHI-1 | APTRANSCO,TGTRANSCO | D | D/C line Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | 2026-05-20 | 08:00 | 2026-05-20 | 18:00 | D/C line Stringing of snapped Earth wire from Loc.Nos. 104 to 113 and clearing of vegetation in various locations from 104 to 138 by CBD Gang | Yes | Approved | Load management to be done by AP & TG for multiple outages | Line Circuits | 16-May-2026 | 10:20 | 17-May-2026 | 10:33
RQ106634 | OCC_237 | aptransco | NARNOOR - 400KV B/R 1 | APTRANSCO | D | For Annualy and Quarterly maintenance works(for Reactor Testings) | 2026-05-20 | 10:00 | 2026-05-20 | 16:00 | Annual maintenance works | Yes | Approved | Concurred, subject to real time grid conditions. | Bus Reactor | 16-May-2026 | 10:20 | 17-May-2026 | 10:33
RQ106670 | OCC_237 | aptransco | GUDDIGUDEM - 400KV - BUS 1 | APTRANSCO | D | For general maintenance by Mintenance wing and periodical testing of equipment by maintenance and MRT | 2026-05-20 | 09:00 | 2026-05-20 | 17:00 | Annual maintenance works | Yes | Approved | Concurred, subject to real time grid conditions. | Bus | 16-May-2026 | 10:20 | 17-May-2026 | 10:29
RQ106469 | OCC_237 | WKTL | 765KV-KURNOOL_PG-MAHESHWARAM_PG-2 | POWERGRID | D | Insulator Replacement | 2026-05-20 | 08:00 | 2026-05-20 | 18:00 | Insulator Replacement | No | Rejected | Deferred by requester. | Line Circuits | 16-May-2026 | 10:15 | 17-May-2026 | 10:24
RQ106754 | OCC_237 | KNTL | KOPPAL - 220KV - BUS 1 | INDIGRID | D | Yearly Bay equipment testing and preventive maintenance. | 2026-05-19 | 09:00 | 2026-05-19 | 17:00 |  | Yes | Rejected | Multiple shutdowns at the same station. | Bus | 16-May-2026 | 08:48 | 16-May-2026 | 16:02
RQ108931 | PNOCC | TGTRANSCO | 132KV-KODADA-CHILLAKALLU-1 | APTRANSCO,TGTRANSCO | C | Replacement of first section of damaged tower at loc.no.44 and also Stringing of Earth wire from loc.no.60 to 71. | 2026-05-25 | 00:00 | 2026-05-25 | 17:00 | It is very urgent to replace the damaged tower parts, and this is the appropriate season to complete the work, as the agricultural season will commence later. Further, the agency is ready to carry out the works. Hence, it is requested to kindly consider and approve the shutdown for the period From 19/05/2026 08:00 To 25/05/2026 17:00. | Yes | Rejected | Multiple shutdowns at the same station. | Line Circuits | 15-May-2026 | 18:46 | 22-May-2026 | 12:53
RQ108930 | PNOCC | TGTRANSCO | 132KV-KODADA-CHILLAKALLU-1 | APTRANSCO,TGTRANSCO | C | Replacement of first section of damaged tower at loc.no.44 and also Stringing of Earth wire from loc.no.60 to 71. | 2026-05-23 | 00:00 | 2026-05-24 | 23:59 | It is very urgent to replace the damaged tower parts, and this is the appropriate season to complete the work, as the agricultural season will commence later. Further, the agency is ready to carry out the works. Hence, it is requested to kindly consider and approve the shutdown for the period From 19/05/2026 08:00 To 25/05/2026 17:00. | Yes | Rejected | Planned Activities to be taken into Main OCC. | Line Circuits | 15-May-2026 | 18:43 | 20-May-2026 | 23:10
RQ108929 | PNOCC | TGTRANSCO | 132KV-KODADA-CHILLAKALLU-1 | APTRANSCO,TGTRANSCO | C | Replacement of first section of damaged tower at loc.no.44 and also Stringing of Earth wire from loc.no.60 to 71. | 2026-05-21 | 00:00 | 2026-05-22 | 23:59 | It is very urgent to replace the damaged tower parts, and this is the appropriate season to complete the work, as the agricultural season will commence later. Further, the agency is ready to carry out the works. Hence, it is requested to kindly consider and approve the shutdown for the period From 19/05/2026 08:00 To 25/05/2026 17:00. | Yes | Rejected | Multiple shutdowns at the same station. Planned Activities to be taken into Main OCC. | Line Circuits | 15-May-2026 | 18:40 | 18-May-2026 | 11:57
RQ108928 | PNOCC | TGTRANSCO | 132KV-KODADA-CHILLAKALLU-1 | APTRANSCO,TGTRANSCO | C | Replacement of first section of damaged tower at loc.no.44 and also Stringing of Earth wire from loc.no.60 to 71. | 2026-05-19 | 18:05 | 2026-05-20 | 23:59 | It is very urgent to replace the damaged tower parts, and this is the appropriate season to complete the work, as the agricultural season will commence later. Further, the agency is ready to carry out the works. Hence, it is requested to kindly consider and approve the shutdown for the period From 19/05/2026 08:00 To 25/05/2026 17:00. | Yes | Rejected | Concurrence from AP is required. AP already availing the shutdown on Daily basis. | Line Circuits | 15-May-2026 | 18:38 | 16-May-2026 | 11:04
RQ106903 | OCC_237 | PGCIL SR-1 | 400KV-MEHBOOBNAGAR-RTPS-1 | POWERGRID | C | For Jack bus erection of 400KV RTPS-Mahaboobnagar line under bay upgradation works | 2026-05-19 | 07:00 | 2026-05-21 | 19:00 | Construction works under ADD-CAP. | Yes | Rejected | Bay and line upgradations are completed and FTC is also facilitated. Details of the works shall be shared | Line Circuits | 15-May-2026 | 17:52 | 16-May-2026 | 16:44
RQ106924 | OCC_237 | PGCIL SR-1 | RTPS - 400KV - BUS 2 | KPCL | C | For Jack bus above bus-2 erection of 400KV RTPS-Mahaboobnagar line under bay upgradation works | 2026-05-19 | 07:00 | 2026-05-21 | 19:00 | Construction works under ADD-CAP. | Yes | Rejected | Bay and line upgradations are completed and FTC is also facilitated. Details of the works shall be shared | Bus | 15-May-2026 | 17:52 | 16-May-2026 | 16:44
RQ106944 | OCC_237 | PGCIL SR-1 | A/R of 400KV-GOOTY-KURNOOL_PG-1 | POWERGRID | D | Hot line stringing works 400kV D/C Peddapodilla to Bethapalle Line at Existing 400kV S/C Gooty – Kurnool (PG) Line, tower no. 746 & 747 - Auto reclosure to be kept in non auto mode | 2026-05-19 | 09:00 | 2026-05-19 | 18:00 | Construction works | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 15-May-2026 | 17:40 | 16-May-2026 | 11:08
RQ106914 | OCC_237 | PGCIL SR-1 | 765KV/400KV MAHESHWARAM_PG-ICT-3 | PGCIL SR-1 | C | For Spare change over, to commissiong New Spare Aux. ICT Bus under SS-118 and SS-12T. | 2026-05-19 | 09:00 | 2026-05-20 | 09:00 | Construction works | No | Rejected | Deferred by requester. | Transformer | 15-May-2026 | 17:40 | 16-May-2026 | 11:00
RQ106955 | OCC_237 | TGTRANSCO | 220KV-RAMAGUNDAM-MALYALAPALLI-2 | NTPC | C | For Isolator Overhauling works and Bay Maintenance works | 2026-05-19 | 09:00 | 2026-05-19 | 19:00 |  | Yes | Approved | 220KV-RAMAGUNDAM-MALYALAPALLI-3 37% 220KV-RAMAGUNDAM-MALYALAPALLI-4 37% 220KV-RAMAGUNDAM-MALYALAPALLI-1 25% shall be in service. | Line Circuits | 15-May-2026 | 16:36 | 16-May-2026 | 11:08
RQ106995 | OCC_237 | TGTRANSCO | 400KV-RAMADUGU-TIPPAPUR-1 | TGTRANSCO | C | Periodical testing of bay equipment | 2026-05-19 | 10:00 | 2026-05-19 | 18:00 |  | Yes | Approved | 400KV-TIPPAPUR-RAMADUGU-2 50% 400KV-RAMADUGU-GAJWEL D/C 9% each 400KV-CHANDALAPUR-BHOOPALAPALLY D/C 400KV-TELANGANA_STPP-NARSAPUR D/C All RAMADUGU ICTs shall be in service. | Line Circuits | 15-May-2026 | 16:36 | 16-May-2026 | 11:36
RQ106965 | OCC_237 | TGTRANSCO | 400KV/220KV DINDI-ICT-2 | TGTRANSCO | C | General and periodical maintenance to be done by both Maintenance and TRE wings | 2026-05-19 | 10:00 | 2026-05-19 | 17:00 |  | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. Load Management need to be done by TG. N-1 limit for DINDI ICTs is 238 MW each. 400KV/220KV DINDI-ICT-1 25% All MEHBOOBNAGAR and N'SAGAR ICTs shall be in service. | Transformer | 15-May-2026 | 16:36 | 16-May-2026 | 16:02
RQ107470 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-KURNOOL_PG-MAHESHWARAM_PG-1 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP146-AP147 | 2026-05-19 | 06:00 | 2026-05-19 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 15-May-2026 | 16:26 | 16-May-2026 | 11:00
RQ107481 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-KURNOOL_PG-MAHESHWARAM_PG-2 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP146-AP147 | 2026-05-19 | 06:00 | 2026-05-19 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 15-May-2026 | 16:26 | 16-May-2026 | 11:00
RQ107492 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-NIZAMABAD-MAHESHWARAM_PG-1 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP147-AP148 | 2026-05-19 | 06:00 | 2026-05-19 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 15-May-2026 | 16:26 | 16-May-2026 | 11:00
RQ107503 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-NIZAMABAD-MAHESHWARAM_PG-2 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP147-AP148 | 2026-05-19 | 06:00 | 2026-05-19 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 15-May-2026 | 16:26 | 16-May-2026 | 11:00
RQ106392 | OCC_237 | TANTRANSCO | 400KV/230KV MTPS_ST_III-ICT-2 | TANTRANSCO | D | Preventive maintenance for bay equipments, Transformer maintenance and P&C testing work. | 2026-05-19 | 09:00 | 2026-05-19 | 17:00 |  | Yes | Approved | Load Management need to be done by TN. N-1 limit for MTPS ICTs is 229 MW each. Subject to ICT loadings to be within their N-1 limit. 400KV/230KV MTPS_ST_III-ICT-1 30% All PALAVADI, SALEM and ARASUR ICTs shall be in service along with 400kV-PALAVADI - MTPS D/C. | Transformer | 15-May-2026 | 14:12 | 16-May-2026 | 16:02
RQ107527 | OCC_2371 | PGCIL SR-2 | 400KV-GADAG_PSS-KOPPAL-1 | GADAG_II_A | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 11/0 - 12/0 | 2026-05-19 | 08:00 | 2026-05-19 | 19:00 | 400KV-GADAG_PSS-KOPPAL- D/C Outage is required to carry out powerline crossing works. Concurrence from connected IPPs will be submitted on D-4 basis. | Yes | Approved | PGCIL SR-2 submitted the RE developer concurrence through mail dated 07-05-2026. 400kV-KUDGI_PG - KOPPAL D/C 50% 400kV-KUDGI_PG - GADAG D/C each shall be in service. Subject to real time RE generation and line loadings. Subject to adherence of proper RE schedules. | Line Circuits | 15-May-2026 | 14:03 | 16-May-2026 | 16:25
RQ107529 | OCC_2371 | PGCIL SR-2 | 400KV-GADAG_PSS-KOPPAL-2 | GADAG_II_A | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 11/0 - 12/0 | 2026-05-19 | 08:00 | 2026-05-19 | 19:00 | 400KV-GADAG_PSS-KOPPAL- D/C Outage is required to carry out powerline crossing works. Concurrence from connected IPPs will be submitted on D-4 basis. | Yes | Approved | PGCIL SR-2 submitted the RE developer concurrence through mail dated 07-05-2026. 400kV-KUDGI_PG - KOPPAL D/C 50% 400kV-KUDGI_PG - GADAG D/C each shall be in service. Subject to real time RE generation and line loadings. Subject to adherence of proper RE schedules. | Line Circuits | 15-May-2026 | 14:03 | 16-May-2026 | 16:25
RQ106716 | OCC_237 | TANTRANSCO | 400KV-THENNAMPATTY-VIRUDHUNAGAR-1 | TANTRANSCO | D | Monthly Maintenance Work | 2026-05-19 | 10:00 | 2026-05-19 | 17:00 |  | Yes | Approved | 400KV-THENNAMPATTY-KAYATHAR-1 52% 400KV-OTTAPIDARAM-KAMUDHI D/C 14% each 400KV-KAMUDHI-KARAIKUDI D/C 14% each All OTTAPIDARAM and THENNAMAPATTY ICTs shall be in service. | Line Circuits | 15-May-2026 | 13:12 | 16-May-2026 | 11:36
RQ106727 | OCC_237 | TANTRANSCO | 230KV-TIRUNELVELI-VEERANAM-2 | TANTRANSCO | D | Monthly Maintenance Work | 2026-05-19 | 09:00 | 2026-05-19 | 17:00 |  | Yes | Approved | Load Management need to be done by TN. Subject to real time grid conditions and line loadings. 230KV-VEERANAM-TIRUNELVELI-1 65% 230KV-VEERANAM-KAYATHAR(TN)-1 18% 220KV-MADURAI_PG-CHECKKANURANI D/C shall be in service. | Line Circuits | 15-May-2026 | 13:12 | 16-May-2026 | 16:25
RQ106374 | OCC_237 | TANTRANSCO | 400KV/110KV KAMUDHI-ICT-5 | TANTRANSCO | D | Monthly Maintenance Work | 2026-05-19 | 16:00 | 2026-05-19 | 21:00 |  | Yes | Approved | Load Management need to be done by TN. | Transformer | 15-May-2026 | 13:12 | 16-May-2026 | 11:04
RQ106555 | OCC_237 | NTPC | 400KV-KUDGI_PG-KUDGI_NTPC-2 | KTL | C | line side eqipment yearly maintenance | 2026-05-19 | 07:00 | 2026-05-20 | 19:00 |  | Yes | Approved | 400KV-KUDGI_PG-KUDGI_NTPC-1,3,4 33% each shall be in service. | Line Circuits | 15-May-2026 | 13:03 | 16-May-2026 | 16:28
RQ106822 | OCC_237 | kptcl | TIE BAY (417) OF 400KV-YELHANKA-NELAMANGALA-1 AND 400KV/220KV NELAMANGALA-ICT-1 @NELAMANGALA - 400KV | KPTCL | D | Breaker testing and maintenance works. | 2026-05-19 | 11:00 | 2026-05-19 | 17:00 |  | No | Rejected | Deferred by requester. | Bay | 15-May-2026 | 12:31 | 16-May-2026 | 11:00
RQ106575 | OCC_237 | aptransco | 132KV-KODADA-CHILLAKALLU-1 | APTRANSCO,TGTRANSCO | D | Stringing of snapped Earth wire from Loc. Nos. 8 to 22, 29 to 36 and clearing of vegetation in various locations from 1 to 41 by CBD Gang | 2026-05-19 | 08:00 | 2026-05-19 | 18:00 | Stringing of snapped Earth wire from Loc. Nos. 8 to 22, 29 to 36 and clearing of vegetation in various locations from 1 to 41 by CBD Gang | Yes | Approved | Load management to be done by AP & TG | Line Circuits | 15-May-2026 | 11:34 | 16-May-2026 | 11:08
RQ106656 | OCC_237 | aptransco | 400KV/220KV JAMMALAMADUGU-ICT-2 | APTRANSCO | D | FOR PERIODICAL MAINTENANCE AND MRT TESTINGS | 2026-05-19 | 10:00 | 2026-05-19 | 17:00 | Annual maintenance works | Yes | Approved | Load Management need to be done by AP. N-1 limit for JAMMALAMADUGU ICTs is 186 MW for 315 MVA ICT each and 295 MW for 500 MVA ICT. 400KV/220KV JAMMALAMADUGU-ICT-3 49% 400KV/220KV JAMMALAMADUGU-ICT-1 31% shall be in service. | Transformer | 15-May-2026 | 11:34 | 16-May-2026 | 11:36
RQ106804 | OCC_237 | aptransco | 220KV-CHINTUR-BG KOTHUR-1 | ANDHRA PRADESH,TGTRANSCO | D | Replacement of jumper and insulators at location no 211 | 2026-05-19 | 08:00 | 2026-05-19 | 17:00 | Replacement of jumper and insulators at location no 211 | Yes | Approved | Healthiness of 220kV-ASUPAKA-LOWER SILERU - CHINTOOR need to be ensured. Generation management need to be done by AP. No N-1 for 220kV CHINTUR S/S. Remaining all other lines in near vicinity shall be in service. | Line Circuits | 15-May-2026 | 11:34 | 16-May-2026 | 16:35
RQ106549 | OCC_237 | aptransco | 400KV-KRISHNAPATNAM-RACHAGUNNERI-2 | APTRANSCO | D | Tightening of spacer dampers and providing of missing keepers to dampers between locno:91 to 93 , arranging repair sleeves to conductor damages between loc. No:91- 93 Top phase in 400KV Krishnapatnam-Rachagunneri-2 feeder. | 2026-05-19 | 07:00 | 2026-05-19 | 17:00 | During the LC period there will be no interruption to loads as 400KV Krishnapatnam TPP - Manubolu feeder, 400KV SEIL – Manubolu feeder, 400KV Krishnapatnam-SEIL feeder and 400KV Krishnapatnam TPP – Rachagunneri - 1 feeders will be in Service. | Yes | Approved | 400KV-RACHAGUNNERI-KRISHNAPATNAM-1 44% 400KV-KRISHNAPATNAM-NELLORE_AP-1 30% 400KV-SEILU2_AP-NELLORE_AP-1 26% 400KV-NELLORE_AP-NELLORE_PG-1 21% 400KV-TVLM-CHITTOOR D/C 11% each 400KV-SRIPERUMBADUR-NELLORE_PG-1 10% All NELLORE_AP ICTs shall be in service. | Line Circuits | 15-May-2026 | 11:34 | 16-May-2026 | 16:02
RQ106795 | OCC_237 | NLC | BUS COUPLER BAY (405) OF NTPL - 400KV - BUS 1 AND NTPL - 400KV - BUS 2 @NTPL - 400KV | NTPL | D | GIS Annual Maintenance and Testing | 2026-05-19 | 09:00 | 2026-05-19 | 18:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 15-May-2026 | 11:24 | 16-May-2026 | 11:08
RQ106468 | OCC_237 | WKTL | 765KV-KURNOOL_PG-MAHESHWARAM_PG-2 | POWERGRID | D | Insulator Replacement Activity | 2026-05-19 | 08:00 | 2026-05-19 | 18:00 | Insulator Replacement Activity | No | Rejected | Deferred by requester. | Line Circuits | 15-May-2026 | 11:19 | 16-May-2026 | 11:00
RQ106617 | OCC_237 | WKTL | UPCL - 220KV - BUS 1 | ADANI_APL | D | Bus-1 CVT periodical testing and Bus coupler breaker overhauling | 2026-05-19 | 08:00 | 2026-05-19 | 18:00 | Bus-1 CVT periodical testing and Bus coupler breaker overhauling | No | Rejected | Deferred by requester. | Bus | 15-May-2026 | 11:19 | 16-May-2026 | 11:00
RQ106751 | OCC_237 | KNTL | MAIN BAY (220) OF KOPPAL - 220KV - BUS 3 @KOPPAL - 220KV | TANTRANSCO | D | Yearly Bay equipment testing and preventive maintenance. | 2026-05-18 | 09:00 | 2026-05-18 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 15-May-2026 | 08:40 | 15-May-2026 | 11:05
RQ106381 | OCC_237 | TANTRANSCO | 400KV-RASIPALYAM-ANAIKADAVU-2 | TANTRANSCO | D | Preventive maintenance for bay equipments ( Breaker, CT, Isolator, LAS, Line maintenance and tree clearance) and P&C testing works. | 2026-05-18 | 09:00 | 2026-05-18 | 17:00 |  | Yes | Approved | No N-1 for 400kV ANAIKADAVU, THAPPUKUNDU. CKT-1 100% shall be in service. | Line Circuits | 14-May-2026 | 19:08 | 15-May-2026 | 11:05
RQ106917 | OCC_237 | PGCIL SR-1 | TIE BAY (717) OF RAICHUR_PG - 765KV B/R 2 AND RAICHUR_PG - 765KV - BUS 1 @RAICHUR_PG - 765KV | PGCIL SR-1 | C | For 765KV Raichur-Koppal line construction works | 2026-05-18 | 07:00 | 2026-05-24 | 19:00 | Construction works | Yes | Approved | Subject to NLDC approval and real time grid conditions. | Bay | 14-May-2026 | 18:24 | 15-May-2026 | 11:30
RQ106943 | OCC_237 | PGCIL SR-1 | A/R of 400KV-GOOTY-KURNOOL_PG-1 | POWERGRID | D | Hot line stringing works 400kV D/C Peddapodilla to Bethapalle Line at Existing 400kV S/C Gooty – Kurnool (PG) Line, tower no. 746 & 747 - Auto reclosure to be kept in non auto mode | 2026-05-18 | 09:00 | 2026-05-18 | 18:00 | Construction works | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 14-May-2026 | 17:32 | 15-May-2026 | 11:05
RQ107469 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-KURNOOL_PG-MAHESHWARAM_PG-1 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP146-AP147 | 2026-05-18 | 06:00 | 2026-05-18 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 14-May-2026 | 16:57 | 15-May-2026 | 10:24
RQ107480 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-KURNOOL_PG-MAHESHWARAM_PG-2 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP146-AP147 | 2026-05-18 | 06:00 | 2026-05-18 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 14-May-2026 | 16:57 | 15-May-2026 | 10:24
RQ107491 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-NIZAMABAD-MAHESHWARAM_PG-1 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP147-AP148 | 2026-05-18 | 06:00 | 2026-05-18 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 14-May-2026 | 16:57 | 15-May-2026 | 10:24
RQ107502 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-NIZAMABAD-MAHESHWARAM_PG-2 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP147-AP148 | 2026-05-18 | 06:00 | 2026-05-18 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 14-May-2026 | 16:57 | 15-May-2026 | 10:24
RQ106426 | OCC_237 | TANTRANSCO | 220KV-SULURPET-GUMMIDIPOONDI-1 | APTRANSCO,TANTRANSCO | D | Breaker isolator rectification work and Monthly Maintenance work, CT Clamp, and Bolt Nuts replacement work. | 2026-05-18 | 09:00 | 2026-05-18 | 17:00 |  | Yes | Approved | Load management to be done by both AP & TN. 230KV-NCTPS_S_1-GUMMIDIPOONDI-1 100% 400KV-SUNGAVARACHATRAM-SRIPERUMBADUR-1 44% 400KV-MANALI-NCTPS_STAGE_II-1 40% 400KV-PULIYANTHOPE-MANALI D/C 31% each shall be in service. | Line Circuits | 14-May-2026 | 16:07 | 15-May-2026 | 18:14
RQ108902 | PNOCC | WKTL | KUDGI_PG - 400KV - BUS 2 | PGCIL SR-2 | C | Extension/Interconnection of400kv Main Bus-2 from existing PGCIL Kudgi to WRSR New Narendra. | 2026-05-18 | 09:00 | 2026-05-19 | 18:00 | Outage of 400kV Bus-2 approved from 11.05.26 to 16.05.26, not avail due to on going 400kV Bus 1 outage. Kindly reschedule from 18.05.26 to 23.05.26 | Yes | Rejected | FTC is required. CEA safety approval need to be submitted on D-1. Remaining all elements shall be in service. | Bus | 14-May-2026 | 14:39 | 15-May-2026 | 11:37
RQ108904 | PNOCC | WKTL | TIE BAY (420) OF 400KV-KOPPAL-KUDGI_PG-1 AND 400KV/220KV KUDGI_PG-ICT-3 @KUDGI_PG - 400KV | KNTL | C | Extension/Interconnection of400kv Main Bus-2 from existing PGCIL Kudgi to WRSR New Narendra. | 2026-05-18 | 09:00 | 2026-05-19 | 18:00 | 3- Additionally along with BUS -2 ,we need 2 tie bays also (420 & 423) for protection wiring purpose(There will be no availability loss due to the same & now both are ideally charged as ICTS are not charged). Outage required from 18.05.26 to 23.05.26 | Yes | Rejected | Applied along with Bus-2 Shutdown. Corresponding Main Bay 421 shutdown not applied | Bay | 14-May-2026 | 14:44 | 15-May-2026 | 11:37
RQ108905 | PNOCC | WKTL | TIE BAY (423) OF 400KV-KOPPAL-KUDGI_PG-2 AND 400KV/220KV KUDGI_PG-ICT-4 @KUDGI_PG - 400KV | KTL | C | Extension/Interconnection of400kv Main Bus-2 from existing PGCIL Kudgi to WRSR New Narendra. | 2026-05-18 | 09:00 | 2026-05-19 | 18:00 | 3- Additionally along with BUS -2 ,we need 2 tie bays also (420 & 423) for protection wiring purpose(There will be no availability loss due to the same & now both are ideally charged as ICTS are not charged). Outage required from 18.05.26 to 23.05.26 on continuous basis | Yes | Rejected | Applied along with Bus-2 Shutdown. Corresponding Main Bay 424 shutdown not applied. | Bay | 14-May-2026 | 14:47 | 15-May-2026 | 11:37
RQ106983 | OCC_237 | NLC | 230KV-NEYVELI_TS_II-ULUNDURPET-1 | TANTRANSCO | C | For LA Testing works | 2026-05-18 | 09:00 | 2026-05-18 | 17:00 | All other Feeders will be in service | Yes | Rejected | Load Management, along with network rearrangement and split bus operation details need to be furnished by TN. | Line Circuits | 14-May-2026 | 14:22 | 15-May-2026 | 11:54
RQ106616 | OCC_237 | WKTL | UPCL - 220KV - BUS 1 | ADANI_APL | D | Bus-1 CVT periodical testing and Bus coupler breaker overhauling | 2026-05-18 | 08:00 | 2026-05-18 | 18:00 | Bus-1 CVT periodical testing and Bus coupler breaker overhauling | No | Rejected | Deferred by requester. | Bus | 14-May-2026 | 13:42 | 15-May-2026 | 10:24
RQ106809 | OCC_237 | kptcl | 400KV/220KV GUTTUR-ICT-2 | KPTCL | D | Submitting proposal for 1st Quarter Maintenance | 2026-05-18 | 10:00 | 2026-05-18 | 17:00 |  | No | Approved | Subject to real time grid conditions and 220kV Line loadings and RE generation at downstream. N-1 limit for GUTTUR ICTs is 192 MW each. 400KV/220KV GUTTUR-ICT-1 55% shall be in service along with NARENDRA ICTs and 220kV-GUTTUR-CHITRADURGA and 400kV-GUTTUR-HIRIYUR D/C. Approved as loading is very less on ICTs. | Transformer | 14-May-2026 | 13:05 | 15-May-2026 | 10:24
RQ106818 | OCC_237 | kptcl | MAIN BAY (418) OF 400KV/220KV NELAMANGALA-ICT-1 AND NELAMANGALA - 400KV - BUS 2 @NELAMANGALA - 400KV | KPTCL | D | Breaker testing and maintenance works. | 2026-05-18 | 11:00 | 2026-05-18 | 17:00 |  | No | Rejected | Deferred by requester. | Bay | 14-May-2026 | 12:47 | 15-May-2026 | 10:24
RQ106794 | OCC_237 | NLC | BUS COUPLER BAY (405) OF NTPL - 400KV - BUS 1 AND NTPL - 400KV - BUS 2 @NTPL - 400KV | NTPL | D | GIS Annual Maintenance and Testing | 2026-05-18 | 09:00 | 2026-05-18 | 18:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 14-May-2026 | 12:16 | 15-May-2026 | 11:05
RQ106470 | OCC_237 | WKTL | 765KV-KURNOOL_PG-MAHESHWARAM_PG-1 | POWERGRID | D | Insulator Replacement | 2026-05-18 | 08:00 | 2026-05-18 | 18:00 | Insulator Replacement | No | Rejected | Deferred by requester. | Line Circuits | 14-May-2026 | 11:55 | 15-May-2026 | 10:24
RQ106675 | OCC_237 | aptransco | 400KV-TALARCHEVU-URAVAKONDA-2 | APTRANSCO | D | "1. Maintenance of Jack bus & connected jumpers. *Note: 400KV Talaricheruvu-1 feeder will be in service" | 2026-05-18 | 09:00 | 2026-05-18 | 15:00 | Annual maintenance works | Yes | Approved | 400KV-TALARCHEVU-URAVAKONDA-1 56% 400KV-JAMMALAMADUGU-NARNOOR D/C 18% each 400KV-KURNOOL_PG-NARNOOR D/C 11% each 400KV-MEHBOOBNAGAR-URAVAKONDA D/C 10% each shall be in service. Approved along with Bus shutdown. | Line Circuits | 14-May-2026 | 11:28 | 15-May-2026 | 11:30
RQ106574 | OCC_237 | aptransco | 132KV-KODADA-CHILLAKALLU-1 | APTRANSCO,TGTRANSCO | D | Stringing of snapped Earth wire from Loc. Nos. 8 to 22, 29 to 36 and clearing of vegetation in various locations from 1 to 41 by CBD Gang | 2026-05-18 | 08:00 | 2026-05-18 | 18:00 | Stringing of snapped Earth wire from Loc. Nos. 8 to 22, 29 to 36 and clearing of vegetation in various locations from 1 to 41 by CBD Gang | Yes | Approved | Load management to be done by AP & TG. | Line Circuits | 14-May-2026 | 11:28 | 15-May-2026 | 10:44
RQ106642 | OCC_237 | aptransco | NARNOOR - 400KV B/R 2 | APTRANSCO | D | For Annualy and Quarterly maintenance works(for Reactor Testings) | 2026-05-18 | 10:00 | 2026-05-18 | 16:00 | Annual maintenance works | Yes | Approved | Concurred, subject to real time grid conditions. | Bus Reactor | 14-May-2026 | 11:28 | 15-May-2026 | 10:44
RQ106667 | OCC_237 | aptransco | URAVAKONDA - 400KV - BUS 1 | APTRANSCO | D | "1. Maintenance of Jack bus & connected jumpers. *Note: 400KV Talaricheruvu-1 feeder will be in service" | 2026-05-18 | 09:00 | 2026-05-18 | 15:00 | Annual maintenance works | Yes | Approved | Remaining elements shall be in service. | Bus | 14-May-2026 | 11:28 | 15-May-2026 | 11:05
RQ106954 | OCC_237 | TGTRANSCO | 220KV-RAMAGUNDAM-MALYALAPALLI-1 | NTPC | C | For Isolator Overhauling works and Bay Maintenance works | 2026-05-18 | 09:00 | 2026-05-18 | 19:00 |  | Yes | Approved | 220KV-RAMAGUNDAM-MALYALAPALLI-3 37% 220KV-RAMAGUNDAM-MALYALAPALLI-4 37% 220KV-RAMAGUNDAM-MALYALAPALLI-2 25% shall be in service. | Line Circuits | 14-May-2026 | 10:40 | 15-May-2026 | 11:30
RQ106993 | OCC_237 | TGTRANSCO | 400KV-VTPS_IV-SURYAPET-1 | APTRANSCO,TGTRANSCO | C | General maintenance works and MRT wing testing works | 2026-05-18 | 10:00 | 2026-05-18 | 17:00 |  | Yes | Approved | 400KV-SURYAPET-VTPS_IV-2 50% 400KV-VTPS_IV-VIJAYAWADA-1 22% 400KV-SATTENPALLY-VTPS_IV-1 18% 400KV-JULURUPADU-SURYAPET D/C 13% each shall be in service. | Line Circuits | 14-May-2026 | 10:40 | 15-May-2026 | 11:37
RQ106615 | OCC_237 | WKTL | 220KV-UPCL-KEMAR-2 | KPTCL | D | 220kV Kemar Line-2 shutdown required for NABL accuracy testing of CVT. Not availed in Mar/Apr 2026 since HV testing equipment under breakdown. | 2026-05-16 | 08:00 | 2026-05-16 | 18:00 | 220kV Kemar Line-2 shutdown required for NABL accuracy testing of CVT. Not availed in Mar/Apr 2026 since HV testing equipment under breakdown. | No | Rejected | Requester does not update the availing status as yes on D-3. Multiple shutdowns ongoing at the same station. | Line Circuits | 14-May-2026 | 09:43 | 13-May-2026 | 10:09
RQ108883 | PNOCC | PGCIL SR-2 | A/R of 400KV-NNTPP-PUDUCHERRY-1 | POWERGRID | D | PID scanning of complete Line due to frequent faliure of Poceline Insulator damage | 2026-05-19 | 08:00 | 2026-05-19 | 17:59 | PID scanning of complete Line due to frequent faliure of Porceline Insulator | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 13-May-2026 | 18:57 | 16-May-2026 | 11:08
RQ108885 | PNOCC | PGCIL SR-2 | A/R of 400KV-NNTPP-PUDUCHERRY-1 | POWERGRID | D | PID scanning of complete Line due to frequent faliure of Poceline Insulator damage | 2026-05-21 | 08:00 | 2026-05-21 | 17:59 | PID scanning of complete Line due to frequent faliure of Porceline Insulator | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 13-May-2026 | 18:57 | 18-May-2026 | 10:13
RQ108886 | PNOCC | PGCIL SR-2 | A/R of 400KV-NNTPP-PUDUCHERRY-1 | POWERGRID | D | PID scanning of complete Line due to frequent faliure of Poceline Insulator damage | 2026-05-22 | 08:00 | 2026-05-22 | 17:59 | PID scanning of complete Line due to frequent faliure of Porceline Insulator | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 13-May-2026 | 18:57 | 19-May-2026 | 10:09
RQ108889 | PNOCC | PGCIL SR-2 | A/R of 400KV-NNTPP-PUDUCHERRY-1 | POWERGRID | D | PID scanning of complete Line due to frequent faliure of Poceline Insulator damage | 2026-05-25 | 08:00 | 2026-05-25 | 18:00 | PID scanning of complete Line due to frequent faliure of Porceline Insulator | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 13-May-2026 | 18:57 | 22-May-2026 | 12:42
RQ108890 | PNOCC | PGCIL SR-2 | A/R of 400KV-NNTPP-PUDUCHERRY-1 | POWERGRID | D | PID scanning of complete Line due to frequent faliure of Poceline Insulator damage | 2026-05-26 | 08:00 | 2026-05-26 | 17:59 | PID scanning of complete Line due to frequent faliure of Porceline Insulator | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 13-May-2026 | 18:57 | 23-May-2026 | 16:29
RQ108882 | PNOCC | PGCIL SR-2 | A/R of 400KV-NNTPP-PUDUCHERRY-1 | POWERGRID | D | PID scanning of complete Line due to frequent faliure of Poceline Insulator damage | 2026-05-18 | 08:00 | 2026-05-18 | 17:59 | PID scanning of complete Line due to frequent faliure of Porceline Insulator | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 13-May-2026 | 18:57 | 15-May-2026 | 10:44
RQ108884 | PNOCC | PGCIL SR-2 | A/R of 400KV-NNTPP-PUDUCHERRY-1 | POWERGRID | D | PID scanning of complete Line due to frequent faliure of Poceline Insulator damage | 2026-05-20 | 08:00 | 2026-05-20 | 17:59 | PID scanning of complete Line due to frequent faliure of Porceline Insulator | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 13-May-2026 | 18:57 | 17-May-2026 | 10:29
RQ108881 | PNOCC | PGCIL SR-2 | A/R of 400KV-NNTPP-PUDUCHERRY-1 | POWERGRID | D | PID scanning of complete Line due to frequent faliure of Poceline Insulator damage | 2026-05-17 | 08:00 | 2026-05-17 | 17:59 | PID scanning of complete Line due to frequent faliure of Porceline Insulator | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 13-May-2026 | 18:57 | 14-May-2026 | 10:59
RQ108887 | PNOCC | PGCIL SR-2 | A/R of 400KV-NNTPP-PUDUCHERRY-1 | POWERGRID | D | PID scanning of complete Line due to frequent faliure of Poceline Insulator damage | 2026-05-23 | 08:00 | 2026-05-23 | 17:59 | PID scanning of complete Line due to frequent faliure of Porceline Insulator | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 13-May-2026 | 18:57 | 20-May-2026 | 10:35
RQ108888 | PNOCC | PGCIL SR-2 | A/R of 400KV-NNTPP-PUDUCHERRY-1 | POWERGRID | D | PID scanning of complete Line due to frequent faliure of Poceline Insulator damage | 2026-05-24 | 08:00 | 2026-05-24 | 17:59 | PID scanning of complete Line due to frequent faliure of Porceline Insulator | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 13-May-2026 | 18:57 | 21-May-2026 | 12:48
RQ106377 | OCC_237 | TANTRANSCO | 230KV-HOSUR_PG-UDANAPALLI-2 | TANTRANSCO | D | Preventive maintenance for bay equipments ( Breaker, CT, Isolator, LAS, Line maintenance and tree clearance) and P&C testing works. | 2026-05-17 | 09:00 | 2026-05-17 | 17:00 |  | No | Rejected | Deferred by requester. | Line Circuits | 13-May-2026 | 18:57 | 14-May-2026 | 10:42
RQ106844 | OCC_237 | kptcl | 220KV-KOLAR_AC-CHINTAMANAI-1 | KPTCL | D | To carry out 1st Quarterly maintenance works at 220kV Chintamani & its down stream station including 220kV Srinivasapura | 2026-05-17 | 09:00 | 2026-05-17 | 17:00 | 3rd qtrly maintenance for 2025-26 was carried out on 14.12.2025 | Yes | Rejected | Subject to BESCOM concurrence & Load Management details need to be furnished by KAR. | Line Circuits | 13-May-2026 | 16:58 | 14-May-2026 | 12:10
RQ106845 | OCC_237 | kptcl | 220KV-KOLAR_AC-CHINTAMANAI-2 | KPTCL | D | To carry out 1st Quarterly maintenance works at 220kV Chintamani & its down stream station including 220kV Srinivasapura | 2026-05-17 | 09:00 | 2026-05-17 | 17:00 | 3rd qtrly maintenance for 2025-26 was carried out on 14.12.2025 | Yes | Rejected | Subject to BESCOM concurrence & Load Management details need to be furnished by KAR. | Line Circuits | 13-May-2026 | 16:58 | 14-May-2026 | 12:10
RQ106942 | OCC_237 | PGCIL SR-1 | A/R of 400KV-GOOTY-KURNOOL_PG-1 | POWERGRID | D | Hot line stringing works 400kV D/C Peddapodilla to Bethapalle Line at Existing 400kV S/C Gooty – Kurnool (PG) Line, tower no. 746 & 747 - Auto reclosure to be kept in non auto mode | 2026-05-17 | 09:00 | 2026-05-17 | 18:00 | Construction works | No | Rejected | Deferred by requester. | Auto Reclosure | 13-May-2026 | 15:04 | 14-May-2026 | 10:42
RQ107464 | OCC_2371 | PGCIL SR-1 | 765KV-KURNOOL_PG-RAICHUR_PG-2 | POWERGRID | C | Stringing works from AP4A/0-AP3A/0 of 765kV Koppal-Raichur line | 2026-05-17 | 08:00 | 2026-05-18 | 18:00 | Construction works | No | Rejected | Deferred by requester. | Line Circuits | 13-May-2026 | 15:04 | 14-May-2026 | 10:43
RQ107468 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-KURNOOL_PG-MAHESHWARAM_PG-1 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP146-AP147 | 2026-05-17 | 06:00 | 2026-05-17 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 13-May-2026 | 15:04 | 14-May-2026 | 10:42
RQ107479 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-KURNOOL_PG-MAHESHWARAM_PG-2 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP146-AP147 | 2026-05-17 | 06:00 | 2026-05-17 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 13-May-2026 | 15:04 | 14-May-2026 | 10:42
RQ107490 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-NIZAMABAD-MAHESHWARAM_PG-1 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP147-AP148 | 2026-05-17 | 06:00 | 2026-05-17 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 13-May-2026 | 15:04 | 14-May-2026 | 10:42
RQ107501 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-NIZAMABAD-MAHESHWARAM_PG-2 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP147-AP148 | 2026-05-17 | 06:00 | 2026-05-17 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 13-May-2026 | 15:04 | 14-May-2026 | 10:42
RQ106427 | OCC_237 | TANTRANSCO | MAIN BAY (403) OF SRIPERUMBADUR_TN - 400KV - BUS 2 AND 400KV/230KV SRIPERUMBADUR_TN-ICT-2 @SRIPERUMBADUR_TN - 400KV | TANTRANSCO | D | QUARTERLY MAINTENANCE WORKS | 2026-05-17 | 09:00 | 2026-05-17 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 13-May-2026 | 15:01 | 14-May-2026 | 10:59
RQ106761 | OCC_237 | TGTRANSCO | 400KV/220KV BHOOPALAPALLY-ICT-1 | TGTRANSCO | C | Yearly maintenance. Testing of tandelta, IR of bushings & relays | 2026-05-17 | 09:00 | 2026-05-17 | 18:00 |  | Yes | Approved | Load Management need to be done by TG. N-1 limit for BHOOPALAPALLY ICTs is 300 MW each. 400KV/220KV BHOOPALAPALLY-ICT-2 48% All WARANGAL and RAMAGUNDAM ICTs shall be in service. 220KV-WARANGAL-NAGARAM D/C 15% each 400KV-CHANDALAPUR-BHOOPALAPALLY D/C 8% each 220KV-RAMAGUNDAM-MALYALAPALLI all lines shall be in service. | Transformer | 13-May-2026 | 13:44 | 14-May-2026 | 11:41
RQ106963 | OCC_237 | TGTRANSCO | 400KV/220KV DICHPALLY-ICT-1 | TGTRANSCO | C | complete overhauling and replacement, to arrest oil seepages and ensure the long-term reliability of the equipment. As this activity involves complete oil draining, removal of the bell jar/main inspection doors, dismantling of 400kV, 220kV, and 33kV bushings, and extensive Hot Oil Circulation (HOC) and vacuuming, a continuous shutdown is required. of all gaskets | 2026-05-17 | 07:00 | 2026-05-31 | 16:00 |  | Yes | Approved | Load Management need to be done by TG. N-1 limit for DICHPALLY ICTs is 219 MW for 315 MVA ICT each and 347 MW for 500 MVA ICT. 400KV/220KV DICHPALLY-ICT-4 37% 400KV/220KV DICHPALLY-ICT-2 24% 400KV/220KV DICHPALLY-ICT-3 24% All RAMADUGU ICTs 400KV-NIRMAL-DICHPALLY D/C shall be in service. | Transformer | 13-May-2026 | 13:44 | 14-May-2026 | 11:41
RQ106837 | OCC_237 | kptcl | 400KV-PAVAGADA_PG-TUMKUR-1 | POWERGRID | C | Conductor Release, Existing tower dismantle, New Tower erection, and stringing of the conductor for the work of Shifting/Heightening/Modification by providing 01 No. of 400KV DD+18 type tower (at Tower No517) to the existing 400KV BPS-VN Pura (Bellary pooling station-Vansthanarasapura) line across VJNL canal and dismantling 01 no of DC+0 type Tower no: 517 near Kemapanadodderi village in Tumakuru Dist., in the jurisdiction of Operation Division, Chitradurga under self-execution basis by M/S Executive Engineer, VJNL, Yettinahole projects division-2, Tumakuru - Continuously for 20 days | 2026-05-17 | 08:00 | 2026-05-31 | 18:00 | Tower heightening and shifting work under self execution by M/s VJNL | Yes | Approved | FTC is required. Load Management need to be done by KPTCL in case of other parallel line contingency. in case of other parallel line contingency the remaining line loading may touch up to its thermal rating. 400kV-TUMKUR-PAVAGADA D/C 21% each 400kV-PAVAGADA-DEVANAHALLI D/C 10% each 400kV-CUDDAPAH-TUMKUR D/C 400kV-BIDADI-NELMANGALA D/C 400kV-KUDGI-TUMKUR D/C 400kV-GOOTY-PAVAGADA D/C 400kV-GOOTY-SOMANAHLLI 400kV-GOOTY-NELAMANGALA 400kV-HOODY-DEVANAHALLI D/C shall be in service. A voltage dip of around -2.5 KV is expected at 400kV PAVAGADA S/S. Voltage management need to done by KPTCL in near vicinity stations. Load Management clarification submitted by KPTCL, "During the shutdown of the above said lines the voltage will be managed by bringing available capacitor banks into service and staggering the irrigation loads in the downstream station according to the voltage level." | Line Circuits | 13-May-2026 | 12:59 | 14-May-2026 | 12:04
RQ106838 | OCC_237 | kptcl | 400KV-PAVAGADA_PG-TUMKUR-2 | POWERGRID | C | Conductor Release, Existing tower dismantle, New Tower erection, and stringing of the conductor for the work of Shifting/Heightening/Modification by providing 01 No. of 400KV DD+18 type tower (at Tower No517) to the existing 400KV BPS-VN Pura (Bellary pooling station-Vansthanarasapura) line across VJNL canal and dismantling 01 no of DC+0 type Tower no: 517 near Kemapanadodderi village in Tumakuru Dist., in the jurisdiction of Operation Division, Chitradurga under self-execution basis by M/S Executive Engineer, VJNL, Yettinahole projects division-2, Tumakuru - Continuously for 20 days | 2026-05-17 | 08:00 | 2026-05-31 | 18:00 | Tower heightening and shifting work under self execution by M/s VJNL | Yes | Approved | FTC is required. Load Management need to be done by KPTCL in case of other parallel line contingency. in case of other parallel line contingency the remaining line loading may touch up to its thermal rating. 400kV-TUMKUR-PAVAGADA D/C 21% each 400kV-PAVAGADA-DEVANAHALLI D/C 10% each 400kV-CUDDAPAH-TUMKUR D/C 400kV-BIDADI-NELMANGALA D/C 400kV-KUDGI-TUMKUR D/C 400kV-GOOTY-PAVAGADA D/C 400kV-GOOTY-SOMANAHLLI 400kV-GOOTY-NELAMANGALA 400kV-HOODY-DEVANAHALLI D/C shall be in service. A voltage dip of around -2.5 KV is expected at 400kV PAVAGADA S/S. Voltage management need to done by KPTCL in near vicinity stations. Load Management clarification submitted by KPTCL, "During the shutdown of the above said lines the voltage will be managed by bringing available capacitor banks into service and staggering the irrigation loads in the downstream station according to the voltage level." | Line Circuits | 13-May-2026 | 12:59 | 14-May-2026 | 12:04
RQ106573 | OCC_237 | aptransco | 132KV-KODADA-CHILLAKALLU-1 | APTRANSCO,TGTRANSCO | D | Stringing of snapped Earth wire from Loc. Nos. 8 to 22, 29 to 36 and clearing of vegetation in various locations from 1 to 41 by CBD Gang | 2026-05-17 | 08:00 | 2026-05-17 | 18:00 | Stringing of snapped Earth wire from Loc. Nos. 8 to 22, 29 to 36 and clearing of vegetation in various locations from 1 to 41 by CBD Gang | Yes | Approved | Load management to be done by AP & TG. | Line Circuits | 13-May-2026 | 10:27 | 14-May-2026 | 10:48
RQ106685 | OCC_237 | aptransco | MAIN BAY (418) OF 400KV/220KV THALLAYAPALEM-ICT-2 AND THALLAYAPALEM - 400KV - BUS 2 @THALLAYAPALEM - 400KV | APTRANSCO | D | For releasing of Air from 500MVA ICT2 and charging of LV side | 2026-05-17 | 10:00 | 2026-05-17 | 12:00 | For releasing of Air from 500MVA ICT2 and charging of LV side | Yes | Approved | Concurred, subject to real time grid conditions. Remaining bays shall be in service. 400KV/220KV THALLAYAPALEM-ICT-2 is a future element. | Bay | 13-May-2026 | 10:27 | 14-May-2026 | 10:48
RQ106686 | OCC_237 | aptransco | TIE BAY (417) OF 400KV/220KV THALLAYAPALEM-ICT-2 AND 400KV-VTPS_IV-THALLAYAPALEM-2 @THALLAYAPALEM - 400KV | APTRANSCO | D | For releasing of Air from 500MVA ICT2 and charging of LV side | 2026-05-17 | 10:00 | 2026-05-17 | 12:00 | For releasing of Air from 500MVA ICT2 and charging of LV side | Yes | Approved | Concurred, subject to real time grid conditions. Remaining bays shall be in service. 400KV/220KV THALLAYAPALEM-ICT-2 is a future element. | Bay | 13-May-2026 | 10:27 | 14-May-2026 | 10:48
RQ106792 | OCC_237 | aptransco | 400KV-TALARCHEVU-JAMMALAMADUGU-2 | APTRANSCO | D | In order to carry out the rectification of spacer keeper pieces between Loc.Nos. 37 to 38. | 2026-05-17 | 08:00 | 2026-05-17 | 16:00 | In order to carry out the rectification of spacer keeper pieces between Loc.Nos. 37 to 38. | Yes | Approved | 400KV-TALARCHEVU-JAMMALAMADUGU-1 84% 400KV-JAMMALAMADUGU-NARNOOR D/C 7% each 400KV-KURNOOL_PG-NARNOOR D/C 4% each shall be in service. | Line Circuits | 13-May-2026 | 10:27 | 14-May-2026 | 11:30
RQ106748 | OCC_237 | KNTL | TRANSFER BUS COUPLER BAY (219) OF KOPPAL - 220KV - BUS 3 AND KOPPAL - 220KV - BUS 4 @KOPPAL - 220KV | TANTRANSCO | D | Yearly Bay equipment testing and preventive maintenance. | 2026-05-16 | 09:00 | 2026-05-16 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 13-May-2026 | 09:30 | 13-May-2026 | 10:12
RQ106776 | OCC_237 | MTL | A/R of 400KV-NIZAMABAD-SHANKARAPALLY-2 | MTL | D | Required A/R in Non auto mode for defect rectification work | 2026-05-16 | 09:00 | 2026-05-16 | 17:00 | A/R OFF | No | Rejected | Deferred by requester. | Auto Reclosure | 13-May-2026 | 09:20 | 13-May-2026 | 10:09
RQ107078 | OCC_237 | PGCIL SR-2 | 400KV/220KV TRIVANDRUM-ICT-1 | PGCIL SR-2 | D | AMP works of ICT-1 | 2026-05-16 | 09:00 | 2026-05-16 | 15:00 |  | Yes | Rejected | Multiple internal shutdowns of KSEB up to 22nd May in the near vicinity. SR-2 may apply after KSEB related work completion via PNOCC. | Transformer | 12-May-2026 | 18:13 | 13-May-2026 | 10:24
RQ107053 | OCC_237 | PGCIL SR-2 | A/R of 400KV-KALVENDAPATTU-VALLUR-1 | POWERGRID | D | Attending shutdown nature defects in a D/C Tower during Line-2 shutdown. | 2026-05-16 | 08:00 | 2026-05-16 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 18:13 | 13-May-2026 | 10:29
RQ107045 | OCC_237 | PGCIL SR-2 | 400KV-KALVENDAPATTU-VALLUR-2 | POWERGRID | D | AMP Works and attending shutdown nature defects in the line. | 2026-05-16 | 08:00 | 2026-05-16 | 18:00 |  | Yes | Approved | Load and Generation Management need to be done by TN. 400KV-VALLUR-KALVENDAPATTU-1 35% 400KV-NCTPS_STAGE_II-VALLUR D/C 18% each 400KV-VALLUR-ALAMATHY D/C 15% each 400KV-THIRUVALAM-KALVENDAPATTU D/C 14% each 400KV-NCTPS_STAGE_II-ALAMATHY-1 12% shall be in service. | Line Circuits | 12-May-2026 | 18:13 | 14-May-2026 | 10:07
RQ107077 | OCC_237 | PGCIL SR-2 | 400KV/230KV ARASUR_PG-ICT-4 | PGCIL SR-2,POWERGRID | D | AMP works of ICT-4 | 2026-05-16 | 09:00 | 2026-05-16 | 13:00 |  | No | Rejected | Deferred by requester. | Transformer | 12-May-2026 | 18:13 | 13-May-2026 | 10:09
RQ107532 | OCC_2371 | PGCIL SR-2 | 220KV-RENEW_SURYA_OJAS_KOPPAL_W-KOPPAL-1 | RSOPL | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 13/0 - 14/0 | 2026-05-16 | 08:00 | 2026-05-16 | 19:00 | 220KV-RENEW_SURYA_OJAS_KOPPAL_W-KOPPAL-1 and 220KV-KOPPAL-RENEW_SURYA_KOPPAL-1 are on same D/C Tower. Therefore, D/C Outage is required to carry out powerline crossing works. Concurrence from concerned IPPs will be submitted on D-4 basis. | No | Rejected | Deferred by requester. | Line Circuits | 12-May-2026 | 18:13 | 13-May-2026 | 10:09
RQ107534 | OCC_2371 | PGCIL SR-2 | 220KV-KOPPAL-RENEW_SURYA_KOPPAL-1 | RENEW POWER PVT LTD | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 13/0 - 14/0 | 2026-05-16 | 08:00 | 2026-05-16 | 19:00 | 220KV-RENEW_SURYA_OJAS_KOPPAL_W-KOPPAL-1 and 220KV-KOPPAL-RENEW_SURYA_KOPPAL-1 are on same D/C Tower. Therefore, D/C Outage is required to carry out powerline crossing works. Concurrence from concerned IPPs will be submitted on D-4 basis. | No | Rejected | Deferred by requester. | Line Circuits | 12-May-2026 | 18:13 | 13-May-2026 | 10:09
RQ106925 | OCC_237 | PGCIL SR-1 | RAICHUR_PG - 765KV - BUS 1 | PGCIL SR-1 | C | For 765KV Raichur-Koppal line construction works | 2026-05-16 | 07:00 | 2026-05-17 | 19:00 | Construction works | No | Rejected | Deferred by requester. | Bus | 12-May-2026 | 17:47 | 13-May-2026 | 10:09
RQ107467 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-KURNOOL_PG-MAHESHWARAM_PG-1 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP146-AP147 | 2026-05-16 | 06:00 | 2026-05-16 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 12-May-2026 | 17:47 | 13-May-2026 | 10:09
RQ107478 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-KURNOOL_PG-MAHESHWARAM_PG-2 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP146-AP147 | 2026-05-16 | 06:00 | 2026-05-16 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 12-May-2026 | 17:47 | 13-May-2026 | 10:09
RQ107489 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-NIZAMABAD-MAHESHWARAM_PG-1 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP147-AP148 | 2026-05-16 | 06:00 | 2026-05-16 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 12-May-2026 | 17:47 | 13-May-2026 | 10:09
RQ107500 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-NIZAMABAD-MAHESHWARAM_PG-2 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP147-AP148 | 2026-05-16 | 06:00 | 2026-05-16 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 12-May-2026 | 17:47 | 13-May-2026 | 10:09
RQ106394 | OCC_237 | TANTRANSCO | 400KV/230KV RASIPALYAM-ICT-5 | TANTRANSCO | D | Preventive maintenance for bay equipments, Transformer maintenance and P&C testing work. | 2026-05-16 | 09:00 | 2026-05-16 | 17:00 |  | Yes | Approved | Load Management need to be done by TN. | Transformer | 12-May-2026 | 16:05 | 13-May-2026 | 10:12
RQ106987 | OCC_237 | TGTRANSCO | 400KV/220KV NIRMAL-ICT-3 | TGTRANSCO | C | For periodical MRT and TRE testing of ICTs and maintenance works | 2026-05-16 | 07:00 | 2026-05-16 | 20:00 |  | Yes | Approved | Load Management need to be done by TG. N-1 limit for NIRMAL ICTs is 223 MW each. 400KV/220KV NIRMAL-ICT-1 38% 400KV/220KV NIRMAL-ICT-2 38% All RAMAGUNDAM and RAMADUGU ICTs shall be in service. | Transformer | 12-May-2026 | 13:38 | 13-May-2026 | 10:17
RQ106979 | OCC_237 | TGTRANSCO | 400KV/220KV JANAGAON-ICT-3 | TGTRANSCO | C | Yearly MAINTENANCE & Testing OF ICT,Relays & BAY equipment. | 2026-05-16 | 08:00 | 2026-05-16 | 18:00 |  | Yes | Approved | Load Management need to be done by TG. N-1 limit for 400KV/220KV JANAGAON-ICTs is 364 MW each. 400KV/220KV JANAGAON-ICT-1 28% 400KV/220KV JANAGAON-ICT-2 28% All KHAMMAM and MALKARAM ICTs 400KV-TIPPAPUR-CHANDALAPUR D/C shall be in service. | Transformer | 12-May-2026 | 13:38 | 14-May-2026 | 09:59
RQ107012 | OCC_237 | TGTRANSCO | 400KV/220KV MEHBOOBNAGAR-ICT-1 | TGTRANSCO | C | For carrying out periodical equipment Maintenance and Testing works by O&m , MRT and TRE wings | 2026-05-16 | 09:00 | 2026-05-16 | 17:00 |  | Yes | Rejected | Multiple shutdowns at the same station. | Transformer | 12-May-2026 | 13:38 | 14-May-2026 | 09:59
RQ106530 | OCC_237 | kseb | A/R of 220KV-ELAPULLY-MADAKATHARA-1 | KSEB | D | For the work associated with replacement of porcelain disc insulator with polymer insulator on 2MDSH/2MDEN feeder | 2026-05-16 | 08:00 | 2026-05-16 | 17:00 | For the work associated with replacement of porcelain disc insulator with polymer insulator on 2MDSH/2MDEN feeder | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 13:08 | 13-May-2026 | 10:12
RQ106572 | OCC_237 | aptransco | 132KV-KODADA-CHILLAKALLU-1 | APTRANSCO,TGTRANSCO | D | Stringing of snapped Earth wire from Loc. Nos. 8 to 22, 29 to 36 and clearing of vegetation in various locations from 1 to 41 by CBD Gang | 2026-05-16 | 08:00 | 2026-05-16 | 18:00 | Stringing of snapped Earth wire from Loc. Nos. 8 to 22, 29 to 36 and clearing of vegetation in various locations from 1 to 41 by CBD Gang | Yes | Approved | Load management to be done by AP & TG | Line Circuits | 12-May-2026 | 13:07 | 13-May-2026 | 10:17
RQ106823 | OCC_237 | kptcl | MAIN BAY (421) OF 400KV/220KV NELAMANGALA-ICT-3 AND NELAMANGALA - 400KV - BUS 2 @NELAMANGALA - 400KV | KPTCL | D | Breaker testing and maintenance works. | 2026-05-16 | 11:00 | 2026-05-16 | 17:00 |  | No | Rejected | Deferred by requester. | Bay | 12-May-2026 | 12:59 | 13-May-2026 | 10:09
RQ106788 | OCC_237 | NLC | 400KV-NTPL-TUTICORIN_PS-2 | POWERGRID | D | RTV Silicone Coating Work | 2026-05-16 | 09:00 | 2026-05-16 | 18:00 |  | Yes | Rejected | No N-1 for NTPL, Subject to at least one unit outage. Both units are in service as of now. | Line Circuits | 12-May-2026 | 10:55 | 13-May-2026 | 10:17
RQ106428 | OCC_237 | TANTRANSCO | MAIN BAY (406) OF SRIPERUMBADUR_TN - 400KV - BUS 1 AND 400KV/110KV SRIPERUMBADUR_TN-ICT-4 @SRIPERUMBADUR_TN - 400KV | TANTRANSCO | D | Quarterly Maintenance Works. | 2026-05-14 | 09:00 | 2026-05-14 | 17:00 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Bay | 12-May-2026 | 09:28 | 11-May-2026 | 10:33
RQ106747 | OCC_237 | KNTL | BUS COUPLER BAY (218) OF KOPPAL - 220KV - BUS 3 AND KOPPAL - 220KV - BUS 4 @KOPPAL - 220KV | TANTRANSCO | D | Yearly Bay equipment testing and preventive maintenance. | 2026-05-15 | 09:00 | 2026-05-15 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 12-May-2026 | 08:48 | 12-May-2026 | 15:24
RQ106775 | OCC_237 | MTL | A/R of 400KV-NIZAMABAD-SHANKARAPALLY-2 | MTL | D | Required A/R in Non auto mode for defect rectification work | 2026-05-15 | 09:00 | 2026-05-15 | 17:00 | A/R OFF | No | Rejected | Deferred by requester. | Auto Reclosure | 12-May-2026 | 08:36 | 12-May-2026 | 10:15
RQ108802 | PNOCC | aptransco | 400KV-SIMHADRI-KALPAKKA-2 | APTRANSCO | C | For replacement of old LA's with New LA's | 2026-05-15 | 10:00 | 2026-05-15 | 16:00 | Under RMI scheme | Yes | Rejected | Multiple shutdowns at the same station. Planned Activities to be taken into Main OCC. | Line Circuits | 11-May-2026 | 18:53 | 12-May-2026 | 15:31
RQ108803 | PNOCC | aptransco | 400KV-GUDIWADA-SATTENPALLY-2 | APTRANSCO | C | For adjusting the compressor switch to make to operate for high pressure value & for replacement of new PD timer relay | 2026-05-15 | 10:00 | 2026-05-15 | 18:00 | due to AR mal operation | Yes | Rejected | Multiple shutdowns at the same station. Planned Activities to be taken into Main OCC. | Line Circuits | 11-May-2026 | 19:00 | 12-May-2026 | 15:31
RQ106560 | OCC_237 | TANTRANSCO | 400KV-KARAIKUDI-KAYATHAR-2 L/R@ KAYATHAR - 400KV | TANTRANSCO | D | Monthly Maintenance Work | 2026-05-15 | 09:00 | 2026-05-15 | 17:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Line Reactor | 11-May-2026 | 22:44 | 12-May-2026 | 15:31
RQ106787 | OCC_237 | NLC | 400KV-NTPL-TUTICORIN_PS-2 | POWERGRID | D | RTV Silicone Coating Work | 2026-05-15 | 09:00 | 2026-05-15 | 18:00 |  | Yes | Rejected | No N-1 for NTPL, Subject to at least one unit outage. Both units are in service as of now. | Line Circuits | 11-May-2026 | 17:59 | 12-May-2026 | 15:13
RQ107466 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-KURNOOL_PG-MAHESHWARAM_PG-1 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP146-AP147 | 2026-05-15 | 06:00 | 2026-05-15 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 11-May-2026 | 16:55 | 12-May-2026 | 10:15
RQ107477 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-KURNOOL_PG-MAHESHWARAM_PG-2 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP146-AP147 | 2026-05-15 | 06:00 | 2026-05-15 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 11-May-2026 | 16:55 | 12-May-2026 | 10:15
RQ107488 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-NIZAMABAD-MAHESHWARAM_PG-1 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP147-AP148 | 2026-05-15 | 06:00 | 2026-05-15 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 11-May-2026 | 16:55 | 12-May-2026 | 10:15
RQ107499 | OCC_2371 | PGCIL SR-1 | A/R of 765KV-NIZAMABAD-MAHESHWARAM_PG-2 | POWERGRID | D | Live line crossing of 765kV Bidar-Maheshwaram D/C line at Location : AP147-AP148 | 2026-05-15 | 06:00 | 2026-05-15 | 18:00 | Construction works- Existing line over crossing. | No | Rejected | Deferred by requester. | Auto Reclosure | 11-May-2026 | 16:55 | 12-May-2026 | 10:15
RQ106941 | OCC_237 | PGCIL SR-1 | A/R of 400KV-GOOTY-KURNOOL_PG-1 | POWERGRID | D | Hot line stringing works 400kV D/C Peddapodilla to Bethapalle Line at Existing 400kV S/C Gooty – Kurnool (PG) Line, tower no. 754 & 755 - Auto reclosure to be kept in non auto mode | 2026-05-15 | 09:00 | 2026-05-15 | 18:00 | Construction works | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 11-May-2026 | 16:24 | 12-May-2026 | 15:24
RQ106913 | OCC_237 | PGCIL SR-1 | 400KV/220KV MEHBOOBNAGAR-ICT-2 | TGTRANSCO | D | Bay upgradation works uder ADDCAP- Construction works under SS-126 Package | 2026-05-15 | 18:00 | 2026-05-15 | 23:30 | Construction works under ADD-CAP. | No | Rejected | Deferred by requester. | Transformer | 11-May-2026 | 16:24 | 12-May-2026 | 10:15
RQ107531 | OCC_2371 | PGCIL SR-2 | 220KV-RENEW_SURYA_OJAS_KOPPAL_W-KOPPAL-1 | RSOPL | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 13/0 - 14/0 | 2026-05-15 | 08:00 | 2026-05-15 | 19:00 | 220KV-RENEW_SURYA_OJAS_KOPPAL_W-KOPPAL-1 and 220KV-KOPPAL-RENEW_SURYA_KOPPAL-1 are on same D/C Tower. Therefore, D/C Outage is required to carry out powerline crossing works. Concurrence from concerned IPPs will be submitted on D-4 basis. | Yes | Rejected | Concurrence from RE developer not received. | Line Circuits | 11-May-2026 | 14:38 | 12-May-2026 | 16:41
RQ107533 | OCC_2371 | PGCIL SR-2 | 220KV-KOPPAL-RENEW_SURYA_KOPPAL-1 | RENEW POWER PVT LTD | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 13/0 - 14/0 | 2026-05-15 | 08:00 | 2026-05-15 | 19:00 | 220KV-RENEW_SURYA_OJAS_KOPPAL_W-KOPPAL-1 and 220KV-KOPPAL-RENEW_SURYA_KOPPAL-1 are on same D/C Tower. Therefore, D/C Outage is required to carry out powerline crossing works. Concurrence from concerned IPPs will be submitted on D-4 basis. | Yes | Rejected | Concurrence from RE developer not received. | Line Circuits | 11-May-2026 | 14:38 | 12-May-2026 | 16:41
RQ107047 | OCC_237 | PGCIL SR-2 | 400KV-TUMKUR-KUDGI_PG-2 | KTL | C | Powerline crossing of 400 KV Gadag_2 - Koppal_2 line 1 & 2 at Loc. DW01-DW02 | 2026-05-15 | 09:00 | 2026-05-16 | 18:00 |  | No | Rejected | Deferred by requester. | Line Circuits | 11-May-2026 | 14:38 | 12-May-2026 | 10:17
RQ107046 | OCC_237 | PGCIL SR-2 | 400KV-TUMKUR-KUDGI_PG-1 | KTL | C | Powerline crossing of 400 KV Gadag_2 - Koppal_2 line 1 & 2 at Loc. DW01-DW02 | 2026-05-15 | 09:00 | 2026-05-16 | 18:00 |  | No | Rejected | Deferred by requester. | Line Circuits | 11-May-2026 | 14:38 | 12-May-2026 | 10:15
RQ107044 | OCC_237 | PGCIL SR-2 | 400KV-KARAMADAI-ARASUR_PG-2 | TANTRANSCO | D | AMP of Terminal Equipments | 2026-05-15 | 09:00 | 2026-05-15 | 17:00 |  | Yes | Approved | 400KV-KARAMADAI-ARASUR_PG-1 65% 230KV-KARUVALUR-ARASUR_PG-1 6% 230KV-KARUVALUR-KARAMADAI-1 6% 400kV-KARAMADAI-MTPS D/C 400KV-PALAVADI-THIRUVALAM_TN D/C 4% each All ARASUR_PG ICTs shall be in service. | Line Circuits | 11-May-2026 | 14:23 | 12-May-2026 | 16:46
RQ107042 | OCC_237 | PGCIL SR-2 | 400KV-KALVENDAPATTU-VALLUR-1 | POWERGRID | D | AMP Works and attending shutdown nature defects in the line. | 2026-05-15 | 08:00 | 2026-05-15 | 18:00 |  | No | Rejected | Deferred by requester. | Line Circuits | 11-May-2026 | 14:23 | 12-May-2026 | 10:15
RQ107052 | OCC_237 | PGCIL SR-2 | A/R of 400KV-KALVENDAPATTU-VALLUR-2 | POWERGRID | D | Attending shutdown nature defects in a D/C Tower during Line-1 shutdown. | 2026-05-15 | 08:00 | 2026-05-15 | 18:00 |  | No | Rejected | Deferred by requester. | Auto Reclosure | 11-May-2026 | 14:23 | 12-May-2026 | 10:15
RQ106971 | OCC_237 | TGTRANSCO | 400KV-GAJWEL-CHANDALAPUR-1 | TGTRANSCO | C | For ct tan delta and relay testing by mrt wing and general maintenance works | 2026-05-15 | 08:00 | 2026-05-15 | 16:00 |  | Yes | Approved | 400KV-CHANDALAPUR-GAJWEL-2 30% 400KV-TUKKAPUR-CHANDALAPUR D/C 13% each 400KV-TUKKAPUR-NARSAPUR D/C 13% each 400KV-RAMADUGU-GAJWEL D/C 9% each shall be in service. | Line Circuits | 11-May-2026 | 13:51 | 12-May-2026 | 15:31
RQ106986 | OCC_237 | TGTRANSCO | 400KV/220KV NIRMAL-ICT-2 | TGTRANSCO | C | For periodical MRT and TRE testing of ICTs and maintenance works | 2026-05-15 | 07:00 | 2026-05-15 | 20:00 |  | Yes | Approved | Load Management need to be done by TG. N-1 limit for NIRMAL ICTs is 223 MW each. 400KV/220KV NIRMAL-ICT-1 38% 400KV/220KV NIRMAL-ICT-3 38% All RAMAGUNDAM and RAMADUGU ICTs shall be in service. | Transformer | 11-May-2026 | 13:51 | 12-May-2026 | 10:20
RQ106817 | OCC_237 | kptcl | MAIN BAY (415) OF 400KV-NELAMANGALA-DEVANAHALLI-1 AND NELAMANGALA - 400KV - BUS 2 @NELAMANGALA - 400KV | KPTCL | D | Breaker testing and maintenance works. | 2026-05-15 | 11:00 | 2026-05-15 | 17:00 |  | No | Rejected | Deferred by requester. | Bay | 11-May-2026 | 12:49 | 12-May-2026 | 10:15
RQ106497 | OCC_237 | kseb | A/R of 220KV-KOCHI-KALAMASSERY-2 | KSEB | D | Disc replacement work | 2026-05-15 | 09:00 | 2026-05-15 | 17:00 | Disc replacement work | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 11-May-2026 | 10:35 | 12-May-2026 | 15:24
RQ106643 | OCC_237 | kseb | 220KV-POTHENCODE-TRIVANDRUM-3 | KSEB | D | For ensuring safety in connection with rearrangement work of 2TVPC#4 feeder. | 2026-05-15 | 08:00 | 2026-05-15 | 17:00 | Re-arrangement of 2EMPC, 2PCNK and 2TVPC #4 feeders at 220kV Substation Pothencode to extend 220kV PGCIL supply directly to 220kV Substation New Kattakada. During the work on the 2TVPC #3 feeder on 15.05.2026 (from 15.05.2026, 08:00Hrs – 17:00Hrs), the following 220 kV feeders, 2EMPC#2, 2PCNK #2 & 2TVPC#4 will be under shutdown. | Yes | Approved | 220KV-POTHENCODE-TRIVANDRUM-1,2 50% each shall be in service. Load Management to be done by KSEB. As per information received from KSEB, 220kV-EDAMON-POTHENCODE one circuit and 220kV-POTHENCODE - NEW KATAKADA one circuit (Internal feeders of KSEB) will also be availed along with 220KV-POTHENCODE-TRIVANDRUM-4,3. 220KV-POTHENCODE-TRIVANDRUM-3 will be availed only for one day. No N-1 for radial loads of 220kV NEW KATAKADA. In case of contingency of 220KV-POTHENCODE-TRIVANDRUM other parallel circuit will lead to overload of 220KV-POTHENCODE-TRIVANDRUM S/C and may lead to cascade tripping of the same and 220kV-EDAPON-POTHENCODE S/C. Accordingly load management need to be done by KSEB. | Line Circuits | 11-May-2026 | 10:35 | 12-May-2026 | 17:19
RQ106674 | OCC_237 | kseb | 220KV-POTHENCODE-TRIVANDRUM-4 | KSEB | C | Re-arrangement of 2EMPC, 2PCNK and 2TVPC #4 feeders at 220kV Substation Pothencode to extend 220kV PGCIL supply directly to 220kV Substation New Kattakada | 2026-05-15 | 08:00 | 2026-05-22 | 17:00 | During the work on the 2TVPC #4 feeder (from 15.05.2026 to 22.05.2026), the following 220kV feeders, 2EMPC#2, 2PCNK #2 & 2TVPC#3 (only on 15.05.2026, 08:00Hrs – 17:00Hrs) will be under shutdown. | Yes | Approved | FTC is required for the proposed network rearrangement from TRIVANDRUM-POTHENCODE-NEW KATAKADA. 220KV-POTHENCODE-TRIVANDRUM-1,2 50% each shall be in service. Load Management to be done by KSEB. As per information received from KSEB, 220kV-EDAMON-POTHENCODE one circuit and 220kV-POTHENCODE - NEW KATAKADA one circuit (Internal feeders of KSEB) will also be availed along with 220KV-POTHENCODE-TRIVANDRUM-4,3. 220KV-POTHENCODE-TRIVANDRUM-3 will be availed only for one day. No N-1 for radial loads of 220kV NEW KATAKADA. In case of contingency of 220KV-POTHENCODE-TRIVANDRUM other parallel circuit will lead to overload of 220KV-POTHENCODE-TRIVANDRUM S/C and may lead to cascade tripping of the same and 220kV-EDAPON-POTHENCODE S/C. Accordingly load management need to be done by KSEB. | Line Circuits | 11-May-2026 | 10:35 | 12-May-2026 | 17:19
RQ106663 | OCC_237 | aptransco | 400KV/220KV GHANI-ICT-1 | APTRANSCO | D | For Relay& Equipment testing works | 2026-05-15 | 17:00 | 2026-05-15 | 22:00 | Annual maintenance works | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. 400KV/220KV GHANI-ICT-2 50% 400KV/220KV GHANI-ICT-3 50% shall be in service. N-1 limit for GHANI ICTs is 316 MW each. | Transformer | 11-May-2026 | 10:06 | 12-May-2026 | 15:13
RQ106683 | OCC_237 | aptransco | MAIN BAY (418) OF 400KV/220KV THALLAYAPALEM-ICT-2 AND THALLAYAPALEM - 400KV - BUS 2 @THALLAYAPALEM - 400KV | APTRANSCO | D | For connecting jumpers to HV side of ICT-2 | 2026-05-15 | 10:00 | 2026-05-15 | 17:00 | For connecting jumpers to HV side of ICT-2 | Yes | Approved | Concurred, subject to real time grid conditions. THALLAYAPALEM-ICT-2 is a future element. | Bay | 11-May-2026 | 10:06 | 12-May-2026 | 15:17
RQ106684 | OCC_237 | aptransco | TIE BAY (417) OF 400KV/220KV THALLAYAPALEM-ICT-2 AND 400KV-VTPS_IV-THALLAYAPALEM-2 @THALLAYAPALEM - 400KV | APTRANSCO | D | For connecting jumpers to HV side of ICT-2 | 2026-05-15 | 10:00 | 2026-05-15 | 17:00 | For connecting jumpers to HV side of ICT-2 | Yes | Approved | Concurred, subject to real time grid conditions. THALLAYAPALEM-ICT-2 is a future element. | Bay | 11-May-2026 | 10:06 | 12-May-2026 | 15:17
RQ106666 | OCC_237 | aptransco | URAVAKONDA - 400KV - BUS 1 | APTRANSCO | D | "1. Maintenance of Jack bus & connected jumpers. *Note: 400KV Talaricheruvu-2 feeder will be in service" | 2026-05-15 | 09:00 | 2026-05-15 | 15:00 | Annual maintenance works | Yes | Approved | Concurred, subject to real time grid conditions. | Bus | 11-May-2026 | 10:04 | 12-May-2026 | 15:24
RQ106673 | OCC_237 | aptransco | 400KV-TALARCHEVU-URAVAKONDA-1 | APTRANSCO | D | "1. Maintenance of Jack bus & connected jumpers. *Note: 400KV Talaricheruvu-2 feeder will be in service" | 2026-05-15 | 09:00 | 2026-05-15 | 15:00 | Annual maintenance works | Yes | Approved | 400KV-TALARCHEVU-URAVAKONDA-2 56% 400KV-JAMMALAMADUGU-NARNOOR D/C 18% each 400KV-KURNOOL_PG-NARNOOR D/C 11% each 400KV-MEHBOOBNAGAR-URAVAKONDA D/C 10% each 400KV-HINDUPUR-NP_KUNTA-1 6% shall be in service. | Line Circuits | 11-May-2026 | 10:04 | 12-May-2026 | 15:24
RQ106777 | OCC_237 | aptransco | 400KV-NARNOOR-JAMMALAMADUGU-1 | APTRANSCO | D | For PMI defects rectification from loc.No.236-239. | 2026-05-15 | 08:00 | 2026-05-15 | 14:00 | Annual maintenance works | Yes | Rejected | Multiple shutdowns at the same station. | Line Circuits | 11-May-2026 | 10:04 | 12-May-2026 | 15:24
RQ106548 | OCC_237 | aptransco | 400KV-KRISHNAPATNAM-RACHAGUNNERI-2 | APTRANSCO | D | Tightening of spacer dampers and providing of missing keepers to dampers between locno:88 to 91 , arranging repair sleeves to conductor damages between loc. No:88- 89 Top phase in 400KV Krishnapatnam-Rachagunneri-2 feeder. | 2026-05-15 | 07:00 | 2026-05-15 | 17:00 | During the LC period there will be no interruption to loads as 400KV Krishnapatnam TPP - Manubolu feeder, 400KV SEIL – Manubolu feeder, 400KV Krishnapatnam-SEIL feeder and 400KV Krishnapatnam TPP – Rachagunneri - 1 feeders will be in Service | Yes | Approved | 400KV-RACHAGUNNERI-KRISHNAPATNAM-1 44% 400KV-KRISHNAPATNAM-NELLORE_AP-1 30% 400KV-SEILU2_AP-NELLORE_AP-1 26% 400KV-NELLORE_AP-NELLORE_PG-1 21% 400KV-TVLM-CHITTOOR D/C 11% each 400KV-SRIPERUMBADUR-NELLORE_PG-1 10% All NELLORE_AP ICTs shall be in service. | Line Circuits | 11-May-2026 | 10:04 | 12-May-2026 | 16:46
RQ106645 | OCC_237 | aptransco | 400KV/220KV SATTENPALLY-ICT-1 | APTRANSCO | D | For maintenance and MRT works | 2026-05-15 | 09:00 | 2026-05-15 | 17:00 | Annual maintenance works | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. Load Management need to be done by AP. N-1 limit for SATTENPALLY ICTs is 207 MW for 315 MVA ICT each and 330 MW for 500 MVA ICT. 400KV/220KV SATTENPALLY-ICT-2 29% 400KV/220KV SATTENPALLY-ICT-3 29% All PODILI and NELLORE AP ICTs shall be in service. | Transformer | 11-May-2026 | 10:04 | 12-May-2026 | 15:41
RQ107024 | OCC_237 | aptransco | 400KV-SRISAILAM_LEFT_BANK-SATTENPALLY-1 | APTRANSCO,TGTRANSCO | C | LC required from 15th to 29th . Providing/Fixing of Vibration dampers for all Suspension towers from Loc. Nos.141-397 in 400KV Srisailam – Sattenapalli Ckt-1 feederby the contract agency and Rectification of major PMI defects at various locations by the department with existing CBD gang. | 2026-05-16 | 22:00 | 2026-05-29 | 18:00 | Providing/Fixing of Vibration dampers for all Suspension towers from Loc. Nos.141-397 in 400KV Srisailam – Sattenapalli Ckt-1 feederby the contract agency and Rectification of major PMI defects at various locations by the department with existing CBD gang. | Yes | Approved | 400KV-SRISAILAM_LEFT_BANK-SATTENPALLY-2 28% 400KV-SATTENPALLY-VTPS_IV-1 15% 400KV-CHILAKALURIPETA-SATTENPALLY D/C 14% each shall be in service along with All C'PETA ICTs. Concurrence from TG received regarding no generation and pump operation at SRISAILAM_LEFT_BANK through mail communication dated 16.05.2026 | Line Circuits | 11-May-2026 | 10:04 | 12-May-2026 | 15:31
RQ107516 | OCC_2371 | aptransco | 132KV-PRATHAP_NAGAR-YANAM-1 | PONDICHERRY,APTRANSCO | D | For erection of 220kV Z-Type Tower underneath the crossing of 132kV KKD-Gollapalem circuit, Pratapnagar-Yanam circuit and 220kV SSS Barge idle line duly the diverting the existing Pratapnagar-Yanam line. | 2026-05-15 | 08:00 | 2026-05-15 | 14:00 | "Formation of 2nd circuit from 220kV SS Kakinada to 132kV Pratapnagar SS" by utilizing the idle 220kV Samalkota - GMR Barge DC line at 132kV Potential, 132kV Kakinada - Ramachandrapuram DC line, 132kV PratapnagarYanam single circuit and 132kV Kakinada-Gollaplem single circuit. The work was awarded to M/s. Radhakrishna Contractors, Rajahmundry vide reference 2nd cited. The work is under progress. | Yes | Rejected | Load management to be done by AP & PED. FTC is required. Need to furnish the details of works and schemes properly prior to the shutdown. SRPC approval is required for the temporary network rearrangement submitted by AP. | Line Circuits | 11-May-2026 | 10:04 | 12-May-2026 | 15:31
RQ106571 | OCC_237 | aptransco | 132KV-KODADA-CHILLAKALLU-1 | APTRANSCO,TGTRANSCO | D | Stringing of snapped Earth wire from Loc. Nos. 8 to 22, 29 to 36 and clearing of vegetation in various locations from 1 to 41 by CBD Gang | 2026-05-15 | 08:00 | 2026-05-15 | 18:00 | Stringing of snapped Earth wire from Loc. Nos. 8 to 22, 29 to 36 and clearing of vegetation in various locations from 1 to 41 by CBD Gang | Yes | Approved | Load management to be done by AP & TG | Line Circuits | 11-May-2026 | 10:04 | 12-May-2026 | 10:20
RQ106821 | OCC_237 | kptcl | TIE BAY (414) OF 400KV-NELAMANGALA-HIRIYUR-2 AND 400KV-NELAMANGALA-DEVANAHALLI-1 @NELAMANGALA - 400KV | KPTCL | D | Breaker testing and maintenance works. | 2026-05-13 | 11:00 | 2026-05-13 | 17:00 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Bay | 11-May-2026 | 09:34 | 10-May-2026 | 11:11
RQ106786 | OCC_237 | NLC | 400KV-NTPL-TUTICORIN_PS-1 | POWERGRID | D | RTV Silicone Coating Work | 2026-05-14 | 09:00 | 2026-05-14 | 18:00 |  | Yes | Rejected | No N-1 for NTPL, Subject to at least one unit outage. Both units are in service as of now. | Line Circuits | 11-May-2026 | 09:16 | 11-May-2026 | 11:12
RQ106436 | OCC_237 | TANTRANSCO | ALAMATHY - 400KV B/R 1 | TANTRANSCO | D | Maintenance work & Tant Delta Testing | 2026-05-14 | 09:00 | 2026-05-14 | 17:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Bus Reactor | 11-May-2026 | 08:45 | 11-May-2026 | 10:57
RQ106746 | OCC_237 | KNTL | MAIN BAY (217) OF KOPPAL - 220KV - BUS 3 @KOPPAL - 220KV | KNTL | D | Yearly Bay equipment testing and preventive maintenance. | 2026-05-14 | 09:00 | 2026-05-14 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 11-May-2026 | 08:30 | 11-May-2026 | 10:57
RQ106774 | OCC_237 | MTL | A/R of 400KV-NIZAMABAD-SHANKARAPALLY-2 | MTL | D | Required A/R in Non auto mode for defect rectification work | 2026-05-14 | 09:00 | 2026-05-14 | 17:00 | A/R OFF | No | Rejected | Deferred by requester. | Auto Reclosure | 11-May-2026 | 08:25 | 11-May-2026 | 10:33
RQ106376 | OCC_237 | TANTRANSCO | 230KV-HOSUR_PG-UDANAPALLI-1 | TANTRANSCO | D | Preventive maintenance for bay equipments ( Breaker, CT, Isolator, LAS, Line maintenance and tree clearance) and P&C testing works. | 2026-05-14 | 09:00 | 2026-05-14 | 17:00 |  | Yes | Approved | subject to real time grid conditions. Load management need to be done by TN in case of any contingency. 230KV-UDANAPALLI-HOSUR_PG-2 73% 230KV-UDANAPALLI-PALAVADI D/C 11% each 230KV-GURUBARAPALLI-HOSUR_PG-1 9% 230KV-PALAVADI-METTURAUTO-1 6% 230KV-PALAVADI-KARIMANGLAM-1 5% All PALAVADI and SALEM_TN ICTs shall be in service. | Line Circuits | 10-May-2026 | 21:05 | 11-May-2026 | 11:34
RQ106371 | OCC_237 | TANTRANSCO | 400KV/110KV KAMUDHI-ICT-4 | TANTRANSCO | D | Monthly Maintenance Work | 2026-05-14 | 16:00 | 2026-05-14 | 21:00 |  | Yes | Approved | Load Management to be done by TN. | Transformer | 10-May-2026 | 20:25 | 11-May-2026 | 10:33
RQ106441 | OCC_237 | TANTRANSCO | 230KV-TIRUNELVELI-TP SOLAR-1 | TANTRANSCO | D | Line maintenance(Tower-Tower inspection) sec T.P.Solar to Abisegapatti | 2026-05-14 | 09:00 | 2026-05-14 | 17:00 |  | Yes | Approved | No N-1 for 230kV T P SOLAR. Load Management need to be done by TN. | Line Circuits | 10-May-2026 | 20:25 | 11-May-2026 | 11:12
RQ106481 | OCC_237 | TANTRANSCO | KANARPATTI - 400KV - BUS 2 | TANTRANSCO | D | Monthly Maintenance work | 2026-05-14 | 10:00 | 2026-05-14 | 17:00 |  | Yes | Approved | Remaining all elements shall be in service. | Bus | 10-May-2026 | 20:25 | 11-May-2026 | 10:57
RQ106561 | OCC_237 | TANTRANSCO | THAPPUKUNDU - 400KV B/R 1 | TANTRANSCO | D | Monthly Maintenance work | 2026-05-14 | 09:00 | 2026-05-14 | 15:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Bus Reactor | 10-May-2026 | 20:25 | 11-May-2026 | 10:57
RQ106900 | OCC_237 | PGCIL SR-1 | 400KV-VIJAYAWADA-NELLORE_AP-3 | POWERGRID | D | amp works | 2026-05-14 | 09:00 | 2026-05-14 | 18:00 | AMP works. | Yes | Approved | 400KV-VIJAYAWADA-NELLORE_PG-1 15% 400KV-VIJAYAWADA-NELLORE_PG-2 15% 400KV-NELLORE_AP-VTPS_IV-1 14% 400KV-KRISHNAPATNAM-NELLORE_AP-1 9% 400KV-SATTENPALLY-VTPS_IV-1 9% shall be in service. | Line Circuits | 10-May-2026 | 18:38 | 11-May-2026 | 11:12
RQ108703 | PNOCC | PGCIL SR-1 | 400KV-CUDDAPAH-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For fecilitating CUDDAPHA-ANATHAPUR Line construction works | 2026-05-14 | 08:00 | 2026-05-14 | 14:00 | For fecilitating CUDDAPHA-ANATHAPUR Line construction works | Yes | Approved | 765kV-KURNOOL-CUDDAPAH D/C 13% each 765kV-CUDDAPAH-C'PETA D/C 12% each 400kV-NAGARJUNASAGAR-MEHBOOBNAGAR 12% 400kV-KURNOOL-NAGARJUNSAGAR 10% 400kV-KURNOOL-MAHESHWARAM D/C 10% each 400kV-GOOTY-PAVAGADA D/C All 765kV/400kV CUDDAPAH ICTs and All 400kV/220kV N'SAGAR ICTs shall be in service. | Line Circuits | 08-May-2026 | 18:21 | 11-May-2026 | 11:31
RQ108704 | PNOCC | PGCIL SR-1 | 400KV-CUDDAPAH-NAGARJUNASAGAR_PG-2 | POWERGRID | D | For fecilitating CUDDAPHA-ANATHAPUR Line construction works | 2026-05-14 | 08:00 | 2026-05-14 | 14:00 | For fecilitating CUDDAPHA-ANATHAPUR Line construction works | Yes | Approved | 765kV-KURNOOL-CUDDAPAH D/C 13% each 765kV-CUDDAPAH-C'PETA D/C 12% each 400kV-NAGARJUNASAGAR-MEHBOOBNAGAR 12% 400kV-KURNOOL-NAGARJUNSAGAR 10% 400kV-KURNOOL-MAHESHWARAM D/C 10% each 400kV-GOOTY-PAVAGADA D/C All 765kV/400kV CUDDAPAH ICTs and All 400kV/220kV N'SAGAR ICTs shall be in service. | Line Circuits | 08-May-2026 | 18:21 | 11-May-2026 | 11:31
RQ108705 | PNOCC | PGCIL SR-1 | 400KV-CUDDAPAH-NP_KUNTA-1 | POWERGRID | D | For fecilitating CUDDAPHA-ANATHAPUR Line construction works | 2026-05-15 | 08:00 | 2026-05-15 | 14:00 | For fecilitating CUDDAPHA-ANATHAPUR Line construction works | Yes | Rejected | Multiple shutdowns having sensitivity overlapping on other elements already planned for S/D on the same day. | Line Circuits | 08-May-2026 | 18:25 | 12-May-2026 | 17:53
RQ108706 | PNOCC | PGCIL SR-1 | 400KV-CUDDAPAH-CHITTOOR-1 | POWERGRID | D | For fecilitating CUDDAPHA-ANATHAPUR Line construction works | 2026-05-15 | 08:00 | 2026-05-15 | 14:00 | For fecilitating CUDDAPHA-ANATHAPUR Line construction works | Yes | Rejected | Multiple shutdowns having sensitivity overlapping on other elements already planned for S/D on the same day. | Line Circuits | 08-May-2026 | 18:25 | 12-May-2026 | 17:53
RQ106921 | OCC_237 | PGCIL SR-1 | MUNIRABAD - 400KV - BUS 2 | PGCIL SR-1 | D | For AMP works | 2026-05-14 | 09:00 | 2026-05-14 | 18:00 | AMP works. | Yes | Approved | Shutdown to be availed only after 11:30 HRS or subject to real time voltage conditions in near vicinity S/S. Remaining all elements shall be in service. | Bus | 10-May-2026 | 15:30 | 11-May-2026 | 11:21
RQ106940 | OCC_237 | PGCIL SR-1 | A/R of 400KV-GOOTY-KURNOOL_PG-1 | POWERGRID | D | Hot line stringing works 400kV D/C Peddapodilla to Bethapalle Line at Existing 400kV S/C Gooty – Kurnool (PG) Line, tower no. 754 & 755 - Auto reclosure to be kept in non auto mode | 2026-05-14 | 09:00 | 2026-05-14 | 18:00 | Construction works | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 10-May-2026 | 15:30 | 11-May-2026 | 11:01
RQ107055 | OCC_237 | PGCIL SR-2 | HASSAN - 220KV - BUS 1 | PGCIL SR-2 | D | AMP works of 220 kV Bus-1 | 2026-05-14 | 09:00 | 2026-05-14 | 17:00 |  | Yes | Approved | Remaining all elements shall be in service. | Bus | 10-May-2026 | 14:39 | 11-May-2026 | 11:01
RQ107059 | OCC_237 | PGCIL SR-2 | PAVAGADA_PG - 400KV - BUS 2 | PGCIL SR-2 | C | Connection of Jumpers with new Bay and Carrying out 400 kV Bus Bar-2 Stability Tests under ICT‑07 construction works. | 2026-05-14 | 17:00 | 2026-05-14 | 23:59 |  | Yes | Approved | Remaining all elements shall be in service. | Bus | 10-May-2026 | 14:39 | 11-May-2026 | 10:57
RQ107075 | OCC_237 | PGCIL SR-2 | 765KV/400KV THIRUVALAM-ICT-2 | PGCIL SR-2 | D | AMP works of ICT-2 | 2026-05-14 | 09:00 | 2026-05-14 | 15:00 |  | No | Rejected | Deferred by requester. | Transformer | 10-May-2026 | 14:39 | 11-May-2026 | 10:33
RQ107076 | OCC_237 | PGCIL SR-2 | 400KV/220KV TRIVANDRUM-ICT-3 | PGCIL SR-2 | D | AMP works of ICT-3 | 2026-05-14 | 09:00 | 2026-05-14 | 15:00 |  | Yes | Approved | Load Management need to be done by KSEB. N-1 limit for TRIVANDRUM ICTs is 219 MW each. 400KV/220KV TRIVANDRUM-ICT-1 37% 400KV/220KV TRIVANDRUM-ICT-2 37% All KOTTAYAM and TIRUNELVELI ICTs shall be in service. | Transformer | 10-May-2026 | 14:39 | 11-May-2026 | 11:12
RQ106991 | OCC_237 | TGTRANSCO | 400KV-SURYAPET-KV_KOTA-1 | APTRANSCO,TGTRANSCO | C | General maintenance works and MRT wing testing works | 2026-05-14 | 10:00 | 2026-05-14 | 17:00 |  | Yes | Rejected | As informed by TG, General maintenance works are already completed during D/C shutdown availed for 15 days. | Line Circuits | 10-May-2026 | 13:50 | 11-May-2026 | 18:10
RQ106985 | OCC_237 | TGTRANSCO | 400KV/220KV NIRMAL-ICT-1 | TGTRANSCO | C | For periodical MRT and TRE testing of ICTs and maintenance works | 2026-05-14 | 07:00 | 2026-05-14 | 20:00 |  | Yes | Approved | Load Management need to be done by TG. N-1 limit for NIRMAL ICTs is 223 MW each. 400KV/220KV NIRMAL-ICT-2 38% 400KV/220KV NIRMAL-ICT-3 38% All RAMAGUNDAM and RAMADUGU ICTs shall be in service. | Transformer | 10-May-2026 | 13:50 | 11-May-2026 | 11:12
RQ106847 | OCC_237 | kptcl | 400KV-GUTTUR-HIRIYUR-1 | KPTCL | D | submitting proposal to attend control circuit overall inspection by RT team as per the recommendation by SEE(RT)-KPTC & & 1st Quarterly maintenance | 2026-05-14 | 10:00 | 2026-05-14 | 17:00 |  | Yes | Approved | 400KV-HIRIYUR-GUTTUR-2 44% 400KV-HIRIYUR-BTPS D/C 10% each 400KV-PAVAGADA_PG-HIRIYUR-1 10% 400kV-KUDGI_PG - TUMKUR D/C All HIRIYUR, DONI and GUTTUR ICTs shall be in service. | Line Circuits | 10-May-2026 | 11:23 | 11-May-2026 | 11:21
RQ106831 | OCC_237 | kptcl | 400KV-BPS-YTPS-2 | KPTCL | D | Tightening/Fixing of spacers clamps bolts and nuts and attending repair of conductor damage (leads open) at location no’s 9-10, 11-12, 14-15, 16-17 of multi circuit BPS-Pavagada line-1 and BPS-HM Hole line-1. | 2026-05-14 | 08:00 | 2026-05-14 | 18:00 | YTPS LINE-2 RUN ALONG WITH HM Ferozabad LINE-2 DUE TO MC TOWER AND ALSO SAME WORKS ON HM Ferozabad LINE-2, HENCE OUTAGE REQUIRED ON BOTH LINES | Yes | Rejected | No N-1 for 400kV KALBURGY. KPTCL need to share the voltage management and load and generation management details along with PSS/E case studies for reliable operation | Line Circuits | 10-May-2026 | 11:23 | 11-May-2026 | 11:13
RQ106836 | OCC_237 | kptcl | 400KV-KALABURAGI-YTPS-2 | KPTCL | D | Tightening/Fixing of spacers clamps bolts and nuts and attending repair of conductor damage (leads open) at location no’s 9-10, 11-12, 14-15, 16-17 of multi circuit BPS-Pavagada line-1 and BPS-HM Hole line-1. | 2026-05-14 | 08:00 | 2026-05-14 | 18:00 | Ferozabad-2 RUN ALONG WITH HM YTPS LINE-2 DUE TO MC TOWER AND ALSO SAME WORKS ON YTPS LINE-2, HENCE OUTAGE REQUIRED ON BOTH LINES | Yes | Rejected | No N-1 for 400kV KALBURGY. KPTCL need to share the voltage management and load and generation management details along with PSS/E case studies for reliable operation | Line Circuits | 10-May-2026 | 11:23 | 11-May-2026 | 11:13
RQ106570 | OCC_237 | aptransco | 132KV-KODADA-CHILLAKALLU-1 | APTRANSCO,TGTRANSCO | D | Stringing of snapped Earth wire from Loc. Nos. 8 to 22, 29 to 36 and clearing of vegetation in various locations from 1 to 41 by CBD Gang | 2026-05-14 | 08:00 | 2026-05-14 | 18:00 | Stringing of snapped Earth wire from Loc. Nos. 8 to 22, 29 to 36 and clearing of vegetation in various locations from 1 to 41 by CBD Gang | Yes | Approved | Load management to be done by AP & TG | Line Circuits | 10-May-2026 | 10:40 | 11-May-2026 | 10:57
RQ106671 | OCC_237 | aptransco | PODILI - 400KV - BUS 2 | APTRANSCO | D | FOR PERIODICAL MAINTENANCE AND MRT WORKS | 2026-05-14 | 09:00 | 2026-05-14 | 17:00 | Annual maintenance works | Yes | Approved | Remaining all elements shall be in service. | Bus | 10-May-2026 | 10:40 | 11-May-2026 | 11:01
RQ106614 | OCC_237 | WKTL | 220KV-UPCL-KEMAR-1 | KPTCL | D | 220kV Kemar Line-1 shutdown required for NABL accuracy testing of CVT. Not availed in Mar/Apr 2026 since HV testing equipment under breakdown. | 2026-05-14 | 08:00 | 2026-05-14 | 18:00 | 220kV Kemar Line-1 shutdown required for NABL accuracy testing of CVT. Not availed in Mar/Apr 2026 since HV testing equipment under breakdown. | No | Rejected | Deferred by requester. | Line Circuits | 10-May-2026 | 10:07 | 11-May-2026 | 10:33
RQ106773 | OCC_237 | MTL | A/R of 400KV-NIZAMABAD-SHANKARAPALLY-2 | MTL | D | Required A/R in Non auto mode for defect rectification work | 2026-05-13 | 09:00 | 2026-05-13 | 17:00 | A/R OFF | No | Rejected | Deferred by requester. | Auto Reclosure | 10-May-2026 | 09:33 | 10-May-2026 | 11:11
RQ106745 | OCC_237 | KNTL | MAIN BAY (216) OF KOPPAL - 220KV - BUS 3 @KOPPAL - 220KV | KNTL | D | Yearly Bay equipment testing and preventive maintenance. | 2026-05-13 | 09:00 | 2026-05-13 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 10-May-2026 | 09:02 | 10-May-2026 | 11:28
RQ106379 | OCC_237 | TANTRANSCO | 220KV-UDUMALPET-PALLIVASAL-1 | KSEB,TANTRANSCO | D | Preventive maintenance for bay equipments ( Breaker, CT, Isolator, LAS, Line maintenance and tree clearance) and P&C testing works. | 2026-05-13 | 09:00 | 2026-05-13 | 17:00 |  | Yes | Approved | Load management to be done by KL & TN. 230KV-MYVADI-UDUMALPET-2 51% 230KV-MYVADI-UDUMALPET-1 45% 220KV-PALLIVASAL-KOTHAMANGALAM-1 25% 230KV-UDUMALPET_PG-MYVADI-1,2,3 19% each 400KV-KOCHI-THRISSUR HVDC D/C 19% each 400KV/230KV UDUMALPET_PG-ICT-1,2,3 19% each All ANAIKADAVU ICTs shall be in service. | Line Circuits | 09-May-2026 | 20:30 | 10-May-2026 | 12:09
RQ106393 | OCC_237 | TANTRANSCO | 400KV/110KV RASIPALYAM-ICT-2 | TANTRANSCO | D | Preventive maintenance for bay equipments, Transformer maintenance and P&C testing work. | 2026-05-13 | 09:00 | 2026-05-13 | 17:00 |  | Yes | Approved | Load Management to be done by TN. | Transformer | 09-May-2026 | 20:30 | 10-May-2026 | 11:24
RQ106929 | OCC_237 | PGCIL SR-1 | MEHBOOBNAGAR - 400KV - BUS 2 | TGTRANSCO | C | Bay upgradation works uder ADDCAP- Construction works under SS-126 Package | 2026-05-13 | 09:00 | 2026-05-14 | 18:00 | Construction works under ADD-CAP. | No | Rejected | Deferred by requester. | Bus | 09-May-2026 | 19:41 | 10-May-2026 | 11:11
RQ108748 | PNOCC | aptransco | 400KV-MARADAM-KALPAKKA-1 | APTRANSCO | C | For replacement of old (served more than 25 years) 2 Nos. LAs with newly received 2 Nos. LAs in 400kV Kalapaka-Maradam-1 bay at 400kV SS Kalapaka | 2026-05-13 | 10:00 | 2026-05-13 | 16:00 | 400KV-MARADAM-KALPAKKA-2 will be in service | Yes | Rejected | Multiple shutdowns at the same station. | Line Circuits | 09-May-2026 | 18:30 | 10-May-2026 | 11:49
RQ106448 | OCC_237 | TANTRANSCO | 400KV-ANAIKADAVU-THAPPUKUNDU-2 | TANTRANSCO | D | Monthly Maintenance | 2026-05-13 | 09:00 | 2026-05-13 | 15:00 |  | Yes | Approved | No N-1 for THAPPUKUNDU S/S. Subject to real time grid conditions. Ckt-1 100% shall be in service. | Line Circuits | 09-May-2026 | 15:53 | 10-May-2026 | 11:28
RQ107074 | OCC_237 | PGCIL SR-2 | 765KV/400KV THIRUVALAM-ICT-1 | PGCIL SR-2 | D | AMP works of ICT-1 | 2026-05-13 | 09:00 | 2026-05-13 | 15:00 |  | Yes | Approved | Subject to real time grid conditions and ICT loadings. Subject to NLDC approval. N-1 limit for THIRUVALLAM ICTs is 897 MW each. 765KV/400KV THIRUVALAM-ICT-2 57% All 765kV/400kV ARIYALUR and CUDDAPAH ICTs 765kV-ARIYALUR-THIRUVALLAM D/C 7% each 400KV-THIRUVALAM-NPS D/C shall be in service. | Transformer | 09-May-2026 | 15:14 | 10-May-2026 | 11:56
RQ106910 | OCC_237 | PGCIL SR-1 | 400KV/220KV GAZUWAKA-ICT-1 | PGCIL SR-1 | C | 01 no. Tertiary Bushing & OLTC chamber replacement works | 2026-05-13 | 07:00 | 2026-05-22 | 19:00 | Shutdown nature maintenance works. | Yes | Rejected | ICT loadings are crossing their N-1 limit. N-1 limit for GAZUWAKA ICTs is 238 MW for 315 MVA ICTs each 376 MW for 500 MVA ICT. 400KV/220KV GAZUWAKA-ICT-3 23% 400KV/220KV GAZUWAKA-ICT-2 15% 400KV/220KV KALPAKKA-ICT-1,2,3 11% each All 400KV/220KV MARADAM-ICTs 400KV-MARADAM-KALPAKKA D/C shall be in service. | Transformer | 09-May-2026 | 15:10 | 10-May-2026 | 12:12
RQ106939 | OCC_237 | PGCIL SR-1 | A/R of 400KV-GOOTY-KURNOOL_PG-1 | POWERGRID | D | Hot line stringing works 400kV D/C Peddapodilla to Bethapalle Line at Existing 400kV S/C Gooty – Kurnool (PG) Line, tower no. 754 & 755 - Auto reclosure to be kept in non auto mode | 2026-05-13 | 09:00 | 2026-05-13 | 18:00 | Construction works | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 09-May-2026 | 15:10 | 10-May-2026 | 11:34
RQ106762 | OCC_237 | TGTRANSCO | 400KV/220KV BHOOPALAPALLY-ICT-2 | TGTRANSCO | C | Yearly maintenance. Testing of tandelta, IR of bushings & relays | 2026-05-13 | 09:00 | 2026-05-13 | 18:00 |  | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. Load Management need to be done by TG. 400KV/220KV BHOOPALAPALLY-ICT-1 48% All WARANGAL and RAMAGUNDAM ICTs 220KV-WARANGAL-NAGARAM D/C 15% each 400KV-CHANDALAPUR-BHOOPALAPALLY D/C each 220KV-RAMAGUNDAM-MALYALAPALLI all lines shall be in service. N-1 limit for BHOOPALAPALLY ICTs is 300 MW each. | Transformer | 09-May-2026 | 13:46 | 10-May-2026 | 12:04
RQ106951 | OCC_237 | TGTRANSCO | 220KV-RAICHUR_KA-UPPER_JURALA-1 | KPTCL,TGTRANSCO | C | For relay testing, Line isolator, CVTs maintenance work(pads cleaning, bolts tightening, male & female contacts cleaning & lubrication of isolator) | 2026-05-13 | 09:00 | 2026-05-19 | 18:00 |  | Yes | Approved | Load and generation management to be done by KA and TG | Line Circuits | 09-May-2026 | 13:46 | 10-May-2026 | 11:24
RQ106952 | OCC_237 | TGTRANSCO | 220KV-RAICHUR_KA-UPPER_JURALA-2 | KPTCL,TGTRANSCO | C | For relay testing, Line isolator, CVTs maintenance work(pads cleaning, bolts tightening, male & female contacts cleaning & lubrication of isolator) | 2026-05-13 | 09:00 | 2026-05-19 | 18:00 |  | Yes | Approved | Load and generation management to be done by KA and TG | Line Circuits | 09-May-2026 | 13:46 | 10-May-2026 | 11:24
RQ106953 | OCC_237 | TGTRANSCO | 220KV-NAGARJUNASAGAR_AP-CHALAKURTHY-1 | APTRANSCO,TGTRANSCO | C | For replacement of existing 220kv twin Zebra bus to twin moose bus | 2026-05-13 | 07:00 | 2026-05-13 | 19:00 |  | Yes | Approved | 220KV-CHALAKURTHY-NAGARJUNASAGAR_TS-1 60% 220KV-NAGARJUNASAGAR_PG-NAGARJUNASAGAR_AP-1,2,3 12% each 400KV-CHOUTUPPAL-YADADRI TPP D/C 5% each 400KV-MEHBOOBNAGAR-NAGARJUNASAGAR_PG-1 5% 400KV-GHANAPUR-NAGARJUNASAGAR_PG-1 4% 400KV/220KV NAGARJUNASAGAR_PG-ICTs shall be in service. Subject to real time grid conditions. Load management needs to be done by AP & TG | Line Circuits | 09-May-2026 | 13:46 | 10-May-2026 | 12:09
RQ107003 | OCC_237 | TGTRANSCO | TIE BAY (402) OF 400KV-TIPPAPUR-CHANDALAPUR-1 AND 400KV-TIPPAPUR-TIPPAPUR-CONS-1 @TIPPAPUR - 400KV | TGTRANSCO | C | Periodical testing of bay equipment | 2026-05-13 | 10:00 | 2026-05-13 | 16:00 |  | Yes | Approved | Load Management need to be done by TG. | Bay | 09-May-2026 | 13:46 | 10-May-2026 | 11:21
RQ107004 | OCC_237 | TGTRANSCO | MAIN BAY (403) OF 400KV-TIPPAPUR-TIPPAPUR-CONS-1 AND TIPPAPUR - 400KV - BUS 2 @TIPPAPUR - 400KV | TGTRANSCO | C | Periodical testing of bay equipment | 2026-05-13 | 10:00 | 2026-05-13 | 16:00 |  | Yes | Approved | Load Management need to be done by TG. | Bay | 09-May-2026 | 13:46 | 10-May-2026 | 11:21
RQ107005 | OCC_237 | TGTRANSCO | MAIN BAY (43M) OF 400KV-TIPPAPUR-TIPPAPUR-CONS-1 AND TIPPAPUR-CONS - 400KV - BUS 1 @TIPPAPUR-CONS - 400KV | TGTRANSCO | C | Periodical testing of bay equipment | 2026-05-13 | 10:00 | 2026-05-13 | 16:00 |  | Yes | Approved | Load Management need to be done by TG. | Bay | 09-May-2026 | 13:46 | 10-May-2026 | 11:21
RQ106569 | OCC_237 | aptransco | 132KV-KODADA-CHILLAKALLU-1 | APTRANSCO,TGTRANSCO | D | Stringing of snapped Earth wire from Loc. Nos. 8 to 22, 29 to 36 and clearing of vegetation in various locations from 1 to 41 by CBD Gang | 2026-05-13 | 08:00 | 2026-05-13 | 18:00 | Stringing of snapped Earth wire from Loc. Nos. 8 to 22, 29 to 36 and clearing of vegetation in various locations from 1 to 41 by CBD Gang | Yes | Approved | Load management to be done by AP & TG | Line Circuits | 09-May-2026 | 11:54 | 10-May-2026 | 11:24
RQ106596 | OCC_237 | aptransco | 132KV-ASWAROAPET-T NARSAPURAM-1 | APTRANSCO,TGTRANSCO | D | for attending Tan delta and relay testings by MRT Wing, Eluru. | 2026-05-13 | 11:00 | 2026-05-13 | 13:00 | for attending Tan delta and relay testings by MRT Wing, Eluru. | Yes | Approved | Load management to be done by AP & TG. Consecutive shutdowns | Line Circuits | 09-May-2026 | 11:54 | 10-May-2026 | 11:21
RQ106597 | OCC_237 | aptransco | 132KV-ASWAROAPET-T NARSAPURAM-2 | APTRANSCO,TGTRANSCO | D | for attending Tan delta and relay testings by MRT Wing, Eluru. | 2026-05-13 | 14:00 | 2026-05-13 | 16:00 | for attending Tan delta and relay testings by MRT Wing, Eluru. | Yes | Approved | Load management to be done by AP & TG. Consecutive shutdowns. | Line Circuits | 09-May-2026 | 11:54 | 10-May-2026 | 11:21
RQ106652 | OCC_237 | aptransco | 400KV/220KV URAVAKONDA-ICT-2 | APTRANSCO | D | "1. Half yearly Maintenance works 2. Periodical Relay testing of ICT *Note : ICT-1,3&4 will be in service" | 2026-05-13 | 09:00 | 2026-05-13 | 15:00 | Annual maintenance works | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. Load Management need to be done by AP. N-1 limit for URAVAKONDA ICTs is 207 MW for 329 MVA ICT each and 347 MW for 500 MVA ICT each. 400KV/220KV URAVAKONDA-ICT-3 33% 400KV/220KV URAVAKONDA-ICT-4 33% 400KV/220KV URAVAKONDA-ICT-1 21% shall be in service. | Transformer | 09-May-2026 | 11:54 | 10-May-2026 | 12:04
RQ106708 | OCC_237 | aptransco | 400KV-VTPS_IV-THALLAYAPALEM-2 | APTRANSCO | D | For periodical Line Maintenance works | 2026-05-13 | 09:00 | 2026-05-13 | 17:00 | Annual maintenance works | Yes | Approved | 400KV-SATTENPALLY-VTPS_IV-1 41% 400KV-VTPS_IV-VIJAYAWADA-1 31% 400KV-CHILAKALURIPETA-SATTENPALLY D/C 12% each 400KV-SRISAILAM_LEFT_BANK-SATTENPALLY D/C All C'PETA ICTs shall be in service. | Line Circuits | 09-May-2026 | 11:54 | 10-May-2026 | 11:56
RQ107515 | OCC_2371 | aptransco | 132KV-PRATHAP_NAGAR-YANAM-1 | PONDICHERRY,APTRANSCO | D | For erection of 220kV Z-Type Tower underneath the crossing of 132kV KKD-Gollapalem circuit, Pratapnagar-Yanam circuit and 220kV SSS Barge idle line duly the diverting the existing Pratapnagar-Yanam line. | 2026-05-13 | 08:00 | 2026-05-13 | 14:00 | "Formation of 2nd circuit from 220kV SS Kakinada to 132kV Pratapnagar SS" by utilizing the idle 220kV Samalkota - GMR Barge DC line at 132kV Potential, 132kV Kakinada - Ramachandrapuram DC line, 132kV PratapnagarYanam single circuit and 132kV Kakinada-Gollaplem single circuit. The work was awarded to M/s. Radhakrishna Contractors, Rajahmundry vide reference 2nd cited. The work is under progress. | Yes | Rejected | Load management to be done by AP & PED. FTC is required. Need to furnish the details of works and schemes properly prior to the shutdown. SRPC approval is required for the temporary network rearrangement submitted by AP. | Line Circuits | 09-May-2026 | 11:54 | 10-May-2026 | 11:24
RQ107388 | OCC_2371 | kseb | 132KV-KUZHITHURAI-PARASSALA-1 | KSEB,TANTRANSCO | D | Bus reconductoring works | 2026-05-13 | 06:00 | 2026-05-13 | 17:00 | Bus reconductoring works | Yes | Approved | Load Management to be done by TN and KSEB. | Line Circuits | 09-May-2026 | 11:17 | 10-May-2026 | 11:28
RQ106459 | OCC_237 | ILFS | ILFS - 400KV B/R 1 | IL&FS | C | Yearly equipment maintenance | 2026-05-13 | 09:00 | 2026-05-15 | 17:00 | Continuous S/D Required | Yes | Approved | Concurred, subject to real time grid conditions. | Bus Reactor | 09-May-2026 | 11:17 | 10-May-2026 | 11:28
RQ106496 | OCC_237 | kseb | A/R of 220KV-KOCHI-KALAMASSERY-2 | KSEB | D | Disc replacement work | 2026-05-13 | 09:00 | 2026-05-13 | 17:00 | Disc replacement work | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 09-May-2026 | 11:10 | 10-May-2026 | 11:28
RQ106525 | OCC_237 | kseb | A/R of 220KV-ELAPULLY-MADAKATHARA-1 | KSEB | D | For the work associated with the replacement of porcelain disc insulator with polymer insulator on 2MDPK feeder. | 2026-05-13 | 08:00 | 2026-05-13 | 17:00 | For the work associated with the replacement of porcelain disc insulator with polymer insulator on 2MDPK feeder. | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 09-May-2026 | 11:10 | 10-May-2026 | 11:28
RQ106722 | OCC_237 | TANTRANSCO | 230KV-KARAIKUDI-KARAIKUDI(TN)-1 | TANTRANSCO | D | Monthly maintenance work. | 2026-05-11 | 16:00 | 2026-05-11 | 22:00 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Line Circuits | 09-May-2026 | 10:27 | 08-May-2026 | 14:43
RQ106728 | OCC_237 | TANTRANSCO | 230KV-KARAIKUDI-SEMBATTI | TANTRANSCO | D | Monthly maintenance work. | 2026-05-11 | 09:00 | 2026-05-11 | 16:00 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Line Circuits | 09-May-2026 | 10:27 | 08-May-2026 | 14:43
RQ107414 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-1 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-11 | 00:00 | 2026-05-11 | 04:00 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Line Circuits | 09-May-2026 | 10:27 | 08-May-2026 | 14:43
RQ107422 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-2 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-11 | 00:00 | 2026-05-11 | 04:00 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Line Circuits | 09-May-2026 | 10:27 | 08-May-2026 | 14:43
RQ106772 | OCC_237 | MTL | A/R of 400KV-NIZAMABAD-SHANKARAPALLY-2 | MTL | D | Required A/R in Non auto mode for defect rectification work | 2026-05-12 | 09:00 | 2026-05-12 | 17:00 | A/R OFF | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 09-May-2026 | 09:05 | 09-May-2026 | 16:48
RQ106744 | OCC_237 | KNTL | MAIN BAY (215) OF 220KV-KOPPAL-CSS_KS_PTR-1 @KOPPAL - 220KV | KNTL | D | Yearly Bay equipment testing and preventive maintenance. | 2026-05-12 | 09:00 | 2026-05-12 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 09-May-2026 | 08:44 | 09-May-2026 | 16:43
RQ106967 | OCC_237 | TGTRANSCO | DINDI - 400KV - BUS 2 | TGTRANSCO | C | General and periodical maintenance to be done | 2026-05-12 | 10:00 | 2026-05-12 | 17:00 |  | Yes | Approved | Remaining all elements shall be in service. | Bus | 08-May-2026 | 19:23 | 09-May-2026 | 16:55
RQ106982 | OCC_237 | TGTRANSCO | KAMALAPURAM - 400KV B/R 1 | TGTRANSCO | C | periodical testings by TRE & maintenance wing | 2026-05-12 | 10:00 | 2026-05-12 | 16:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Bus Reactor | 08-May-2026 | 19:23 | 09-May-2026 | 16:27
RQ106920 | OCC_237 | PGCIL SR-1 | MUNIRABAD - 400KV - BUS 1 | PGCIL SR-1 | D | For AMP works | 2026-05-12 | 12:00 | 2026-05-12 | 18:00 | AMP works. | Yes | Approved | Shutdown to be availed only after 12:00 HRS or subject to voltage profile condition in near vicinity substation in real time. | Bus | 08-May-2026 | 18:07 | 09-May-2026 | 16:55
RQ106938 | OCC_237 | PGCIL SR-1 | A/R of 400KV-GOOTY-KURNOOL_PG-1 | POWERGRID | D | Hot line stringing works 400kV D/C Peddapodilla to Bethapalle Line at Existing 400kV S/C Gooty – Kurnool (PG) Line, tower no. 754 & 755 - Auto reclosure to be kept in non auto mode | 2026-05-12 | 09:00 | 2026-05-12 | 18:00 | Construction works | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 08-May-2026 | 18:07 | 09-May-2026 | 16:48
RQ107039 | OCC_237 | PGCIL SR-2 | 220KV-HASSAN-YECHANAHALLI-1 | KPTCL | D | AMP of Terminal Equipments | 2026-05-12 | 09:00 | 2026-05-12 | 17:00 |  | Yes | Approved | No N-1 for 220kV-YECHANAHALLI S/S. Load & Voltage management to be done by KA Subject to real time grid conditions and line loadings. 220kV- K R PET - C R PATNA (YECHANAHALLI) 220KV-MYSORE-K R PET-1 100% 220KV-HASSAN-GOPALPURA-1 14% 220KV-SHANTIPURA-DUDDA-1 7% 220KV-SHANTIPURA-MRS_SHIMOGA-1 7% 220KV-HASSAN_KA-HASSAN-1 6% 220KV-DUDDA-HASSAN_KA-1 6% All MYSORE and BIDADI ICTs shall be in service. | Line Circuits | 08-May-2026 | 17:57 | 09-May-2026 | 17:44
RQ107073 | OCC_237 | PGCIL SR-2 | 400KV/230KV HOSUR_PG-ICT-1 | PGCIL SR-2 | D | AMP works of ICT-1 | 2026-05-12 | 09:00 | 2026-05-12 | 15:00 |  | Yes | Approved | The same will lead to increase the loading of Hosur ICTs. N-1 limit for HOSUR ICTs is 219 MW for 315 MVA ICT each and 347 MW for 500 MVA ICT. | Transformer | 08-May-2026 | 17:57 | 09-May-2026 | 17:19
RQ107058 | OCC_237 | PGCIL SR-2 | PAVAGADA_PG - 400KV - BUS 1 | PGCIL SR-2 | C | Connection of Jumpers with new Bay and Carrying out 400 kV Bus Bar-1 Stability Tests under ICT‑07 construction works. | 2026-05-12 | 17:00 | 2026-05-12 | 23:59 |  | Yes | Approved | Remaining all elements shall be in service. | Bus | 08-May-2026 | 17:57 | 09-May-2026 | 16:55
RQ107536 | OCC_2371 | PGCIL SR-2 | 220KV-KOPPAL-AYANA_SIX_KOPPAL-1 | AYANA RENEWABLE POWER SIX PVT LTD | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 19/0 - 20/0 | 2026-05-12 | 08:00 | 2026-05-12 | 19:00 | Concurrence from concerned IPPs will be submitted on D-4 basis. | Yes | Approved | Concurred IPP concurrence forwarded by PGCIL. Subject to real time grid conditions and RE generation and proper revision and adherence of schedules. | Line Circuits | 08-May-2026 | 17:57 | 09-May-2026 | 16:43
RQ106370 | OCC_237 | TANTRANSCO | 400KV/110KV KAMUDHI-ICT-3 | TANTRANSCO | D | Monthly Maintenance Work | 2026-05-12 | 16:00 | 2026-05-12 | 21:00 |  | Yes | Approved | Load Management need to be done by TN. Subject to ICT loadings to be within their N-1 limit. | Transformer | 08-May-2026 | 12:24 | 09-May-2026 | 16:27
RQ106447 | OCC_237 | TANTRANSCO | 400KV-ANAIKADAVU-THAPPUKUNDU-1 | TANTRANSCO | D | Monthly Maintenance | 2026-05-12 | 09:00 | 2026-05-12 | 15:00 |  | Yes | Approved | No N-1 for THAPPUKUNDU S/S. Subject to real time grid conditions ckt-2 100% shall be in service. | Line Circuits | 08-May-2026 | 12:24 | 09-May-2026 | 16:43
RQ107387 | OCC_2371 | kptcl | 400KV-HEBBANAHALLI-UPCL-1 | KARNATAKA | C | Retain the existing Tower No. 43 and removal of conductor from Tower No. 42 (DD +06) to Tower No. 44 (DC+00). At the same time providing backstay support for both Towers 42 and 44. and Erection of Tower No. 42A (DD +06), Tower No. 43,(DD+09) and Tower No. 01 (MD+00) | 2026-05-12 | 18:01 | 2026-05-31 | 23:59 | Establishing 2X500MVA, 400/220kV sub-station at Kadandale in Moodabidre Taluk, Dakshina Kannada District. Shutdown required continuous from 02.05.2026 to 10.06.2026. The portal was not allowed to take shutdown request for 12.05.2026 and 13.05.2026 as it was showing duplicate request. | Yes | Rejected | 400KV-HEBBANAHALLI-UPCL D/C already under S/D. Duplicate request. | Line Circuits | 08-May-2026 | 11:55 | 09-May-2026 | 16:55
RQ106976 | OCC_237 | NLC | 230KV/6.6KV NEYVELI TS II-ST-4 | NLC | C | For Circuit Breaker Operating Boxes retrofitting works | 2026-05-12 | 09:00 | 2026-05-14 | 17:00 | All other ST will be in Service. Shutdown is requested before Peak period | No | Rejected | Deferred by requester. | Transformer | 08-May-2026 | 10:58 | 09-May-2026 | 16:27
RQ106500 | OCC_237 | NPCIL | 400KV-KUDANKULAM-TIRUNELVELI-2 | POWERGRID | C | Line insulator cleaning work. Wave trap top side connectors CRM measurements. SF6 gas properties checking in the compartments. SF6 Density meters calibration to be done. | 2026-05-12 | 07:00 | 2026-05-12 | 18:00 |  | Yes | Approved | 400KV-KUDANKULAM-TIRUNELVELI-1 40% 400KV-KUDANKULAM-TIRUNELVELI-3 36% 400KV-TUTICORIN_PS-KUDANKULAM-2 16% 400KV-TUTICORIN_PS-TIRUNELVELI-1 9% 400KV-KANARPATTI-TIRUNELVELI-1 4% shall be in service. | Line Circuits | 08-May-2026 | 10:30 | 09-May-2026 | 17:19
RQ106687 | OCC_237 | aptransco | 400KV/220KV KALIKIRI-ICT-2 | APTRANSCO | D | Maintenance works | 2026-05-12 | 10:00 | 2026-05-12 | 17:00 | Annual maintenance works | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. Load Management need to be done by AP. 400KV/220KV KALIKIRI-ICT-1 60% All CHITTOOR and RACHAGUNNERI ICTs shall be in service. N-1 limit for KALIKIRI ICTs is 191 MW each. | Transformer | 08-May-2026 | 10:00 | 09-May-2026 | 17:19
RQ106568 | OCC_237 | aptransco | 132KV-KODADA-CHILLAKALLU-1 | APTRANSCO,TGTRANSCO | D | Stringing of snapped Earth wire from Loc. Nos. 8 to 22, 29 to 36 and clearing of vegetation in various locations from 1 to 41 by CBD Gang | 2026-05-12 | 08:00 | 2026-05-12 | 18:00 | Stringing of snapped Earth wire from Loc. Nos. 8 to 22, 29 to 36 and clearing of vegetation in various locations from 1 to 41 by CBD Gang | Yes | Approved | Load management to be done by AP & TG | Line Circuits | 08-May-2026 | 10:00 | 09-May-2026 | 16:40
RQ106679 | OCC_237 | aptransco | TIE BAY (423) OF 400KV-KONASEEMA-VEMAGIRI_AP-2 AND 400KV-GAUTAMI-VEMAGIRI_AP-2 @VEMAGIRI_AP - 400KV | APTRANSCO | D | MRT testings at Vemagiri end | 2026-05-12 | 09:00 | 2026-05-12 | 17:00 | Annual maintenance works | Yes | Approved | Remaining bays shall be in service. | Bay | 08-May-2026 | 10:00 | 09-May-2026 | 16:43
RQ106763 | OCC_237 | aptransco | 400KV-URAVAKONDA-MEHBOOBNAGAR-1 | APTRANSCO,TGTRANSCO | D | For PMI defects rectification from loc.No. 299-303. | 2026-05-12 | 07:00 | 2026-05-12 | 12:00 | Annual maintenance works | Yes | Approved | 400KV-MEHBOOBNAGAR-URAVAKONDA-2 31% 400KV-YEDULA-DINDI-2 17% 400KV-TALARCHEVU-JAMMALAMADUGU D/C 16% each 400KV-TALARCHEVU-URAVAKONDA D/C 16% each 400KV-HINDUPUR-NP_KUNTA D/C 12% each shall be in service. | Line Circuits | 08-May-2026 | 10:00 | 09-May-2026 | 16:56
RQ106613 | OCC_237 | WKTL | 400KV-HEBBANAHALLI-UPCL-1 | KARNATAKA | D | 400kVHebbanahalli line -1 shutdown required for NABL accuracy testing of CVT | 2026-05-10 | 08:00 | 2026-05-10 | 18:00 | 400kVHebbanahalli line -1 shutdown required for NABL accuracy testing of CVT | No | Rejected | Requester does not update the availing status as yes on D-3. Line under long outage since 06.05.2026. May use the opportunity for completion of works. | Line Circuits | 08-May-2026 | 09:40 | 07-May-2026 | 10:07
RQ106743 | OCC_237 | KNTL | BUS SECTIONALIZER BAY (212) OF KOPPAL - 220KV - BUS 2 AND KOPPAL - 220KV - BUS 4 @KOPPAL - 220KV | KNTL | D | Yearly Bay equipment testing and preventive maintenance. | 2026-05-11 | 09:00 | 2026-05-11 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 08-May-2026 | 08:15 | 08-May-2026 | 15:12
RQ106771 | OCC_237 | MTL | A/R of 400KV-NIZAMABAD-SHANKARAPALLY-2 | MTL | D | Required A/R in Non auto mode for defect rectification work | 2026-05-11 | 09:00 | 2026-05-11 | 17:00 | A/R OFF | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 08-May-2026 | 08:10 | 08-May-2026 | 15:01
RQ106928 | OCC_237 | PGCIL SR-1 | MAHESHWARAM_PG - 765KV - BUS 2 | PGCIL SR-1 | C | Commissioning of 765kV BUS-II for Bidar Bay extension works (SS-12T) | 2026-05-11 | 09:00 | 2026-05-14 | 18:00 | Construction works | Yes | Approved | Subject to NLDC approval and real time grid conditions. Remaining all elements shall be in service. | Bus | 07-May-2026 | 17:17 | 08-May-2026 | 15:12
RQ106820 | OCC_237 | kptcl | TIE BAY (411) OF 400KV-NELAMANGALA-TALGUPPA-1 AND 400KV-NELAMANGALA-HIRIYUR-1 @NELAMANGALA - 400KV | KPTCL | D | Breaker testing and maintenance works. | 2026-05-11 | 11:00 | 2026-05-11 | 17:00 |  | No | Rejected | Deferred by requester. | Bay | 07-May-2026 | 16:57 | 08-May-2026 | 14:43
RQ106846 | OCC_237 | kptcl | 400KV-GUTTUR-BTPS-1 | KPTCL | D | submitting proposal to attend C isolator allignment issue & 1st Quarterly maintenance | 2026-05-11 | 10:00 | 2026-05-11 | 17:00 |  | Yes | Approved | Shutdown to be availed only after 11:00 HRS or subject to voltage profile in near vicinity stations at real time. 400KV-HIRIYUR-BTPS-1 29% 400KV-HIRIYUR-BTPS-2 29% 400KV-BTPS-RTPS-1 25% 400KV-DONI-GUTTUR-1 22% 400KV-DONI-MUNIRABAD-1 15% 220KV-LINGAPUR-BTPS-1 11% 400KV-MUNIRABAD-RTPS-1 10% 220KV-SOMASAMUDRA-REGULAPADU-1 6% All BTPS and MUNIRABAAD ICTs shall be in service. | Line Circuits | 07-May-2026 | 16:55 | 08-May-2026 | 16:11
RQ106835 | OCC_237 | kptcl | 400KV-KALABURAGI-YTPS-1 | KPTCL | D | Tightening/Fixing of spacers clamps bolts and nuts and attending repair of conductor damage (leads open) at location no’s 9-10, 11-12, 14-15, 16-17 of multi circuit BPS-Pavagada line-1 and BPS-HM Hole line-1. | 2026-05-11 | 08:00 | 2026-05-11 | 18:00 | Ferozabad-1 RUN ALONG WITH HM YTPS LINE-1 DUE TO MC TOWER AND ALSO SAME WORKS ON YTPS LINE-1, HENCE OUTAGE REQUIRED ON BOTH LINES | Yes | Rejected | No N-1 for 400kV KALBURGY. KPTCL need to share the voltage management and load and generation management details along with PSS/E case studies for reliable operation | Line Circuits | 07-May-2026 | 16:16 | 08-May-2026 | 15:54
RQ106990 | OCC_237 | TGTRANSCO | 400KV/220KV SURYAPET-ICT-2 | TGTRANSCO | C | General maintenance works and MRT,TRE wing testing works | 2026-05-11 | 10:00 | 2026-05-12 | 17:00 |  | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. Load Management need to be done by TG. N-1 limit for SURYAPET ICTs is 222 MW for 315 MVA ICT each and 352 MW for 500 MVA ICT. | Transformer | 07-May-2026 | 15:31 | 08-May-2026 | 15:33
RQ107021 | OCC_237 | TGTRANSCO | 400KV-SRISAILAM_LEFT_BANK-SATTENPALLY-2 | APTRANSCO,TGTRANSCO | C | Annual Maintenance works at 400KV OD YARD- overhauling of operating mechanism box and cleaning of the contacts of isolator and earth switch,cleaning of porcelin insulators and Realy testing works | 2026-05-11 | 06:00 | 2026-05-12 | 17:00 |  | Yes | Approved | 400KV-SRISAILAM_LEFT_BANK-SATTENPALLY-1 28% 400KV-SATTENPALLY-VTPS_IV-1 15% 400KV-CHILAKALURIPETA-SATTENPALLY D/C 14% each 400KV-KURNOOL_PG-NARNOOR D/C 8% each 765KV/400KV CHILAKALURIPETA-ICT-1,2 14% each shall be in service. | Line Circuits | 07-May-2026 | 15:31 | 08-May-2026 | 15:54
RQ106997 | OCC_237 | TGTRANSCO | 400KV-TIPPAPUR-CHANDALAPUR-1 | TGTRANSCO | C | Periodical testing of bay equipment | 2026-05-11 | 10:00 | 2026-05-12 | 18:00 |  | Yes | Approved | 400KV-TIPPAPUR-CHANDALAPUR-2 74% 400KV-JANAGAON-TIPPAPUR-2 4% 400KV-RAMADUGU-GAJWEL D/C 4% each shall be in service. | Line Circuits | 07-May-2026 | 15:31 | 08-May-2026 | 14:57
RQ106383 | OCC_237 | TANTRANSCO | 400KV/230KV ANAIKADAVU-ICT-4 | TANTRANSCO | D | Preventive maintenance for bay equipments, Transformer maintenance and P&C testing work. | 2026-05-11 | 09:00 | 2026-05-11 | 17:00 |  | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. Load Management need to be done by TN. N-1 limit for ANAIKADAVU ICTs is 227 MW each. 400KV/230KV ANAIKADAVU-ICT-3 35% 400KV/230KV ANAIKADAVU-ICT-5 35% All UDUMALPET and PALAVADI ICTs shall be in service. | Transformer | 07-May-2026 | 14:25 | 08-May-2026 | 15:48
RQ107535 | OCC_2371 | PGCIL SR-2 | 220KV-KOPPAL-AYANA_SIX_KOPPAL-1 | AYANA RENEWABLE POWER SIX PVT LTD | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 19/0 - 20/0 | 2026-05-11 | 08:00 | 2026-05-11 | 19:00 | Concurrence from concerned IPPs will be submitted on D-4 basis. | Yes | Approved | Concurred IPP concurrence forwarded by PGCIL. Subject to real time grid conditions and RE generation and proper revision and adherence of schedules. | Line Circuits | 07-May-2026 | 14:06 | 08-May-2026 | 15:12
RQ106567 | OCC_237 | aptransco | 132KV-KODADA-CHILLAKALLU-1 | APTRANSCO,TGTRANSCO | D | Stringing of snapped Earth wire from Loc. Nos. 8 to 22, 29 to 36 and clearing of vegetation in various locations from 1 to 41 by CBD Gang | 2026-05-11 | 08:00 | 2026-05-11 | 18:00 | Stringing of snapped Earth wire from Loc. Nos. 8 to 22, 29 to 36 and clearing of vegetation in various locations from 1 to 41 by CBD Gang | Yes | Approved | Load management to be done by AP & TG | Line Circuits | 07-May-2026 | 11:51 | 08-May-2026 | 15:01
RQ106630 | OCC_237 | aptransco | RACHAGUNNERI - 400KV B/R 1 | APTRANSCO | D | 125MVAR Reactor general maintenance | 2026-05-11 | 09:00 | 2026-05-11 | 16:00 | Annual maintenance works | Yes | Approved | Concurred, subject to real time grid conditions. | Bus Reactor | 07-May-2026 | 11:51 | 08-May-2026 | 15:12
RQ106660 | OCC_237 | aptransco | 400KV/220KV GUDDIGUDEM-ICT-2 | APTRANSCO | D | For General maintenance work by equipment | 2026-05-11 | 09:00 | 2026-05-11 | 17:00 | Annual maintenance works | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. Load Management need to be done by AP. 400KV/220KV GUDDIGUDEM-ICT-1 40% All VEMAGIRI AP and K V KOTA ICTs 400KV-GUDDIGUDEM-KV_KOTA D/C 22% each shall be in service. N-1 limit for GUDDIGUDEM ICTs is 221 MW each. | Transformer | 07-May-2026 | 11:51 | 08-May-2026 | 15:48
RQ106669 | OCC_237 | aptransco | URAVAKONDA - 400KV - BUS 1 | APTRANSCO | D | "1. Maintenance of Jack bus & connected jumpers. *Note: 400KV Veltoor-1 feeder will be in service " | 2026-05-11 | 09:00 | 2026-05-11 | 15:00 | Annual maintenance works | Yes | Approved | Concurred, approved along with 400KV-URAVAKONDA-MEHBOOBNAGAR-2 due to the nature of works. | Bus | 07-May-2026 | 11:51 | 08-May-2026 | 15:33
RQ106677 | OCC_237 | aptransco | 400KV-URAVAKONDA-MEHBOOBNAGAR-2 | APTRANSCO,TGTRANSCO | D | "1. Maintenance of Jack bus & connected jumpers. *Note: 400KV Veltoor-1 feeder will be in service " | 2026-05-11 | 09:00 | 2026-05-11 | 15:00 | Annual maintenance works | Yes | Approved | 400KV-MEHBOOBNAGAR-URAVAKONDA-1 31% 400KV-YEDULA-DINDI-2 17% 400KV-TALARCHEVU-JAMMALAMADUGU D/C 16% each 400KV-TALARCHEVU-URAVAKONDA D/C 16% each 400KV-HINDUPUR-NP_KUNTA D/C 12% each shall be in service. | Line Circuits | 07-May-2026 | 11:51 | 08-May-2026 | 15:33
RQ106494 | OCC_237 | kseb | A/R of 220KV-KOCHI-KALAMASSERY-2 | KSEB | D | Disc replacement work | 2026-05-11 | 09:00 | 2026-05-11 | 17:00 | Disc replacement work | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 07-May-2026 | 11:15 | 08-May-2026 | 15:05
RQ106784 | OCC_237 | NLC | 400KV/230KV NTPL-ICT-2 | NTPL | C | RTV Silicone Coating Work | 2026-05-11 | 09:00 | 2026-05-13 | 18:00 |  | Yes | Approved | Other ICT shall be in service. | Transformer | 07-May-2026 | 10:56 | 08-May-2026 | 15:48
RQ106467 | OCC_237 | WKTL | KUDGI_PG - 400KV - BUS 2 | PGCIL SR-2 | C | Extension/Interconnection of400kv Main Bus-2 from existing PGCIL Kudgi to WRSR New Narendra. | 2026-05-11 | 09:00 | 2026-05-16 | 18:00 | Extension/Interconnection of400kv Main Bus-2 from existing PGCIL Kudgi to WRSR New Narendra. | Yes | Rejected | As WKTL requested to extend the shutdown of Bus-1. To be given only after normalization of Bus-1 and subject to no other overlapping shutdowns. | Bus | 07-May-2026 | 10:14 | 08-May-2026 | 15:12
RQ107412 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-1 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-09 | 00:00 | 2026-05-09 | 04:00 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Line Circuits | 07-May-2026 | 10:03 | 06-May-2026 | 11:26
RQ107420 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-2 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-09 | 00:00 | 2026-05-09 | 04:00 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Line Circuits | 07-May-2026 | 10:03 | 06-May-2026 | 11:26
RQ108630 | EMERGENCY | JSW_Renew_Two | 230KV-TTGS-JSW_SAVALAPERI-1 | JINDAL | C | BCU hardware issue rectification work at PGCIL Tuticorin GIS endBay no:215 i | 2026-05-07 | 10:00 | 2026-05-07 | 12:01 |  | Yes | Approved |  | Line Circuits | 06-May-2026 | 12:01 | 07-May-2026 | 09:25
RQ106912 | OCC_237 | PGCIL SR-1 | 400KV/220KV MEHBOOBNAGAR-ICT-2 | TGTRANSCO | D | Bay upgradation works uder ADDCAP- Construction works under SS-126 Package | 2026-05-10 | 18:00 | 2026-05-10 | 23:30 | Construction works under ADD-CAP. | No | Rejected | Deferred by requester. | Transformer | 06-May-2026 | 19:57 | 07-May-2026 | 10:07
RQ106909 | OCC_237 | PGCIL SR-1 | 400KV/220KV NAGARJUNASAGAR_PG-ICT-3 | PGCIL SR-1 | D | OIL LEAKAGE ARRESTING | 2026-05-10 | 09:00 | 2026-05-10 | 18:00 | Shutdown nature maintenance works. | Yes | Approved | Load Management need to be done by AP and TG. N-1 limit of 315MVA ICT is 215MW & 500MVA ICT is 340MW. Pump operation need to be restricted if 315MVA ICTs is loading above 180MW & 500MVA ICT above 280MW No pump operation shall be allowed subject to real time conditions. 400KV/220KV NAGARJUNASAGAR_PG-ICT-2 37% 400KV/220KV NAGARJUNASAGAR_PG-ICT-1 23% All DINDI ICTs 220KV-CHALAKURTHY-NAGARJUNASAGAR_AP-1 15% 220KV-CHALAKURTHY-MIRYALAGUDA-1 9% 220kV KM Pally -DINDI D/C shall be in service | Transformer | 06-May-2026 | 16:12 | 07-May-2026 | 14:38
RQ106933 | OCC_237 | PGCIL SR-1 | A/R of 400KV-GOOTY-RAICHUR_PG-1 | POWERGRID | D | Hot line stringing works 400kV D/C Bethapalle to PGCIL Anantapur Line at Existing 400kV D/C Gooty – Raichur Line, Existing tower no. 365 & 366 - Auto reclosure to be kept in non auto mode | 2026-05-10 | 09:00 | 2026-05-10 | 18:00 | Construction works | No | Rejected | Deferred by requester. | Auto Reclosure | 06-May-2026 | 16:12 | 07-May-2026 | 10:07
RQ106937 | OCC_237 | PGCIL SR-1 | A/R of 400KV-GOOTY-RAICHUR_PG-2 | POWERGRID | D | Hot line stringing works 400kV D/C Bethapalle to PGCIL Anantapur Line at Existing 400kV D/C Gooty – Raichur Line, Existing tower no. 365 & 366 - Auto reclosure to be kept in non auto mode | 2026-05-10 | 09:00 | 2026-05-10 | 18:00 | Construction works | No | Rejected | Deferred by requester. | Auto Reclosure | 06-May-2026 | 16:12 | 07-May-2026 | 10:07
RQ107514 | OCC_2371 | PGCIL SR-1 | MAIN BAY (406) OF 400KV/220KV MEHBOOBNAGAR-ICT-2 AND MEHBOOBNAGAR - 400KV - BUS 2 @MEHBOOBNAGAR - 400KV | TGTRANSCO | C | Continuation of S/D upto 16th may for constuction works under SS-126 for Bay upgradation under ADDCAP. Kindly note S/D is originally approved upto 04th to 09th on Main OCC | 2026-05-10 | 00:30 | 2026-05-16 | 19:00 | Construction works under ADD-CAP. | Yes | Approved | Remaining bays shall be in service. | Bay | 06-May-2026 | 16:12 | 07-May-2026 | 11:00
RQ107072 | OCC_237 | PGCIL SR-2 | 400KV/220KV KOZHIKODE-ICT-3 | POWERGRID | D | AMP works of ICT-3 | 2026-05-10 | 09:00 | 2026-05-10 | 13:00 |  | Yes | Approved | S3 - 500MW reduction. Load Management need to be done by KSEB. N-1 limit for KOZHIKODE ICTs is 194 MW for 315 MVA ICTs each and 307 MW for 500 MVA ICT. Timelines of shutdown to be strictly adhered as ICTs are violating their N-1 limits after 15:00 HRS on weekends as per previous loading trends. 400KV/220KV KOZHIKODE-ICT-1 30% 400KV/220KV KOZHIKODE-ICT-2 30% All MADAKKATHARA and THRISSUR HVDC ICTs shall be in service. | Transformer | 06-May-2026 | 15:21 | 07-May-2026 | 14:24
RQ106855 | OCC_237 | kptcl | 400KV-KOLAR_AC-MYLASANDRA-1 | KPTCL | C | To take up 400kV MC monopole line balance foundation, erection, stringing and destringing work. As work is mandatory to take up for commission of 400 kV domasandra station | 2026-05-10 | 09:00 | 2026-05-31 | 23:45 | LC for 400KV SC KOLAR_AC-MYLASANDRA-1 LC from 05.05.2026 to 06.07.2026 (62 days) | Yes | Rejected | Details of works to be taken up along with the present status of the works completed, status of the 400kV Dommasandra SS commisioning with full network shall be informed. Load/Voltage Management and Network rearrangemnt details need to be furnished by KPTCL to ensure Reliable supply to the Banglore system. | Line Circuits | 06-May-2026 | 12:50 | 07-May-2026 | 13:09
RQ107398 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-1 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-10 | 19:00 | 2026-05-10 | 23:59 |  | Yes | Approved | Concurred, subject to real time grid conditions and RE generations. | Line Circuits | 06-May-2026 | 12:25 | 07-May-2026 | 10:45
RQ107406 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-2 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-10 | 19:00 | 2026-05-10 | 23:59 |  | Yes | Approved | Concurred, subject to real time grid conditions and RE generations. | Line Circuits | 06-May-2026 | 12:25 | 07-May-2026 | 10:45
RQ107413 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-1 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-10 | 00:00 | 2026-05-10 | 04:00 |  | Yes | Approved | Concurred, subject to real time grid conditions and RE generations. | Line Circuits | 06-May-2026 | 12:25 | 07-May-2026 | 10:45
RQ107421 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-2 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-10 | 00:00 | 2026-05-10 | 04:00 |  | Yes | Approved | Concurred, subject to real time grid conditions and RE generations. | Line Circuits | 06-May-2026 | 12:25 | 07-May-2026 | 10:45
RQ106644 | OCC_237 | aptransco | 400KV/220KV NELLORE_AP-ICT-3 | APTRANSCO | D | For maintenance Works & MRT Works | 2026-05-10 | 10:00 | 2026-05-10 | 16:00 | Annual maintenance works | Yes | Approved | subject to ICT loading conditions and load management by AP. N-1 limit for NELLORE_AP ICTs is 220 MW for 315 MVA ICT each and 376 MW for 500 MVA ICT. 400KV/220KV NELLORE_AP-ICT-4 31% 400KV/220KV NELLORE_AP-ICT-1 20% 400KV/220KV NELLORE_AP-ICT-2 20% All RACHAGUNNERI ICTs 400KV-RACHAGUNNERI-KRISHNAPATNAM D/C shall be in service. KRISHNAPATTANAM generation need to be managed by AP in order to keep the ICT loadings within their N-1 limit. | Transformer | 06-May-2026 | 10:07 | 07-May-2026 | 14:24
RQ106566 | OCC_237 | aptransco | 132KV-KODADA-CHILLAKALLU-1 | APTRANSCO,TGTRANSCO | D | Stringing of snapped Earth wire from Loc. Nos. 8 to 22, 29 to 36 and clearing of vegetation in various locations from 1 to 41 by CBD Gang | 2026-05-10 | 08:00 | 2026-05-10 | 18:00 | Stringing of snapped Earth wire from Loc. Nos. 8 to 22, 29 to 36 and clearing of vegetation in various locations from 1 to 41 by CBD Gang | Yes | Approved | Load management to be done by AP & TG. Subject to real time grid conditions. | Line Circuits | 06-May-2026 | 10:07 | 07-May-2026 | 11:00
RQ107396 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-1 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-08 | 19:00 | 2026-05-08 | 23:59 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Line Circuits | 06-May-2026 | 09:27 | 05-May-2026 | 10:20
RQ107404 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-2 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-08 | 19:00 | 2026-05-08 | 23:59 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Line Circuits | 06-May-2026 | 09:27 | 05-May-2026 | 10:20
RQ107411 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-1 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-08 | 00:00 | 2026-05-08 | 04:00 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Line Circuits | 06-May-2026 | 09:27 | 05-May-2026 | 10:20
RQ107419 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-2 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-08 | 00:00 | 2026-05-08 | 04:00 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Line Circuits | 06-May-2026 | 09:27 | 05-May-2026 | 10:20
RQ106742 | OCC_237 | KNTL | BUS SECTIONALIZER BAY (211) OF KOPPAL - 220KV - BUS 1 AND KOPPAL - 220KV - BUS 3 @KOPPAL - 220KV | KNTL | D | Yearly Bay equipment testing and preventive maintenance. | 2026-05-09 | 09:00 | 2026-05-09 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 06-May-2026 | 08:57 | 06-May-2026 | 11:26
RQ107071 | OCC_237 | PGCIL SR-2 | 400KV/220KV SOMANAHALLI-ICT-3 | PGCIL SR-2 | D | AMP works of ICT-3 | 2026-05-09 | 09:00 | 2026-05-09 | 15:00 |  | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. N-1 limit for SOMANAHALLI ICTs is 333 MW each. Load Management need to be done by KPTCL. Line loadings of 400kV-SOMANAHALLI-MYLASANDRA need to be monitored continuously. 400KV/220KV SOMANAHALLI-ICT-1 21% 400KV/220KV SOMANAHALLI-ICT-2 21% All MYLASANDRA ICTs and BIDADI ICTs 400KV-MYLASANDRA-SOMANAHALLI-1 22% 400KV-BIDADI_PG-NELAMANGALA D/C shall be in service. Subject to real time grid and voltage conditions. | Transformer | 05-May-2026 | 16:21 | 06-May-2026 | 12:12
RQ107397 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-1 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-09 | 19:00 | 2026-05-09 | 23:59 |  | Yes | Approved | Subject to real time RE generation and grid conditions. | Line Circuits | 05-May-2026 | 15:27 | 06-May-2026 | 11:26
RQ107405 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-2 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-09 | 19:00 | 2026-05-09 | 23:59 |  | Yes | Approved | Subject to real time RE generation and grid conditions. | Line Circuits | 05-May-2026 | 15:27 | 06-May-2026 | 11:26
RQ106932 | OCC_237 | PGCIL SR-1 | A/R of 400KV-GOOTY-RAICHUR_PG-1 | POWERGRID | D | Hot line stringing works 400kV D/C Bethapalle to PGCIL Anantapur Line at Existing 400kV D/C Gooty – Raichur Line, Existing tower no. 365 & 366 - Auto reclosure to be kept in non auto mode | 2026-05-09 | 09:00 | 2026-05-09 | 18:00 | Construction works | No | Rejected | Deferred by requester. | Auto Reclosure | 05-May-2026 | 15:17 | 06-May-2026 | 11:26
RQ106936 | OCC_237 | PGCIL SR-1 | A/R of 400KV-GOOTY-RAICHUR_PG-2 | POWERGRID | D | Hot line stringing works 400kV D/C Bethapalle to PGCIL Anantapur Line at Existing 400kV D/C Gooty – Raichur Line, Existing tower no. 365 & 366 - Auto reclosure to be kept in non auto mode | 2026-05-09 | 09:00 | 2026-05-09 | 18:00 | Construction works | No | Rejected | Deferred by requester. | Auto Reclosure | 05-May-2026 | 15:17 | 06-May-2026 | 11:26
RQ106966 | OCC_237 | TGTRANSCO | 400KV/220KV DINDI-ICT-1 | TGTRANSCO | C | General and periodical maintenance to be done by both Maintenance and TRE wings | 2026-05-09 | 10:00 | 2026-05-09 | 17:00 |  | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. Load Management need to be done by TG. N-1 limit for DINDI ICTs is 238 MW each. 400KV/220KV DINDI-ICT-2 25% All MEHBOOBNAGAR and NAGARJUNASAGAR ICTs shall be in service. | Transformer | 05-May-2026 | 13:40 | 06-May-2026 | 11:56
RQ106833 | OCC_237 | kptcl | 400KV-PAVAGADA_PG-BPS-2 | POWERGRID | D | Replacement of damaged polymer insulator at location no. 61 of 400KV BPS-Pavagda line-2 | 2026-05-09 | 08:00 | 2026-05-09 | 18:00 | Maintenance work, Shut down of BPS Jagalur 2 also required due to multitower circuit . HENCE OUTAGE REQUIRED ON BOTH LINES | Yes | Rejected | Subject to real time grid conditions. SPS for 400kV BPS-Pavagada contingency - Jindal Concurrence needs to be submitted prior to the shutdown. SPS- stage -2 need to be in service. Stage-I SPS need to be disbaled. 400KV-PAVAGADA_PG-BPS-1 and 220kV lines in downstream shall be in service, | Line Circuits | 05-May-2026 | 12:38 | 06-May-2026 | 11:32
RQ106850 | OCC_237 | kptcl | 400KV-BPS-JAGALUR-2 | KPTCL | D | Replacement of damaged polymer insulator at location no. 61 of 400KV BPS-Pavagda line-2 | 2026-05-09 | 08:00 | 2026-05-09 | 18:00 | Maintenance work,Shut down of Pavagada BPS 2 also required due to multitower circuit . HENCE OUTAGE REQUIRED ON BOTH LINES | Yes | Rejected | No N-1 for 400kV JAGALUR S/S. Subject to real time grid conditions. SPS for 400kV BPS-Pavagada contingency - Jindal Concurrence needs to be submitted prior to the shutdown. SPS- stage -2 need to be in service. Stage-I SPS need to be disbaled. 400KV-PAVAGADA_PG-BPS-1 and 220kV lines in downstream shall be in service, | Line Circuits | 05-May-2026 | 12:38 | 06-May-2026 | 11:32
RQ106826 | OCC_237 | kptcl | 400KV-NELAMANGALA-HASSAN-1 | KPTCL | D | Emergency tree cutting in the Loc no: 696,712,727,751,756. | 2026-05-09 | 08:00 | 2026-05-09 | 18:00 | Maintenance work | Yes | Approved | 400KV-MYSORE-HASSAN D/C 37% each 400KV-MYSORE-NELAMANGALA D/C 23% each 400KV-MYSORE-HIRIYUR-1 12% 400KV-TALGUPPA-NELAMANGALA-1 11% 400KV-TALGUPPA-HASSAN-1 10% 400KV-PAVAGADA_PG-MYSORE-1 8% shall be in service. | Line Circuits | 05-May-2026 | 12:38 | 06-May-2026 | 11:56
RQ108599 | PNOCC | aptransco | 220KV-CHITTOOR_AP-THIRUVALAM_TN-1 | APTRANSCO,TANTRANSCO | C | for Power Relay replacement due to non- availability of Time-Sync | 2026-05-09 | 10:00 | 2026-05-09 | 15:30 | (as per SRLDC recommendation) & During the above period there will be no interruption to any loads. | Yes | Approved | Element under idle charged condition. Concurred, subject to real time grid conditions. | Line Circuits | 05-May-2026 | 10:44 | 06-May-2026 | 11:51
RQ106757 | OCC_237 | aptransco | 400KV-NARNOOR-JAMMALAMADUGU-2 | APTRANSCO | D | For PMI defects rectification from loc.No.236-239. | 2026-05-09 | 07:00 | 2026-05-09 | 12:00 | Annual maintenance works | Yes | Approved | 400KV-JAMMALAMADUGU-NARNOOR-1 60% 400KV-TALARCHEVU-JAMMALAMADUGU D/C 17% each 400KV-TALARCHEVU-URAVAKONDA D/C 17% each 400KV-HINDUPUR-URAVAKONDA-1 7% 400KV-YEDULA-DINDI-2 6% shall be in service. | Line Circuits | 05-May-2026 | 10:38 | 06-May-2026 | 11:51
RQ107410 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-1 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-07 | 00:00 | 2026-05-07 | 04:00 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Line Circuits | 05-May-2026 | 10:26 | 04-May-2026 | 12:14
RQ107418 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-2 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-07 | 00:00 | 2026-05-07 | 04:00 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Line Circuits | 05-May-2026 | 10:26 | 04-May-2026 | 12:14
RQ106770 | OCC_237 | MTL | A/R of 400KV-NIZAMABAD-SHANKARAPALLY-1 | MTL | D | Required A/R in Non auto mode for defect rectification work | 2026-05-08 | 09:00 | 2026-05-08 | 17:00 | A/R OFF | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 05-May-2026 | 08:39 | 05-May-2026 | 10:30
RQ106740 | OCC_237 | KNTL | BUS COUPLER BAY (209) OF KOPPAL - 220KV - BUS 1 AND KOPPAL - 220KV - BUS 2 @KOPPAL - 220KV | KNTL | D | Yearly Bay equipment testing and preventive maintenance. | 2026-05-08 | 09:00 | 2026-05-08 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 05-May-2026 | 08:35 | 05-May-2026 | 10:30
RQ106492 | OCC_237 | kseb | A/R of 220KV-KOCHI-KALAMASSERY-2 | KSEB | D | Disc replacement work | 2026-05-08 | 09:00 | 2026-05-08 | 17:00 | Disc replacement work | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 05-May-2026 | 01:32 | 05-May-2026 | 10:30
RQ106714 | OCC_237 | TANTRANSCO | 400KV-TIRUNELVELI-KANARPATTI-1 | TANTRANSCO | D | Monthly Maintenance Work | 2026-05-08 | 15:00 | 2026-05-08 | 20:00 |  | Yes | Approved | Shutdown to be availed only after 16:00 HRS. Load Management need to be done by TN. 400KV-KAYATHAR-KARAIKUDI-1 21% 400KV-KAYATHAR-KARAIKUDI-2 21% 400KV-TUTICORIN_PS-TIRUNELVELI-1 18% 400KV-KARAIKUDI-MADURAI_PG-1 17% 230KV-KAYATHAR(TN)-TIRUNELVELI-1 14% 400KV-VELLALAVIDUTHI-KARAIKUDI-1 12% 400KV-PUGALUR-KARAIKUDI-1 12% 400KV-KARAIKUDI-TRICHY-1 12% shall be in service. | Line Circuits | 04-May-2026 | 23:30 | 05-May-2026 | 10:49
RQ106919 | OCC_237 | PGCIL SR-1 | SRIKAKULAM - 765KV - BUS 2 | PGCIL SR-1 | D | 765KV BUS BAR PROTECTION TESTING WORKS | 2026-05-08 | 08:00 | 2026-05-08 | 18:00 | AMP works. | No | Rejected | Deferred by requester. | Bus | 04-May-2026 | 16:20 | 05-May-2026 | 10:20
RQ106931 | OCC_237 | PGCIL SR-1 | A/R of 400KV-GOOTY-RAICHUR_PG-1 | POWERGRID | D | Hot line stringing works 400kV D/C Bethapalle to PGCIL Anantapur Line at Existing 400kV D/C Gooty – Raichur Line, Existing tower no. 365 & 366 - Auto reclosure to be kept in non auto mode | 2026-05-08 | 09:00 | 2026-05-08 | 18:00 | Construction works | No | Rejected | Deferred by requester. | Auto Reclosure | 04-May-2026 | 16:20 | 05-May-2026 | 10:20
RQ106935 | OCC_237 | PGCIL SR-1 | A/R of 400KV-GOOTY-RAICHUR_PG-2 | POWERGRID | D | Hot line stringing works 400kV D/C Bethapalle to PGCIL Anantapur Line at Existing 400kV D/C Gooty – Raichur Line, Existing tower no. 365 & 366 - Auto reclosure to be kept in non auto mode | 2026-05-08 | 09:00 | 2026-05-08 | 18:00 | Construction works | No | Rejected | Deferred by requester. | Auto Reclosure | 04-May-2026 | 16:20 | 05-May-2026 | 10:20
RQ108590 | PNOCC | NPCIL | 220KV-KAIGA-KADRA-1 | KPTCL | C | Preventive maintenance work of bay equipment | 2026-05-08 | 08:00 | 2026-05-09 | 20:00 | Line outage required for 3 days i.e. up to 10/05/2026, 20.00hrs. | Yes | Rejected | Planned Activities to be taken into Main OCC. Prior SRPC approval is required for any PNOCC shutdown exceeding more than two days as per SRPC outage planning procedure. | Line Circuits | 04-May-2026 | 12:41 | 05-May-2026 | 10:34
RQ108591 | PNOCC | NPCIL | KAIGA - 220KV - BUS 1 | NPCIL_KAIGA | C | Replacement of String insulators and preventive maintenance | 2026-05-08 | 08:00 | 2026-05-09 | 20:00 | Preventive maintenance | Yes | Rejected | Planned Activities to be taken into Main OCC. | Bus | 04-May-2026 | 12:47 | 05-May-2026 | 10:34
RQ107038 | OCC_237 | PGCIL SR-2 | 220KV-PAVAGADA_PG-RYCHALU1 | KSPDCL | D | AMP of Terminal Equipments | 2026-05-08 | 18:00 | 2026-05-08 | 23:59 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Line Circuits | 04-May-2026 | 14:42 | 05-May-2026 | 10:37
RQ107070 | OCC_237 | PGCIL SR-2 | 400KV/220KV KOCHI-ICT-2 | PGCIL SR-2 | D | AMP works of ICT-2 | 2026-05-08 | 09:00 | 2026-05-08 | 15:00 |  | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. Load Management need to be done by KSEB. N-1 limit for KOCHI ICTs is 208 MW for 315 MVA ICT each and 330 MW for 500 MVA ICT each. 400KV/220KV KOCHI-ICT-3 38% 400KV/220KV KOCHI-ICT-2 24% All KOTTAYAM and MADAKKATHARA ICTs 400KV-KOCHI-THRISSUR HVDC D/C 400KV-THRISSUR HVDC-TRICHUR D/C shall be in service. | Transformer | 04-May-2026 | 14:42 | 05-May-2026 | 10:37
RQ106816 | OCC_237 | kptcl | MAIN BAY (409) OF 400KV/220KV NELAMANGALA-ICT-2 AND NELAMANGALA - 400KV - BUS 2 @NELAMANGALA - 400KV | KPTCL | D | Breaker testing and maintenance works. | 2026-05-08 | 11:00 | 2026-05-08 | 17:00 |  | No | Rejected | Deferred by requester. | Bay | 04-May-2026 | 12:11 | 05-May-2026 | 10:20
RQ106832 | OCC_237 | kptcl | 400KV-PAVAGADA_PG-BPS-1 | POWERGRID | D | Replacement of damaged polymer insulator at location no. 61 of 400KV BPS-Pavagda line-1 | 2026-05-08 | 08:00 | 2026-05-08 | 18:00 | Maintenance workMaintenance work,Shut down of BPS Jagalur 1 also required due to multitower circuit . HENCE OUTAGE REQUIRED ON BOTH LINES | Yes | Rejected | Subject to real time grid conditions. SPS for 400kV BPS-Pavagada contingency - Jindal Concurrence needs to be submitted prior to the shutdown. SPS- stage -2 need to be in service. Stage-I SPS need to be disbaled. 400KV-PAVAGADA_PG-BPS-2 and 220kV lines in downstream shall be in service, | Line Circuits | 04-May-2026 | 12:05 | 05-May-2026 | 11:04
RQ106849 | OCC_237 | kptcl | 400KV-BPS-JAGALUR-1 | KPTCL | D | Replacement of damaged polymer insulator at location no. 61 of 400KV BPS-Pavagda line-1 | 2026-05-08 | 08:00 | 2026-05-08 | 18:00 | Maintenance work,Shut down of Pavagada BPS 1 also required due to multitower circuit . HENCE OUTAGE REQUIRED ON BOTH LINES | Yes | Rejected | No N-1 for 400kV JAGALUR S/S. Subject to real time grid conditions. SPS for 400kV BPS-Pavagada contingency - Jindal Concurrence needs to be submitted prior to the shutdown. SPS- stage -2 need to be in service. Stage-I SPS need to be disbaled. 400KV-PAVAGADA_PG-BPS-2 and 220kV lines in downstream shall be in service, | Line Circuits | 04-May-2026 | 12:02 | 05-May-2026 | 11:04
RQ106830 | OCC_237 | kptcl | 400KV-JINDAL-BPS-4 | KPTCL | D | Quarterly Maintenance & DCRM Testing | 2026-05-08 | 10:00 | 2026-05-08 | 17:00 | Quarterly Maintenance & DCRM Testing | Yes | Rejected | Multiple shutdowns at the same station. | Line Circuits | 04-May-2026 | 11:37 | 05-May-2026 | 11:04
RQ106554 | OCC_237 | aptransco | 400KV/220KV CHITTOOR-ICT-3 | APTRANSCO | D | hot lines wing had conducted thermo vision scanning on 14.02.2026 and reported hot spots with temperature of 850C at LV CB jumper clamp and CT stud clamp at LV Isolator pad clamp (Y & B phases) of ICT-3 | 2026-05-08 | 17:00 | 2026-05-08 | 19:00 | for attending hot line remarks | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. Load Management need to be done by AP. N-1 limit for CHITTOOR ICTs is 230 MW each. 400KV/220KV CHITTOOR-ICT-1 30% 400KV/220KV CHITTOOR-ICT-3 30% All KALIKIRI and RACHAGUNNERI ICTs shall be in service along with 400KV-KALIKIRI-CHITTOOR D/C. | Transformer | 04-May-2026 | 10:11 | 05-May-2026 | 10:42
RQ106440 | OCC_237 | TANTRANSCO | 400KV/230KV PULIYANTHOPE-ICT-1 | TANTRANSCO | D | Monthly Maintenance Work | 2026-05-08 | 09:00 | 2026-05-08 | 17:00 |  | No | Rejected | Deferred by requester. | Transformer | 04-May-2026 | 10:08 | 05-May-2026 | 10:20
RQ106493 | OCC_237 | kseb | A/R of 220KV-KOCHI-KALAMASSERY-1 | KSEB | D | Disc replacement work | 2026-05-06 | 09:00 | 2026-05-06 | 17:00 | Disc replacement work | No | Approved | Availing status confirmed through mail. Concurred subject to real time grid conditions. | Auto Reclosure | 04-May-2026 | 09:30 | 03-May-2026 | 11:39
RQ106524 | OCC_237 | kseb | 220KV-ELAPULLY-MADAKATHARA-1 | KSEB | D | For replacing porcelain disc insulator with polymer insulator and jumper tightening. | 2026-05-06 | 08:00 | 2026-05-06 | 17:00 | For replacing porcelain disc insulator with polymer insulator and jumper tightening. | No | Approved | Availing status confirmed through mail. 220KV-PALAKKAD(KL)-MADAKATHARA-1 27% 400KV-MADAKKATHARA-TRICHUR D/C 26% each 400KV-PALAKKAD-TRICHUR D/C 26% each 220KV-ELAPULLY-PALAKKAD(KL)-1,2,3 400KV/220KV MADAKATHARA-ICT-1,2,3 16% each and All KOZHIKODE ICTs shall be in service. | Line Circuits | 04-May-2026 | 09:30 | 03-May-2026 | 11:39
RQ107394 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-1 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-06 | 19:00 | 2026-05-06 | 23:59 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Line Circuits | 04-May-2026 | 09:30 | 03-May-2026 | 11:39
RQ107402 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-2 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-06 | 19:00 | 2026-05-06 | 23:59 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Line Circuits | 04-May-2026 | 09:30 | 03-May-2026 | 11:39
RQ107409 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-1 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-06 | 00:00 | 2026-05-06 | 04:00 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Line Circuits | 04-May-2026 | 09:30 | 03-May-2026 | 11:39
RQ107417 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-2 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-06 | 00:00 | 2026-05-06 | 04:00 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Line Circuits | 04-May-2026 | 09:30 | 03-May-2026 | 11:39
RQ106739 | OCC_237 | KNTL | MAIN BAY (418) OF 400KV-GADAG_PSS-KOPPAL-2 AND KOPPAL - 400KV - BUS 1 @KOPPAL - 400KV | GADAG_II_A | D | Yearly Bay equipment testing and preventive maintenance. | 2026-05-07 | 09:00 | 2026-05-07 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 04-May-2026 | 08:37 | 04-May-2026 | 12:22
RQ106769 | OCC_237 | MTL | A/R of 400KV-NIZAMABAD-SHANKARAPALLY-1 | MTL | D | Required A/R in Non auto mode for defect rectification work | 2026-05-07 | 09:00 | 2026-05-07 | 17:00 | A/R OFF | No | Rejected | Deferred by requester. | Auto Reclosure | 04-May-2026 | 08:21 | 04-May-2026 | 12:14
RQ106373 | OCC_237 | TANTRANSCO | 400KV/230KV KAMUDHI-ICT-2 | TANTRANSCO | D | Monthly Maintenance Work | 2026-05-07 | 16:00 | 2026-05-07 | 21:00 |  | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. Load Management need to be done by TN. N-1 limit for KAMUDHI ICTs is 211 MW each. 400KV/230KV KAMUDHI-ICT-1 100% shall be in service. | Transformer | 03-May-2026 | 23:15 | 04-May-2026 | 12:43
RQ106484 | OCC_237 | TANTRANSCO | 400KV/110KV THAPPUKUNDU-ICT-4 | TANTRANSCO | D | Monthly Maintenance work | 2026-05-07 | 09:00 | 2026-05-07 | 15:00 |  | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. Load Management need to be done by TN. | Transformer | 03-May-2026 | 23:15 | 04-May-2026 | 12:22
RQ106556 | OCC_237 | TANTRANSCO | MAIN BAY (403) OF 400KV-TIRUNELVELI-KANARPATTI-2 AND KANARPATTI - 400KV - BUS 1 @KANARPATTI - 400KV | TANTRANSCO | D | Monthly Maintenance Work | 2026-05-07 | 09:00 | 2026-05-07 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. Other element in dia (400KV-TIRUNELVELI-KANARPATTI-2) is future element. Approved along with Tie Bay. | Bay | 03-May-2026 | 23:15 | 04-May-2026 | 12:28
RQ106557 | OCC_237 | TANTRANSCO | TIE BAY (402) OF 400KV-TIRUNELVELI-KANARPATTI-1 AND 400KV-TIRUNELVELI-KANARPATTI-2 @KANARPATTI - 400KV | TANTRANSCO | D | Monthly Maintenance Work | 2026-05-07 | 09:00 | 2026-05-07 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. Other element in dia (400KV-TIRUNELVELI-KANARPATTI-2) is future element. Approved along with Main Bay. | Bay | 03-May-2026 | 23:15 | 04-May-2026 | 12:28
RQ107395 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-1 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-07 | 19:00 | 2026-05-07 | 23:59 |  | Yes | Approved | Concurred, subject to real time RE generation and grid conditions. | Line Circuits | 03-May-2026 | 21:28 | 04-May-2026 | 12:28
RQ107403 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-2 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-07 | 19:00 | 2026-05-07 | 23:59 |  | Yes | Approved | Concurred, subject to real time RE generation and grid conditions. | Line Circuits | 03-May-2026 | 21:28 | 04-May-2026 | 12:28
RQ106899 | OCC_237 | PGCIL SR-1 | 400KV-NELLORE_AP-VTPS_IV-1 | POWERGRID | D | amp works | 2026-05-07 | 09:00 | 2026-05-07 | 18:00 | AMP works. | Yes | Approved | 400KV-VTPS_IV-VIJAYAWADA-1 51% 400KV-SATTENPALLY-VTPS_IV-1 17% 400KV-NELLORE_AP-VIJAYAWADA-3 14% 400KV-VIJAYAWADA-NELLORE_PG-1 14% 400KV-VIJAYAWADA-NELLORE_PG-2 14% 400KV-KRISHNAPATNAM-NELLORE_AP-1 10% 400KV-SEILU2_AP-NELLORE_AP-1 9% shall be in service. | Line Circuits | 03-May-2026 | 15:34 | 04-May-2026 | 15:39
RQ106930 | OCC_237 | PGCIL SR-1 | A/R of 400KV-GOOTY-RAICHUR_PG-1 | POWERGRID | D | Hot line stringing works 400kV D/C Bethapalle to PGCIL Anantapur Line at Existing 400kV D/C Gooty – Raichur Line, Existing tower no. 365 & 366 - Auto reclosure to be kept in non auto mode | 2026-05-07 | 09:00 | 2026-05-07 | 18:00 | Construction works | No | Rejected | Deferred by requester. | Auto Reclosure | 03-May-2026 | 15:34 | 04-May-2026 | 12:14
RQ106934 | OCC_237 | PGCIL SR-1 | A/R of 400KV-GOOTY-RAICHUR_PG-2 | POWERGRID | D | Hot line stringing works 400kV D/C Bethapalle to PGCIL Anantapur Line at Existing 400kV D/C Gooty – Raichur Line, Existing tower no. 365 & 366 - Auto reclosure to be kept in non auto mode | 2026-05-07 | 09:00 | 2026-05-07 | 18:00 | Construction works | No | Rejected | Deferred by requester. | Auto Reclosure | 03-May-2026 | 15:34 | 04-May-2026 | 12:14
RQ106962 | OCC_237 | TGTRANSCO | 400KV/220KV CHOUTUPPAL-ICT-1 | TGTRANSCO | C | For periodical testing and general maintenance | 2026-05-07 | 10:00 | 2026-05-07 | 18:00 |  | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. Load Management need to be done by TG. N-1 limit for CHOUTUPPAL ICTs is 319 MW each. 400KV/220KV CHOUTUPPAL-ICT-2 36% All DAMARCHERLA ICTs 220KV-SURYAPET-NARKETPALLY-1 23% 400KV-CHOUTUPPAL-MAMIDAPALLI D/C 13% each shall be in service. | Transformer | 03-May-2026 | 14:21 | 04-May-2026 | 15:39
RQ107014 | OCC_237 | TGTRANSCO | 400KV-YADADRI TPP-DAMARCHERLA-2 | TGTRANSCO | C | for Testing and Inspection of Line Protection Relays | 2026-05-07 | 09:00 | 2026-05-07 | 18:00 |  | Yes | Approved | 400KV-YADADRI TPP-DAMARCHERLA-1 98% shall be in service. Line loading to be within 50% of its thermal rating. | Line Circuits | 03-May-2026 | 14:21 | 04-May-2026 | 12:58
RQ107019 | OCC_237 | TGTRANSCO | 400KV-SRISAILAM_LEFT_BANK-DINDI-2 | TGTRANSCO | C | Annual Maintenance works at 400KV OD YARD- overhauling of operating mechanism box and cleaning of the contacts of isolator and earth switch,cleaning of porcelin insulators, replacement LS and Realy testing work | 2026-05-07 | 06:00 | 2026-05-08 | 17:00 |  | Yes | Approved | 400KV-DINDI-SRISAILAM_LEFT_BANK-1 51% 400KV-SRISAILAM_LEFT_BANK-NARNOOR-1 24% 400KV-SATTENPALLY-VTPS_IV-1 6% 400KV-CHOUTUPPAL-YADADRI TPP D/C 400KV-CHILAKALURIPETA-SATTENPALLY D/C All C'PETA ICTs shall be in service. | Line Circuits | 03-May-2026 | 14:21 | 04-May-2026 | 13:03
RQ107049 | OCC_237 | PGCIL SR-2 | 400KV-HOSUR_PG-KOLAR_AC-2 | POWERGRID | D | AMP Works and attending shutdown nature defects in the line. | 2026-05-07 | 09:00 | 2026-05-07 | 17:00 |  | Yes | Rejected | Severe low voltages are observed at 400kV HOSUR_PG S/S. The said shutdown will further worsen the voltage profile. Thus shutdown to be availed during nominal voltage conditions. 400KV-HOSUR_PG-KOLAR_AC-1 46% 400KV-HOSUR_PG-SOMANAHALLI-1 14% 400KV-KOLAR_AC-HOODY D/C 13% each 400KV-MYLASANDRA-KOLAR_AC-1 12% 400KV-HOSUR_PG-SALEM D/C 10% each 400KV-DEVANAHALLI-NELAMANGALA-1 7% All PALAVADI and HOODY ICTs shall be in service. Subject to real time grid conditions. | Line Circuits | 03-May-2026 | 13:42 | 04-May-2026 | 15:57
RQ106812 | OCC_237 | kptcl | DEVANAHALLI - 400KV B/R 1 | KPTCL | D | quarterly maintenance work | 2026-05-07 | 08:00 | 2026-05-07 | 18:00 | The reactor is usually in off condition during the day time | Yes | Approved | Concurred, subject to real time grid conditions. | Bus Reactor | 03-May-2026 | 12:20 | 04-May-2026 | 12:22
RQ106647 | OCC_237 | aptransco | 400KV/220KV PODILI-ICT-3 | APTRANSCO | D | FOR PERIODICAL MAINTENANCE AND MRT WORKS | 2026-05-07 | 09:00 | 2026-05-07 | 17:00 | Annual maintenance works | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. Load Management need to be done by AP. 400KV/220KV PODILI-ICT-1 30% 400KV/220KV PODILI-ICT-2 30% All SATTENPALLY and NELLORE AP ICTs shall be in service. N-1 limit for PODILI ICTs is 232 MW each. | Transformer | 03-May-2026 | 11:11 | 04-May-2026 | 12:58
RQ106649 | OCC_237 | aptransco | 400KV/220KV NARNOOR-ICT-2 | APTRANSCO | D | For Annualy and Quarterly maintenance works(for ICT Testings) | 2026-05-07 | 10:00 | 2026-05-07 | 16:00 | Annual maintenance works | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. Load Management need to be done by AP. N-1 limit for 400KV/220KV NARNOOR-ICTs is 200 MW for 315 MVA ICT each and 316 MW for 500 MVA ICT. 400KV/220KV NARNOOR-ICT-1 34% 400KV/220KV NARNOOR-ICT-3 34% All GOOTY ICTs shall be in service along with 400kV-GOOTY-NARNOOR. | Transformer | 03-May-2026 | 11:11 | 04-May-2026 | 13:03
RQ106783 | OCC_237 | aptransco | 400KV/220KV HINDUPUR-ICT-2 | APTRANSCO | C | Temporary diversion of 315 MVA ICT-II from 400/220KV SS Hindupur to 400/220KV SS Gudivada. | 2026-05-07 | 16:01 | 2026-05-15 | 18:00 | 315 MVA ICT - II will be diverted to 400KV SS Gudivada. ICT HV Bays 408,409 bays will be taken into service and LV Bay 206 will be in off condition after dismantling work completion. | Yes | Approved | All the necessary approval related documents received. Load Management need to be done by AP. N-1 limit for HINDUPUR ICTs is 238 MW each. 400KV/220KV HINDUPUR-ICT-1,3,4 26% each shall be in service. ICT will be removed until commissioning of NEW ICT at 400kV HINDUPUR S/S. | Transformer | 03-May-2026 | 11:11 | 04-May-2026 | 12:43
RQ106790 | OCC_237 | aptransco | 400KV-TALARCHEVU-JAMMALAMADUGU-1 | APTRANSCO | D | In order to carry out the rectification of spacer keeper pieces between Loc.Nos. 31 to 32. | 2026-05-07 | 08:00 | 2026-05-07 | 16:00 | In order to carry out the rectification of spacer keeper pieces between Loc.Nos. 31 to 32. | Yes | Approved | 400KV-TALARCHEVU-JAMMALAMADUGU-2 84% 400KV-JAMMALAMADUGU-NARNOOR D/C 7% each 400KV-KURNOOL_PG-NARNOOR D/C shall be in service. | Line Circuits | 03-May-2026 | 11:11 | 04-May-2026 | 12:43
RQ106632 | OCC_237 | aptransco | TALARCHERUVU - 400KV B/R 1 | APTRANSCO | D | FOR PERIODICAL MAINTENANCE AND MRT TESTINGS | 2026-05-07 | 09:00 | 2026-05-07 | 16:00 | Annual maintenance works | Yes | Approved | Concurred, subject to real time grid conditions. | Bus Reactor | 03-May-2026 | 11:11 | 04-May-2026 | 12:22
RQ106681 | OCC_237 | aptransco | TIE BAY (402) OF 400KV-RAYALSEEMA TPP-KALIKIRI-2 AND KALIKIRI - 400KV B/R 1 @KALIKIRI - 400KV | APTRANSCO | D | CTs Tan Delta & Maintenance works | 2026-05-07 | 10:00 | 2026-05-07 | 17:00 | Annual maintenance works | Yes | Approved | Remaining bays shall be in service. | Bay | 03-May-2026 | 11:11 | 04-May-2026 | 12:22
RQ106803 | OCC_237 | aptransco | 220KV-ASUPAKA-LOWER_SILERU-1 | APTRANSCO,TGTRANSCO | D | Emergency tree cutting at location no 285 to 286 and at location no 145 to 146 | 2026-05-07 | 10:00 | 2026-05-07 | 17:00 | Emergency tree cutting at location no 285 to 286 and at location no 145 to 146 | Yes | Approved | Load and generation management need to be done by AP and TG. Healthiness of 220kV-Lower Sileru - Chintoor - BG_Kothur shall be ensured prior to the shutdown. 220KV-BGKOTHUR-CHINTOOR-1 100% 220KV-CHINTOOR-LOWER_SILERU-1 100% 220KV-BGKOTHUR-KOTHAGUDEM_TPS-1 38% 220KV-BGKOTHUR-KTS_V-1 37% 220KV-BGKOTHUR-MANUGURU-1 30% shall be in service. Subject to real time grid conditions, line loadings and hydro generation requirements. | Line Circuits | 03-May-2026 | 11:11 | 04-May-2026 | 12:22
RQ107393 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-1 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-05 | 19:00 | 2026-05-05 | 23:59 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Line Circuits | 03-May-2026 | 09:48 | 02-May-2026 | 17:45
RQ107401 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-2 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-05 | 19:00 | 2026-05-05 | 23:59 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Line Circuits | 03-May-2026 | 09:48 | 02-May-2026 | 17:45
RQ107408 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-1 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-05 | 00:00 | 2026-05-05 | 04:00 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Line Circuits | 03-May-2026 | 09:48 | 02-May-2026 | 17:45
RQ107416 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-2 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-05 | 00:00 | 2026-05-05 | 04:00 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Line Circuits | 03-May-2026 | 09:48 | 02-May-2026 | 17:45
RQ106768 | OCC_237 | MTL | A/R of 400KV-NIZAMABAD-SHANKARAPALLY-1 | MTL | D | Required A/R in Non auto mode for defect rectification work | 2026-05-06 | 09:00 | 2026-05-06 | 17:00 | A/R OFF | No | Rejected | Deferred by requester. | Auto Reclosure | 03-May-2026 | 08:51 | 03-May-2026 | 11:39
RQ106738 | OCC_237 | KNTL | TIE BAY (417) OF 400KV-GADAG_PSS-KOPPAL-2 AND FUTURE @KOPPAL - 400KV | GADAG_II_A | D | "Yearly Bay equipment testing and preventive maintenance. " | 2026-05-06 | 09:00 | 2026-05-06 | 18:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 03-May-2026 | 08:48 | 03-May-2026 | 12:29
RQ108269 | PNOCC | NPCIL | 230KV-KUDANKULAM-KUDANKULAM 3&amp;4-1 | KKNPP | C | Due to ongoing construction activities in KK34, heavy dust deposition is there on the insulators. Cleaning to be done urgently as corona discharge is observed. | 2026-05-10 | 00:00 | 2026-05-11 | 23:59 | Total six towers are there to be cleaned, there fore six days shut down required upto 11.05.2026 | Yes | Rejected | Shutdown already ongoing under emergency. For any planned extension beyond two days, prior SRPC approval is required. | Line Circuits | 02-May-2026 | 17:16 | 07-May-2026 | 13:16
RQ108265 | PNOCC | NPCIL | 230KV-KUDANKULAM-KUDANKULAM 3&amp;4-1 | KKNPP | C | Due to ongoing construction activities in KK34, heavy dust deposition is there on the insulators. Cleaning to be done urgently as corona discharge is observed. | 2026-05-08 | 00:00 | 2026-05-09 | 23:59 | Total six towers are there to be cleaned, there fore six days shut down required up to 11.05.2026. | Yes | Rejected | Prior SRPC approval is required for any PNOCC shutdown exceeding more than two days as per SRPC outage planning procedure. | Line Circuits | 02-May-2026 | 16:58 | 05-May-2026 | 10:34
RQ108263 | PNOCC | NPCIL | 230KV-KUDANKULAM-KUDANKULAM 3&amp;4-1 | KKNPP | C | Due to ongoing construction activities in KK34, heavy dust deposition is there on the insulators. Cleaning to be done urgently as corona discharge is observed. | 2026-05-06 | 08:00 | 2026-05-07 | 23:59 | Total six towers are there to be cleaned, there fore six days shut down required up to 11.05.2026. | Yes | Rejected | SRPC approval is required for any shutdown exceeding beyond two days. | Line Circuits | 02-May-2026 | 16:45 | 03-May-2026 | 12:42
RQ106893 | OCC_237 | PGCIL SR-1 | 220KV-WARANGAL-NAGARAM-2 | TGTRANSCO | D | AMP | 2026-05-06 | 09:30 | 2026-05-06 | 17:30 | AMP works. | No | Rejected | Deferred by requester. | Line Circuits | 02-May-2026 | 16:45 | 03-May-2026 | 11:39
RQ106978 | OCC_237 | TGTRANSCO | 400KV/220KV JANAGAON-ICT-2 | TGTRANSCO | C | Yearly MAINTENANCE & Testing OF ICT,Relays & BAY equipment. | 2026-05-06 | 08:00 | 2026-05-06 | 18:00 |  | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. Load Management need to be done by TG. N-1 limit for JANAGAON ICTs is 364 MW each. 400KV/220KV JANAGAON-ICT-1 28% 400KV/220KV JANAGAON-ICT-3 28% All KHAMMAM and MALKARAM ICTs shall be in service. | Transformer | 02-May-2026 | 15:59 | 03-May-2026 | 12:42
RQ107000 | OCC_237 | TGTRANSCO | TIE BAY (405) OF 400KV-TIPPAPUR-CHANDALAPUR-2 AND 400KV-TIPPAPUR-TIPPAPUR-CONS-2 @TIPPAPUR - 400KV | TGTRANSCO | C | Periodical testing of bay equipment | 2026-05-06 | 10:00 | 2026-05-06 | 16:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. Load Management need to be done by TG in case of any contingency. | Bay | 02-May-2026 | 15:59 | 03-May-2026 | 12:33
RQ107001 | OCC_237 | TGTRANSCO | MAIN BAY (406) OF 400KV-TIPPAPUR-TIPPAPUR-CONS-2 AND TIPPAPUR - 400KV - BUS 2 @TIPPAPUR - 400KV | TGTRANSCO | C | Periodical testing of bay equipment | 2026-05-06 | 10:00 | 2026-05-06 | 16:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. Load Management need to be done by TG in case of any contingency. | Bay | 02-May-2026 | 15:59 | 03-May-2026 | 12:33
RQ107002 | OCC_237 | TGTRANSCO | MAIN BAY (46M) OF 400KV-TIPPAPUR-TIPPAPUR-CONS-2 AND TIPPAPUR-CONS - 400KV - BUS 1 @TIPPAPUR-CONS - 400KV | TGTRANSCO | C | Periodical testing of bay equipment | 2026-05-06 | 10:00 | 2026-05-06 | 16:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. Load Management need to be done by TG in case of any contingency. | Bay | 02-May-2026 | 15:59 | 03-May-2026 | 12:33
RQ107043 | OCC_237 | PGCIL SR-2 | 400KV-HOSUR_PG-SOMANAHALLI-1 | POWERGRID | D | AMP Works and attending shutdown nature defects in the line. | 2026-05-06 | 09:00 | 2026-05-06 | 17:00 |  | Yes | Rejected | Severe low voltages are observed at 400kV SOMANAHALLI S/S and 400kV HOSUR S/S. Shutdown may be availed during weekend (Sunday) subject to no other overlapping shutdown or during nominal voltage condition. 400KV-HOSUR_PG-KOLAR_AC D/C 28% each 400KV-MYLASANDRA-SOMANAHALLI-1 22% 400KV-HOSUR_PG-SALEM D/C 14% each 400KV-DHARMAPURI-SALEM D/C 12% each All SOMANAHALLI ICTs shall be in service. Subject to real time grid and voltage conditions. | Line Circuits | 02-May-2026 | 13:53 | 04-May-2026 | 10:34
RQ107069 | OCC_237 | PGCIL SR-2 | 400KV/220KV KOCHI-ICT-1 | PGCIL SR-2 | D | AMP works of ICT-1 | 2026-05-06 | 09:00 | 2026-05-06 | 15:00 |  | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. Load Management need to be done by KSEB. N-1 limit for KOCHI ICTs is 208 MW for 315 MVA ICT each and 330 MW for 500 MVA ICT each. 400KV/220KV KOCHI-ICT-3 38% 400KV/220KV KOCHI-ICT-2 24% All KOTTAYAM and MADAKKATHARA ICTs 400KV-KOCHI-THRISSUR HVDC D/C 400KV-THRISSUR HVDC-TRICHUR D/C shall be in service. | Transformer | 02-May-2026 | 13:53 | 03-May-2026 | 12:42
RQ107035 | OCC_237 | PGCIL SR-2 | 220KV-PAVAGADA_PG-KSPDCL3 | KSPDCL | D | AMP of Terminal Equipments | 2026-05-06 | 18:00 | 2026-05-06 | 23:59 |  | Yes | Approved | subject to real time grid conditions. | Line Circuits | 02-May-2026 | 13:53 | 03-May-2026 | 12:20
RQ106445 | OCC_237 | TANTRANSCO | 230KV-PUGALUR-PARAMATHY-1 | TANTRANSCO | D | BKR Mtce & Line Inspection Work | 2026-05-06 | 09:00 | 2026-05-06 | 17:00 |  | Yes | Rejected | Load Management details need to be submitted by TN as the line loadings are crossing their N-1 limits after 15:30 HRS as per present loading trends. Sensitivity on other lines: 230KV-PARAMATHY-PUGALUR-2 71% 220KV-VALLAYAPATTY-PUDANCHANDAI-1 14% 220KV-VALLAYAPATTY-PUGALUR-1 12% | Line Circuits | 02-May-2026 | 13:48 | 04-May-2026 | 10:01
RQ106483 | OCC_237 | TANTRANSCO | 400KV/110KV THAPPUKUNDU-ICT-3 | TANTRANSCO | D | Monthly Maintenance work | 2026-05-06 | 09:00 | 2026-05-06 | 15:00 |  | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. Load Management need to be done by TN. | Transformer | 02-May-2026 | 13:48 | 03-May-2026 | 12:20
RQ106486 | OCC_237 | TANTRANSCO | 400KV/110KV KAYATHAR-ICT-1 | TANTRANSCO | D | Monthly Maintenance work | 2026-05-06 | 14:00 | 2026-05-06 | 20:00 |  | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. Load Management need to be done by TN. | Transformer | 02-May-2026 | 13:48 | 03-May-2026 | 12:20
RQ106839 | OCC_237 | kptcl | 400KV-DONI-GUTTUR-1 | KPTCL | D | submitting proposal to attend Bus2 B ph PG isolator mechanism issue & 1st Quarterly maintenance | 2026-05-06 | 10:00 | 2026-05-06 | 17:00 |  | Yes | Rejected | No N-1 for 400kV DONI S/S. Severe Low voltages are observed at 400kV DHONI S/S and 400kV GUTTUR S/S. Shutdown may be availed on weekends (Sunday) subject to no other overlapping shutdown or during nominal voltage condition Load Management need to be done by KPTCL. 400kV-DONI-MUNIRABAAD 220KV-DONI-GADAG D/C 18% each 400KV-GUTTUR-BTPS-1 17% 220KV-HARTI-GADAG D/C 12% each 220KV-HARTI-BIDNAL D/C 12% each All DONI ICTs 27% each shall be in service. | Line Circuits | 02-May-2026 | 13:13 | 04-May-2026 | 10:01
RQ106819 | OCC_237 | kptcl | TIE BAY (408) OF 400KV/220KV NELAMANGALA-ICT-2 AND 400KV-NELAMANGALA-HASSAN-1 @NELAMANGALA - 400KV | KPTCL | D | Breaker testing and maintenance works. | 2026-05-06 | 11:00 | 2026-05-06 | 17:00 |  | No | Rejected | Deferred by requester. | Bay | 02-May-2026 | 12:59 | 03-May-2026 | 11:39
RQ106829 | OCC_237 | kptcl | 400KV-JINDAL-BPS-3 | KPTCL | D | Quarterly Maintenance & DCRM Testing | 2026-05-06 | 10:00 | 2026-05-06 | 17:00 | Quarterly Maintenance & DCRM Testing | Yes | Approved | 400KV-BPS-JINDAL-4 98% shall be in service. Line loadings to be within 50% of their thermal rating. No N-1 for 400kV JINDAL S/S. Load and generation management need to be by KPTCL. | Line Circuits | 02-May-2026 | 12:43 | 04-May-2026 | 10:13
RQ106546 | OCC_237 | aptransco | 400KV-KRISHNAPATNAM-RACHAGUNNERI-2 | APTRANSCO | D | Tightening of spacer dampers and providing of missing keepers to dampers between locno:58 to 59 , arranging repair sleeves to conductor damages between loc. No:58- 59 Top phase in 400KV Krishnapatnam-Rachagunneri-2 feeder. | 2026-05-06 | 07:00 | 2026-05-06 | 17:00 | During the LC period there will be no interruption to loads as 400KV Krishnapatnam TPP - Manubolu feeder, 400KV SEIL – Manubolu feeder, 400KV Krishnapatnam-SEIL feeder and 400KV Krishnapatnam TPP – Rachagunneri - 1 feeders will be in Service. | Yes | Approved | 400KV-RACHAGUNNERI-KRISHNAPATNAM-1 44% 400KV-KRISHNAPATNAM-NELLORE_AP-1 30% 400KV-SEILU2_AP-NELLORE_AP-1 26% 400KV-NELLORE_AP-NELLORE_PG-1 21% 400KV-TVLM-CHITTOOR D/C 11% each 400KV-SRIPERUMBADUR-NELLORE_PG D/C All NELLORE_AP ICTs shall be in service. | Line Circuits | 02-May-2026 | 12:23 | 04-May-2026 | 09:51
RQ106650 | OCC_237 | aptransco | 400KV/220KV URAVAKONDA-ICT-1 | APTRANSCO | D | "1. Half yearly Maintenance works 2. Periodical Relay testing of ICT *Note : ICT-2,3&4 will be in service" | 2026-05-06 | 09:00 | 2026-05-06 | 15:00 | Annual maintenance works | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. Load Management need to be done by AP. N-1 limit for URAVAKONDA ICTs is 207 MW for 315 MVA ICT each and 329 MW for 500 MVA ICT each. 400KV/220KV URAVAKONDA-ICT-3 33% 400KV/220KV URAVAKONDA-ICT-4 33% 400KV/220KV URAVAKONDA-ICT-2 21% shall be in service. | Transformer | 02-May-2026 | 12:23 | 03-May-2026 | 12:42
RQ106802 | OCC_237 | aptransco | 220KV-ASUPAKA-LOWER_SILERU-1 | APTRANSCO,TGTRANSCO | D | Emergency tree cutting at location no 285 to 286 and at location no 145 to 146 | 2026-05-06 | 10:00 | 2026-05-06 | 17:00 | Emergency tree cutting at location no 285 to 286 and at location no 145 to 146 | Yes | Approved | Load and generation management need to be done by AP and TG. Healthiness of 220kV-Lower Sileru - Chintoor - BG_Kothur shall be ensured prior to the shutdown. 220KV-BGKOTHUR-CHINTOOR-1 100% 220KV-CHINTOOR-LOWER_SILERU-1 100% 220KV-BGKOTHUR-KOTHAGUDEM_TPS-1 38% 220KV-BGKOTHUR-KTS_V-1 37% 220KV-BGKOTHUR-MANUGURU-1 30% shall be in service. Subject to real time grid conditions, line loadings and hydro generation requirements. | Line Circuits | 02-May-2026 | 12:23 | 04-May-2026 | 09:51
RQ106664 | OCC_237 | aptransco | 400KV/220KV GHANI-ICT-2 | APTRANSCO | D | For Relay& Equipment testing works | 2026-05-06 | 17:00 | 2026-05-06 | 22:00 | Annual maintenance works | Yes | Approved | 400KV/220KV GHANI-ICT-1 50% 400KV/220KV GHANI-ICT-3 50% shall be in service. Load Management need to be done by AP. N-1 limit for GHANI ICTs is 316 MW each. | Transformer | 02-May-2026 | 12:23 | 03-May-2026 | 12:20
RQ106463 | OCC_237 | WKTL | 765KV-WARANGAL(NEW)-CHILAKALURIPETA-2 | WKTL | C | For 24Hrs. Trail Run of NGR Bypass at Both Warangal and C'peta end | 2026-05-06 | 08:00 | 2026-05-07 | 08:00 | For 24Hrs. Trail Run of NGR Bypass at Both Warangal and C'peta end | Yes | Approved | Subject to NLDC approval and real time grid conditions. NEW-SR ATC reduction of 450 MW In SR Import. 765KV-WARANGAL(NEW)-CHILAKALURIPETA-1 44% 765kV-WARANGAL-MAHESHWARAM D/C 16% each 765kV-KURNOOL-MAHESHWARAM D/C 9% each 765kV-VEMAGIRI-C'PETA D/C 7% each All 765kV/400kV MAHESHWARAM_PG ICTs shall be in service. | Line Circuits | 02-May-2026 | 11:07 | 03-May-2026 | 12:20
RQ106767 | OCC_237 | MTL | A/R of 400KV-NIZAMABAD-SHANKARAPALLY-1 | MTL | D | Required A/R in Non auto mode for defect rectification work | 2026-05-05 | 09:00 | 2026-05-05 | 17:00 | A/R OFF | No | Rejected | Deferred by requester. | Auto Reclosure | 02-May-2026 | 08:52 | 02-May-2026 | 17:45
RQ106736 | OCC_237 | KNTL | MAIN BAY (415) OF 400KV-GADAG_PSS-KOPPAL-1 AND KOPPAL - 400KV - BUS 1 @KOPPAL - 400KV | GADAG_II_A | D | "Yearly Bay equipment testing and preventive maintenance. " | 2026-05-05 | 09:00 | 2026-05-05 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 02-May-2026 | 08:47 | 02-May-2026 | 17:55
RQ106969 | OCC_237 | NLC | 230KV/6.6KV NEYVELI TS II-ST-2 | NLC | C | For carrying out the preventive maintenance of bay equipment and line maintenance work | 2026-05-05 | 09:00 | 2026-05-07 | 17:00 | ST-1 will be in service | No | Rejected | Deferred by requester. | Transformer | 02-May-2026 | 07:12 | 02-May-2026 | 17:45
RQ107392 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-1 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-04 | 19:00 | 2026-05-04 | 23:59 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Line Circuits | 02-May-2026 | 03:36 | 01-May-2026 | 13:48
RQ107400 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-2 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-04 | 19:00 | 2026-05-04 | 23:59 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Line Circuits | 02-May-2026 | 03:36 | 01-May-2026 | 13:48
RQ107407 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-1 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-04 | 00:00 | 2026-05-04 | 04:00 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Line Circuits | 02-May-2026 | 03:36 | 01-May-2026 | 13:48
RQ107415 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-2 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-04 | 00:00 | 2026-05-04 | 04:00 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Line Circuits | 02-May-2026 | 03:36 | 01-May-2026 | 13:48
RQ108158 | PNOCC | aptransco | 400KV-SIMHADRI-VEMAGIRI_AP-1 | APTRANSCO | C | To carry out Replacement of badly damaged rusted towers at Loc No:10 in 400kV kalapaka -STPP-3 & 4 TMDC Line wedge / Bridge connectors required to connect Loc. No. 3 of Kalapaka-STPP-1 and Loc. No 3 of STPP –Vemagiri Line (Kalapaka/STPP-Vemagiri Circuits), which will be kept in open condition, to make the old Kalapaka-STPP-1 line live and to withstand the loading from STPP to Kalapaka as the Kalapaka is the nearest load point. | 2026-05-05 | 06:00 | 2026-05-05 | 18:00 |  | Yes | Rejected | APSLDC has proposed reconfiguration of the 400 kV Kalpaka–Vemagiri AP S/C line to a 400 kV Simhadri–Vemagiri AP S/C line, thereby restoring the earlier configuration of the 400 kV Kalpaka–Simhadri-1 line. Under this arrangement, during the shutdown of 400 kV Kalpaka–Simhadri-3 & 4, the 400 kV Kalpaka–Simhadri-1 (through reconfiguration) and 400 kV Kalpaka–Simhadri-2 lines will remain in service. With this reconfiguration, it is observed that the 400 kV Vemagiri AP–Vemagiri PG D/C line may be loaded up to 750 MW, which would violate the N-1 limit of 500 MW per circuit. Tripping of these lines may lead to overloading of the 220 kV network and possible load loss in the Vemagiri downstream area. APSLDC may be requested to provide a detailed action plan to mitigate this risk. With the above reconfiguration and planned shutdowns, the voltage levels in the Vizag area are expected to reduce by approximately 1–2 kV. Further, under full generation conditions at Simhadri Stage-I & II (4 × 500 MW) and HNPCL (2 × 520 MW), the loading on the 400 kV Kalpaka–Simhadri-1 & 2 lines is likely to exceed N-1 limits (approximately 440 MW), considering the operational constraints at Kalpaka substation. The HVDC Gazuwaka power order has a sensitivity of about 3% on each line, while HNPCL generation has a sensitivity of about 12% on each line. Hence, any reduction in generation at HNPCL or reduction in HVDC Gazuwaka import would aggravate the loading on these lines. To maintain compliance with N-1 limits on 400 kV Kalpaka–Simhadri-1 & 2 lines ,the generation at Simhadri Stage-I & II may be restricted to below 1550 MW. In case of reduction in HNPCL generation or HVDC Gazuwaka import or tripping of poles, further reduction in Simhadri generation may be required. It is also noted that the proposed shutdowns are of a planned nature, and any shutdown exceeding two days requires approval from SRPC. Additionally, the proposed change in network configuration requires approval from SRPC, along with corresponding revisions in protection settings. FTC is required for these configuration changes. | Line Circuits | 01-May-2026 | 17:34 | 02-May-2026 | 20:01
RQ108157 | PNOCC | aptransco | 400KV-KALPAKKA-VEMAGIRI_AP-1 | APTRANSCO | C | To carry out Replacement of badly damaged rusted towers at Loc No:10 in 400kV kalapaka -STPP-3 & 4 TMDC Line wedge / Bridge connectors required to connect Loc. No. 3 of Kalapaka-STPP-1 and Loc. No 3 of STPP –Vemagiri Line (Kalapaka/STPP-Vemagiri Circuits), which will be kept in open condition, to make the old Kalapaka-STPP-1 line live and to withstand the loading from STPP to Kalapaka as the Kalapaka is the nearest load point. | 2026-05-05 | 00:00 | 2026-05-05 | 18:00 |  | Yes | Rejected | APSLDC has proposed reconfiguration of the 400 kV Kalpaka–Vemagiri AP S/C line to a 400 kV Simhadri–Vemagiri AP S/C line, thereby restoring the earlier configuration of the 400 kV Kalpaka–Simhadri-1 line. Under this arrangement, during the shutdown of 400 kV Kalpaka–Simhadri-3 & 4, the 400 kV Kalpaka–Simhadri-1 (through reconfiguration) and 400 kV Kalpaka–Simhadri-2 lines will remain in service. With this reconfiguration, it is observed that the 400 kV Vemagiri AP–Vemagiri PG D/C line may be loaded up to 750 MW, which would violate the N-1 limit of 500 MW per circuit. Tripping of these lines may lead to overloading of the 220 kV network and possible load loss in the Vemagiri downstream area. APSLDC may be requested to provide a detailed action plan to mitigate this risk. With the above reconfiguration and planned shutdowns, the voltage levels in the Vizag area are expected to reduce by approximately 1–2 kV. Further, under full generation conditions at Simhadri Stage-I & II (4 × 500 MW) and HNPCL (2 × 520 MW), the loading on the 400 kV Kalpaka–Simhadri-1 & 2 lines is likely to exceed N-1 limits (approximately 440 MW), considering the operational constraints at Kalpaka substation. The HVDC Gazuwaka power order has a sensitivity of about 3% on each line, while HNPCL generation has a sensitivity of about 12% on each line. Hence, any reduction in generation at HNPCL or reduction in HVDC Gazuwaka import would aggravate the loading on these lines. To maintain compliance with N-1 limits on 400 kV Kalpaka–Simhadri-1 & 2 lines ,the generation at Simhadri Stage-I & II may be restricted to below 1550 MW. In case of reduction in HNPCL generation or HVDC Gazuwaka import or tripping of poles, further reduction in Simhadri generation may be required. It is also noted that the proposed shutdowns are of a planned nature, and any shutdown exceeding two days requires approval from SRPC. Additionally, the proposed change in network configuration requires approval from SRPC, along with corresponding revisions in protection settings. FTC is required for these configuration changes. | Line Circuits | 01-May-2026 | 17:30 | 02-May-2026 | 20:01
RQ108159 | PNOCC | aptransco | 400KV-SIMHADRI-KALPAKKA-3 | APTRANSCO | C | For Replacement the badly rusted Towers at Loc.No.10 | 2026-05-06 | 06:00 | 2026-05-07 | 23:59 | LC requested upto 11/05/2026 | Yes | Rejected | APSLDC has proposed reconfiguration of the 400 kV Kalpaka–Vemagiri AP S/C line to a 400 kV Simhadri–Vemagiri AP S/C line, thereby restoring the earlier configuration of the 400 kV Kalpaka–Simhadri-1 line. Under this arrangement, during the shutdown of 400 kV Kalpaka–Simhadri-3 & 4, the 400 kV Kalpaka–Simhadri-1 (through reconfiguration) and 400 kV Kalpaka–Simhadri-2 lines will remain in service. With this reconfiguration, it is observed that the 400 kV Vemagiri AP–Vemagiri PG D/C line may be loaded up to 750 MW, which would violate the N-1 limit of 500 MW per circuit. Tripping of these lines may lead to overloading of the 220 kV network and possible load loss in the Vemagiri downstream area. APSLDC may be requested to provide a detailed action plan to mitigate this risk. With the above reconfiguration and planned shutdowns, the voltage levels in the Vizag area are expected to reduce by approximately 1–2 kV. Further, under full generation conditions at Simhadri Stage-I & II (4 × 500 MW) and HNPCL (2 × 520 MW), the loading on the 400 kV Kalpaka–Simhadri-1 & 2 lines is likely to exceed N-1 limits (approximately 440 MW), considering the operational constraints at Kalpaka substation. The HVDC Gazuwaka power order has a sensitivity of about 3% on each line, while HNPCL generation has a sensitivity of about 12% on each line. Hence, any reduction in generation at HNPCL or reduction in HVDC Gazuwaka import would aggravate the loading on these lines. To maintain compliance with N-1 limits on 400 kV Kalpaka–Simhadri-1 & 2 lines ,the generation at Simhadri Stage-I & II may be restricted to below 1550 MW. In case of reduction in HNPCL generation or HVDC Gazuwaka import or tripping of poles, further reduction in Simhadri generation may be required. It is also noted that the proposed shutdowns are of a planned nature, and any shutdown exceeding two days requires approval from SRPC. Additionally, the proposed change in network configuration requires approval from SRPC, along with corresponding revisions in protection settings. FTC is required for these configuration changes. | Line Circuits | 01-May-2026 | 17:42 | 03-May-2026 | 12:29
RQ108160 | PNOCC | aptransco | 400KV-SIMHADRI-KALPAKKA-4 | APTRANSCO | C | For Replacement the badly rusted Towers at Loc.No.10 | 2026-05-06 | 06:00 | 2026-05-07 | 23:59 | LC requested upto 11/05/2026 | Yes | Rejected | APSLDC has proposed reconfiguration of the 400 kV Kalpaka–Vemagiri AP S/C line to a 400 kV Simhadri–Vemagiri AP S/C line, thereby restoring the earlier configuration of the 400 kV Kalpaka–Simhadri-1 line. Under this arrangement, during the shutdown of 400 kV Kalpaka–Simhadri-3 & 4, the 400 kV Kalpaka–Simhadri-1 (through reconfiguration) and 400 kV Kalpaka–Simhadri-2 lines will remain in service. With this reconfiguration, it is observed that the 400 kV Vemagiri AP–Vemagiri PG D/C line may be loaded up to 750 MW, which would violate the N-1 limit of 500 MW per circuit. Tripping of these lines may lead to overloading of the 220 kV network and possible load loss in the Vemagiri downstream area. APSLDC may be requested to provide a detailed action plan to mitigate this risk. With the above reconfiguration and planned shutdowns, the voltage levels in the Vizag area are expected to reduce by approximately 1–2 kV. Further, under full generation conditions at Simhadri Stage-I & II (4 × 500 MW) and HNPCL (2 × 520 MW), the loading on the 400 kV Kalpaka–Simhadri-1 & 2 lines is likely to exceed N-1 limits (approximately 440 MW), considering the operational constraints at Kalpaka substation. The HVDC Gazuwaka power order has a sensitivity of about 3% on each line, while HNPCL generation has a sensitivity of about 12% on each line. Hence, any reduction in generation at HNPCL or reduction in HVDC Gazuwaka import would aggravate the loading on these lines. To maintain compliance with N-1 limits on 400 kV Kalpaka–Simhadri-1 & 2 lines ,the generation at Simhadri Stage-I & II may be restricted to below 1550 MW. In case of reduction in HNPCL generation or HVDC Gazuwaka import or tripping of poles, further reduction in Simhadri generation may be required. It is also noted that the proposed shutdowns are of a planned nature, and any shutdown exceeding two days requires approval from SRPC. Additionally, the proposed change in network configuration requires approval from SRPC, along with corresponding revisions in protection settings. FTC is required for these configuration changes. | Line Circuits | 01-May-2026 | 17:42 | 03-May-2026 | 12:29
RQ108133 | PNOCC | aptransco | 400KV-SIMHADRI-VEMAGIRI_AP-1 | APTRANSCO | D | Removal of jumpers. Restoration of LILO arrangement of 400KV Simhadri – Vemagiri and Vemagiri – Kalapaka | 2026-05-12 | 06:00 | 2026-05-12 | 18:00 | Removal of jumpers. Restoration of LILO arrangement of 400KV Simhadri – Vemagiri and Vemagiri – Kalapaka | Yes | Rejected | Deferred by AP as per mail communication received. | Line Circuits | 01-May-2026 | 15:55 | 09-May-2026 | 16:43
RQ108134 | PNOCC | aptransco | 400KV-KALPAKKA-VEMAGIRI_AP-1 | APTRANSCO | D | Removal of jumpers. Restoration of LILO arrangement of 400KV Simhadri – Vemagiri and Vemagiri – Kalapaka | 2026-05-12 | 06:00 | 2026-05-12 | 18:00 | Removal of jumpers. Restoration of LILO arrangement of 400KV Simhadri – Vemagiri and Vemagiri – Kalapaka | Yes | Rejected | Deferred by AP as per mail communication received. | Line Circuits | 01-May-2026 | 15:55 | 09-May-2026 | 16:43
RQ108161 | PNOCC | aptransco | 400KV-SIMHADRI-KALPAKKA-3 | APTRANSCO | C | For Replacement the badly rusted Towers at Loc.No.10 | 2026-05-08 | 00:00 | 2026-05-09 | 23:59 | LC is requested upto 11/05/2026 | Yes | Rejected | Deferred by AP as per mail received dated 04.05.2026. | Line Circuits | 01-May-2026 | 17:46 | 05-May-2026 | 10:24
RQ108162 | PNOCC | aptransco | 400KV-SIMHADRI-KALPAKKA-4 | APTRANSCO | C | For Replacement the badly rusted Towers at Loc.No.10 | 2026-05-08 | 00:00 | 2026-05-09 | 23:59 | LC is requested upto 11/05/2026 | Yes | Rejected | Deferred by AP as per mail received dated 04.05.2026. | Line Circuits | 01-May-2026 | 17:46 | 05-May-2026 | 10:24
RQ108163 | PNOCC | aptransco | 400KV-SIMHADRI-KALPAKKA-3 | APTRANSCO | C | For Replacement the badly rusted Towers at Loc.No.10 | 2026-05-10 | 00:00 | 2026-05-11 | 18:00 |  | Yes | Rejected | Deferred by AP as per mail received dated 04.05.2026. | Line Circuits | 01-May-2026 | 17:50 | 07-May-2026 | 10:51
RQ108164 | PNOCC | aptransco | 400KV-SIMHADRI-KALPAKKA-4 | APTRANSCO | C | For Replacement the badly rusted Towers at Loc.No.10 | 2026-05-10 | 00:00 | 2026-05-11 | 18:00 |  | Yes | Rejected | Deferred by AP as per mail received dated 04.05.2026. | Line Circuits | 01-May-2026 | 17:50 | 07-May-2026 | 10:51
RQ106372 | OCC_237 | TANTRANSCO | 400KV/230KV KAMUDHI-ICT-1 | TANTRANSCO | D | Monthly Maintenance Work | 2026-05-05 | 16:00 | 2026-05-05 | 21:00 |  | No | Rejected | Deferred by requester. | Transformer | 01-May-2026 | 19:33 | 02-May-2026 | 17:45
RQ106482 | OCC_237 | TANTRANSCO | 400KV/110KV THAPPUKUNDU-ICT-2 | TANTRANSCO | D | Monthly Maintenance work | 2026-05-05 | 09:00 | 2026-05-05 | 15:00 |  | No | Rejected | Deferred by requester. | Transformer | 01-May-2026 | 19:33 | 02-May-2026 | 17:45
RQ106988 | OCC_237 | TGTRANSCO | 400KV/220KV RAMADUGU-ICT-2 | TGTRANSCO | C | For rectification of 400KV, S&S make, R-ph isolator (430-89T) alignment problem pertaining to 500MVA ICT-2 HV at 400KV SS Ramadugu by S&S service engineer | 2026-05-05 | 10:00 | 2026-05-06 | 18:00 |  | Yes | Approved | Load Management need to be done by TG. N-1 limit for RAMADUGU ICTs is 330 MW each. 400KV/220KV RAMADUGU-ICT-1 43% All RAMAGUNDAM and GAJWEL ICTs shall be in service along with 400KV-TIPPAPUR-RAMADUGU D/C. Subject to ICT loadings to be within their N-1 limit. | Transformer | 01-May-2026 | 15:54 | 02-May-2026 | 19:53
RQ106989 | OCC_237 | TGTRANSCO | 400KV/220KV SURYAPET-ICT-1 | TGTRANSCO | C | General maintenance works and MRT,TRE wing testing works | 2026-05-05 | 10:00 | 2026-05-06 | 17:00 |  | Yes | Approved | Load Management need to be done by TG. N-1 limit for SURYAPET ICTs is 222 MW for 315 MVA ICTs each and 352 MW for 500 MVA ICT each. 400KV/220KV SURYAPET-ICT-2 20% 400KV/220KV SURYAPET-ICT-3 20% 400KV-VTPS_IV-VIJAYAWADA-1 10% 400KV-SURYAPET-VTPS_IV D/C 10% each shall be in service. Subject to ICT loadings to be within their N-1 limit. | Transformer | 01-May-2026 | 15:54 | 02-May-2026 | 19:58
RQ107013 | OCC_237 | TGTRANSCO | 400KV-YADADRI TPP-DAMARCHERLA-1 | TGTRANSCO | C | for Testing and Inspection of Line Protection Relays | 2026-05-05 | 09:00 | 2026-05-05 | 18:00 |  | Yes | Approved | 400KV-YADADRI TPP-DAMARCHERLA-2 98% shall be in service. Line loading to be within 50% of its thermal rating. | Line Circuits | 01-May-2026 | 15:54 | 02-May-2026 | 19:53
RQ106927 | OCC_237 | PGCIL SR-1 | MAHESHWARAM_PG - 765KV - BUS 1 | PGCIL SR-1 | C | Commissioning of 765kV BUS-I for Bidar Bay extension works (SS-12T) | 2026-05-06 | 09:00 | 2026-05-08 | 18:00 | Construction works | Yes | Approved | Subject to NLDC approval and real time grid conditions. Remaining elements shall be in service. | Bus | 01-May-2026 | 15:40 | 02-May-2026 | 17:55
RQ106896 | OCC_237 | PGCIL SR-1 | 765KV-RAICHUR_PG-SHOLAPUR-1 | POWERGRID | C | Tower erection works of AP 4A/0-- 765KV KOPPAL RAICHUR LINE | 2026-05-10 | 08:00 | 2026-05-14 | 18:00 | Construction works | Yes | Approved | NEW-SR - 150 Import / 700 Export MW reduction, Subject to real time grid conditions. As discussed in 237 outage co-ordination meeting, Forum approved the S/D from 5th May for 10 days. PG to strictly adhere to the timelines. 765KV-RAICHUR_PG-SHOLAPUR-2 49% 765kV-KURNOOL-MAHESHWARAM D/C 13% each 765kV-WARORA-WARANGAL D/C 11% each 765kV-WARDHA-NIZAMABAAD D/C 9% each 765kV-WARANGAL-MAHESHWARAM D/C 6% each All NIZAMABAAD ICTs shall be in service. PGCIL SR-1 is not availing the shutdown of 765kV-RAICHUR-KURNOOL-1. Postponed by requester over telephonic communication. PGCIL SR-1 requested to avail from 10.05.2026 to 14.05.2026. | Line Circuits | 01-May-2026 | 15:40 | 03-May-2026 | 10:11
RQ106897 | OCC_237 | PGCIL SR-1 | 765KV-KURNOOL_PG-RAICHUR_PG-1 | POWERGRID | C | Tower erection works of AP 4A/0-- 765KV KOPPAL RAICHUR LINE | 2026-05-05 | 11:00 | 2026-05-14 | 18:00 | Construction works | Yes | Rejected | Note: Shutdown of 765kV-SOLAPUR-RAICHUR-1 and 765kV-RAICHUR-KURNOOL-1 shall only be facilitated after the revival of 765KV-NIZAMABAD-WARDHA-1. NEW-SR - 200 Import / 800 Export MW reduction, Subject to real time grid conditions. As discussed in 237 outage co-ordination meeting, Forum approved the S/D from 5th May for 10 days. PG to strictly adhere to the timelines. 765KV-RAICHUR_PG-SHOLAPUR-2 49% 765kV-KURNOOL-MAHESHWARAM D/C 13% each 765kV-WARORA-WARANGAL D/C 11% each 765kV-WARDHA-NIZAMABAAD D/C 9% each 765kV-WARANGAL-MAHESHWARAM D/C 6% each All NIZAMABAAD ICTs shall be in service. Deferred by requester over telephonic communication. | Line Circuits | 01-May-2026 | 15:40 | 03-May-2026 | 10:11
RQ106905 | OCC_237 | PGCIL SR-1 | 765KV/400KV SRIKAKULAM-ICT-2 | PGCIL SR-1 | D | amp works | 2026-05-05 | 10:00 | 2026-05-05 | 17:00 | AMP works. | Yes | Rejected | Subject to NLDC approval and real time grid conditions and ICT loadings within its N-1 limit. N-1 limit for 765kV/400kV SRIKAKULAM ICTs is 797 MW each. NEW-SR tentative ATC/TTC curtailment of 50 MW in SR import. 765KV/400KV SRIKAKULAM-ICT-1 78% 765KV/400KV VEMAGIRI_PG-ICT-1,2 6% each 400KV-MARADAM-KALPAKKA D/C 8% each 765KV-VEMAGIRI_PG-SRIKAKULAM D/C 7% each 400KV-VEMAGIRI_PG-VEMAGIRI_AP D/C 2% each 400KV-SIMHADRI-KALPAKKA-2,3,4 2% each shall be in service. Shutdown deferred by NLDC. | Transformer | 01-May-2026 | 15:40 | 02-May-2026 | 20:32
RQ106752 | OCC_237 | NTPC | VALLUR - 400KV B/R 1 | NTECL | C | To attend Low oil level in Conservator and Oil leakage from GCD. | 2026-05-05 | 09:00 | 2026-05-06 | 18:00 | Shutdown required for two days for attending conservator and radiator oil leakage and Oil Filtration | Yes | Approved | Concurred, subject to real time grid conditions. | Bus Reactor | 01-May-2026 | 13:21 | 02-May-2026 | 17:55
RQ106680 | OCC_237 | aptransco | MAIN BAY (401) OF 400KV-RAYALSEEMA TPP-KALIKIRI-2 AND KALIKIRI - 400KV - BUS 1 @KALIKIRI - 400KV | APTRANSCO | D | CTs Tan Delta & Maintenance works | 2026-05-05 | 10:00 | 2026-05-05 | 17:00 | Annual maintenance works | Yes | Approved | Remaining bays shall be in service. | Bay | 01-May-2026 | 10:36 | 02-May-2026 | 17:55
RQ106798 | OCC_237 | aptransco | 400KV-GUDIWADA-SATTENPALLY-1 | APTRANSCO | D | Completion of the balance pending Statutory remaks | 2026-05-05 | 06:00 | 2026-05-05 | 18:00 | There will be no interruption to the 400kv ss Gudivada | Yes | Approved | 400KV-VEMAGIRI_PG-VEMAGIRI_AP D/C 25% each 400KV-VTPS_IV-VIJAYAWADA-1 24% 765KV-CHILAKALURIPETA-VEMAGIRI_PG 18% D/C each 400KV-GUDIWADA-SATTENPALLY-2 17% All VEMAGIRI_PG ICTs shall be in service. | Line Circuits | 01-May-2026 | 10:36 | 02-May-2026 | 17:55
RQ106801 | OCC_237 | aptransco | 400KV-GUDIWADA-VEMAGIRI_AP-2 | APTRANSCO | D | Completion of the balance pending Statutory remaks | 2026-05-05 | 06:00 | 2026-05-05 | 18:00 | There will be no interruption to the 400kv ss Gudivada | Yes | Approved | 400KV-VEMAGIRI_PG-VEMAGIRI_AP D/C 25% each 400KV-VTPS_IV-VIJAYAWADA-1 24% 765KV-CHILAKALURIPETA-VEMAGIRI_PG 18% D/C each 400KV-GUDIWADA-VEMAGIRI_AP-1 17% All VEMAGIRI_PG ICTs shall be in service. | Line Circuits | 01-May-2026 | 10:36 | 02-May-2026 | 17:55
RQ106553 | OCC_237 | aptransco | 400KV/220KV CHITTOOR-ICT-2 | APTRANSCO | D | hot lines wing had conducted thermo vision scanning on 14.02.2026 and reported hot spots with temperature of 850C at LV CB jumper clamp and CT stud clamp (Y Phase) of ICT-2 | 2026-05-05 | 17:00 | 2026-05-05 | 19:00 | for attending hot line remarks | Yes | Approved | Load Management need to be done by AP. N-1 limit for CHITTOOR ICTs is 230 MW each. 400KV/220KV CHITTOOR-ICT-1 30% 400KV/220KV CHITTOOR-ICT-3 30% All KALIKIRI and RACHAGUNNERI ICTs shall be in service along with 400KV-KALIKIRI-CHITTOOR D/C. Subject to ICT loadings to be within their N-1 limit. | Transformer | 01-May-2026 | 10:36 | 02-May-2026 | 19:53
RQ106657 | OCC_237 | aptransco | 400KV/220KV TALARCHEVU-ICT-3 | APTRANSCO | D | FOR PERIODICAL MAINTENANCE AND MRT TESTINGS | 2026-05-05 | 17:00 | 2026-05-05 | 22:00 | Annual maintenance works | Yes | Approved | Load Management need to be done by AP. N-1 limit for TALARCHEVU ICTs is 200 MW each. 400KV/220KV TALARCHERUVU-ICT-1 50% 400KV/220KV TALARCHERUVU-ICT-2 50% shall be in service. Subject to ICT loadings to be within their N-1 limit. | Transformer | 01-May-2026 | 10:36 | 02-May-2026 | 19:53
RQ106661 | OCC_237 | aptransco | 400KV/220KV KV_KOTA-ICT-1 | APTRANSCO | D | General maintenance works as per schedule. | 2026-05-05 | 09:00 | 2026-05-05 | 17:00 | Annual maintenance works | Yes | Rejected | Subject to ICT loadings to be within their N-1 limit. Subject to availability of the 3rd ICT. Load Management need to be done by AP. N-1 limit for KV_KOTA ICTs is 226 MW each. 400KV/220KV KV_KOTA-ICT-2 43% All GUDDIGUDEM and VEMAGIRI_AP ICTs shall be in service. | Transformer | 01-May-2026 | 10:36 | 02-May-2026 | 19:53
RQ106599 | OCC_237 | aptransco | 400KV-KALPAKKA-KHAMMAM_PG-1 | APTRANSCO,TGTRANSCO | C | For “Replacement of badly damaged rusted towers from Loc No.1 to 11 in 400KV Kalapaka – Khammam & Asupaka TMDC line with Heavy galvanized Towers (120 Microns) along with stringing of conductor on turnkey basis under RMI scheme”at 400kv SS Kalapaka | 2026-05-05 | 09:00 | 2026-05-31 | 23:59 | Subject work awarded to M/s. Kalki Engineering works,Visakhapatnam and the agency requested for LC to take up the work by engaging men and material. Requested for approval through proper channel | Yes | Approved | No N-1 for 400kV ASUPAKA S/S. Load Management need to be done by AP and TG. 400kV-SIMHADRI-VEMAGIRI_AP 12% 400kV-GAZUWAKA-VEMAGIRI 12% 400kV-SIMHADRI-VEMAGIRI_PG D/C 11% each 400kV-KALPAKKA-VEMAGIRI 11% 400kV-KHAMMAM-WARANGAL 10% and remaining all other lines at 400kV KALPAKKA and 400kV KHAMMAM shall be in service. FTC is required. | Line Circuits | 01-May-2026 | 10:36 | 02-May-2026 | 20:19
RQ106600 | OCC_237 | aptransco | 400KV-KALPAKKA-ASUPAKA-1 | APTRANSCO,TGTRANSCO | C | For “Replacement of badly damaged rusted towers from Loc No.1 to 11 in 400KV Kalapaka – Khammam & Asupaka TMDC line with Heavy galvanized Towers (120 Microns) along with stringing of conductor on turnkey basis under RMI scheme”at 400kv SS Kalapaka | 2026-05-05 | 17:01 | 2026-05-31 | 23:59 | Subject work awarded to M/s. Kalki Engineering works,Visakhapatnam and the agency requested for LC to take up the work by engaging men and material. Requested for approval through proper channel | Yes | Approved | No N-1 for 400kV ASUPAKA S/S. Load Management need to be done by AP and TG. 400kV-SIMHADRI-VEMAGIRI_AP 12% 400kV-GAZUWAKA-VEMAGIRI 12% 400kV-SIMHADRI-VEMAGIRI_PG D/C 11% each 400kV-KALPAKKA-VEMAGIRI 11% 400kV-KHAMMAM-WARANGAL 10% and remaining all other lines at 400kV KALPAKKA and 400kV KHAMMAM shall be in service. FTC is required. | Line Circuits | 01-May-2026 | 10:36 | 02-May-2026 | 20:19
RQ106749 | OCC_237 | aptransco | 400KV-NARNOOR-GHANI-2 | APTRANSCO | D | For PMI defects rectification at loc.No.20-21, 23-24. | 2026-05-05 | 17:00 | 2026-05-05 | 21:00 | Annual maintenance works | Yes | Approved | 400KV-NARNOOR-GHANI-1 100% shall be in service. | Line Circuits | 01-May-2026 | 10:36 | 02-May-2026 | 19:40
RQ106416 | OCC_237 | TANTRANSCO | 400KV-ARIYALUR-KALVENDAPATTU-1 | TANTRANSCO | D | Monthly Maintenance work | 2026-05-05 | 09:00 | 2026-05-05 | 17:00 |  | Yes | Approved | 400KV-ARIYALUR-KALVENDAPATTU-2 31% 400KV-THIRUVALAM-KALVENDAPATTU D/C 17% each 400KV-PUDUCHERRY-NNTPP-1 11% 400KV-PUDUCHERRY-SUNGAVARACHATRAM-1 11% 400KV-ARIYALUR-NNTPP D/C 11% each 400KV-SUNGAVARACHATRAM-SRIPERUMBADUR-1 7% All 765kV/400kV THIRUVALLAM ICTs shall be in service. Subject to real time line loadings and grid conditions. | Line Circuits | 01-May-2026 | 10:34 | 02-May-2026 | 19:58
RQ107034 | OCC_237 | PGCIL SR-2 | 220KV-TUMKUR-MADHUGIRI-1 | KPTCL | D | AMP of Terminal Equipments | 2026-05-05 | 09:00 | 2026-05-05 | 17:00 |  | Yes | Approved | Load Management need to be done by KPTCL. Subject to real time line loadings and grid conditions. 220KV-KIADB_VNPURA-MADHUGIRI-1 45% 220KV-HIRIYUR_KAR-HIRIYUR D/C 15% each 220KV-MADHUGIRI-GOWRIBIDANUR-1 14% 400KV-BPS-PAVAGADA_PG D/C 8% each 400KV/220KV TUMKUR-ICT-1,2,3 20% each shall be in service. | Line Circuits | 01-May-2026 | 10:31 | 02-May-2026 | 20:39
RQ106539 | OCC_237 | NTPC | MAIN BAY (213) OF 220KV-KUDGI_NTPC-NANDHIHAL-4 @KUDGI_NTPC - 220KV | NTPC | C | yearly bay equipment maintenance | 2026-05-05 | 07:00 | 2026-05-06 | 19:00 | line-4 will be in service through transfer bay | Yes | Approved | Remaining bays shall be in service. | Bay | 01-May-2026 | 10:27 | 02-May-2026 | 17:55
RQ106499 | OCC_237 | NPCIL | 400KV-KUDANKULAM-TIRUNELVELI-3 | POWERGRID | C | Line insulator cleaning work. Wave trap top side connectors CRM measurements. SF6 gas properties checking in all compartments. SF6 Density meters calibration to be done. | 2026-05-05 | 07:00 | 2026-05-05 | 18:00 |  | Yes | Approved | 400KV-KUDANKULAM-TIRUNELVELI-1 39% 400KV-KUDANKULAM-TIRUNELVELI-2 39% 400KV-TUTICORIN_PS-KUDANKULAM-2 16% 400KV-TUTICORIN_PS-TIRUNELVELI-1 9% 400KV-KANARPATTI-TIRUNELVELI-1 4% 230KV-KUDANKULAM-S R PUDUR-1 4% 230KV-S R PUDUR-SANGANERI-1 4% shall be in service. | Line Circuits | 01-May-2026 | 10:06 | 02-May-2026 | 19:58
RQ107391 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-1 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-03 | 19:00 | 2026-05-03 | 23:59 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Line Circuits | 01-May-2026 | 09:41 | 30-Apr-2026 | 10:33
RQ107399 | OCC_2371 | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-2 | PVG_IRCON_S | D | Commissioning works of JSW Site | 2026-05-03 | 19:00 | 2026-05-03 | 23:59 |  | No | Rejected | Requester does not update the availing status as yes on D-3. | Line Circuits | 01-May-2026 | 09:41 | 30-Apr-2026 | 10:33
RQ106735 | OCC_237 | KNTL | TIE BAY (414) OF 400KV/220KV KOPPAL-ICT-5 AND FUTURE @KOPPAL - 400KV | KNTL | D | "Yearly Bay equipment testing and preventive maintenance. " | 2026-05-04 | 09:00 | 2026-05-04 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 01-May-2026 | 08:57 | 01-May-2026 | 13:54
RQ106766 | OCC_237 | MTL | A/R of 400KV-NIZAMABAD-SHANKARAPALLY-1 | MTL | D | Required A/R in Non auto mode for defect rectification work | 2026-05-04 | 09:00 | 2026-05-04 | 17:00 | A/R OFF | No | Rejected | Deferred by requester. | Auto Reclosure | 01-May-2026 | 08:51 | 01-May-2026 | 13:48
RQ106655 | OCC_237 | aptransco | 400KV/220KV JAMMALAMADUGU-ICT-1 | APTRANSCO | D | FOR PERIODICAL MAINTENANCE AND MRT TESTINGS | 2026-05-04 | 10:00 | 2026-05-04 | 17:00 | Annual maintenance works | Yes | Approved | Load Management need to be done by AP. N-1 limit for JAMMALAMADUGU ICTs is 186 MW for 315 MVA ICT each and 295 MW for 500 MVA ICT each. 400KV/220KV JAMMALAMADUGU-ICT-3 49% 400KV/220KV JAMMALAMADUGU-ICT-2 31% shall be in service. | Transformer | 30-Apr-2026 | 20:49 | 02-May-2026 | 04:28
RQ106799 | OCC_237 | aptransco | 400KV-GUDIWADA-SATTENPALLY-2 | APTRANSCO | D | Completion of the balance pending Statutory remaks | 2026-05-04 | 06:00 | 2026-05-04 | 18:00 | There will be no interruption to the 400kv ss Gudivada | Yes | Approved | 400KV-VEMAGIRI_PG-VEMAGIRI_AP D/C 25% each 400KV-VTPS_IV-VIJAYAWADA-1 24% 765KV-CHILAKALURIPETA-VEMAGIRI_PG 18% D/C each 400KV-GUDIWADA-SATTENPALLY-1 17% All VEMAGIRI_PG ICTs shall be in service. | Line Circuits | 30-Apr-2026 | 20:49 | 02-May-2026 | 04:43
RQ106800 | OCC_237 | aptransco | 400KV-GUDIWADA-VEMAGIRI_AP-1 | APTRANSCO | D | Completion of the balance pending Statutory remaks | 2026-05-04 | 06:00 | 2026-05-04 | 18:00 | There will be no interruption to the 400kv ss Gudivada | Yes | Approved | 400KV-VEMAGIRI_PG-VEMAGIRI_AP D/C 25% each 400KV-VTPS_IV-VIJAYAWADA-1 24% 765KV-CHILAKALURIPETA-VEMAGIRI_PG 18% D/C each 400KV-GUDIWADA-VEMAGIRI_AP-2 17% All VEMAGIRI_PG ICTs shall be in service. | Line Circuits | 30-Apr-2026 | 20:49 | 02-May-2026 | 04:43
RQ106678 | OCC_237 | aptransco | TIE BAY (420) OF 400KV-GAUTAMI-VEMAGIRI_AP-1 AND 400KV-GMR-VEMAGIRI_AP-2 @VEMAGIRI_AP - 400KV | APTRANSCO | D | MRT testings at Vemagiri end | 2026-05-04 | 09:00 | 2026-05-04 | 17:00 | Annual maintenance works | Yes | Approved | Concurred, subject to real time grid conditions. | Bay | 30-Apr-2026 | 20:49 | 01-May-2026 | 13:58
RQ106785 | OCC_237 | aptransco | TIE BAY (405) OF 400KV-NARNOOR-SRISAILAM_LEFT_BANK-1 AND 400KV/220KV NARNOOR-ICT-2 @NARNOOR - 400KV | APTRANSCO | C | For replacing the old hydraulic 400KV CB with new CGL CB. Feeder will be inservice with main bay 404-52. Hence no interruption. | 2026-05-04 | 17:01 | 2026-05-20 | 18:00 | For replacing the old hydraulic 400KV CB with new CGL CB. Feeder will be inservice with main bay 404-52. Hence no interruption. | Yes | Approved | FTC is required. Remaining bays shall be in service. | Bay | 30-Apr-2026 | 20:49 | 01-May-2026 | 13:58
RQ107087 | OCC_237 | aptransco | 400KV-SIMHADRI-KALPAKKA-4 | APTRANSCO | D | Replacement of completely rusted and damaged 7/3.66 HTGS Earth wire & OPGW Wherever existing on 400KV Kalapaka-STPP-4 feeders | 2026-05-04 | 09:00 | 2026-05-04 | 17:00 | Replacement of completely rusted and damaged 7/3.66 HTGS Earth wire & OPGW Wherever existing on 400KV Kalapaka-STPP-4 feeders | Yes | Approved | 400KV-SIMHADRI-KALPAKKA-2,3 39% each 400KV-SIMHADRI-GAZUWAKA D/C 10% each 400KV-VEMAGIRI_AP-SIMHADRI all lines shall be in service. | Line Circuits | 30-Apr-2026 | 20:49 | 01-May-2026 | 13:54
RQ106731 | OCC_237 | TANTRANSCO | 230KV-KUDANKULAM-S R PUDUR | TANTRANSCO | D | Monthly Maintenance | 2026-05-04 | 09:00 | 2026-05-04 | 14:00 |  | No | Rejected | Deferred by requester. | Line Circuits | 30-Apr-2026 | 20:04 | 01-May-2026 | 13:48
RQ106815 | OCC_237 | kptcl | MAIN BAY (407) OF 400KV-NELAMANGALA-HASSAN-1 AND NELAMANGALA - 400KV - BUS 1 @NELAMANGALA - 400KV | KPTCL | D | Breaker testing and maintenance works. | 2026-05-04 | 11:00 | 2026-05-04 | 17:00 |  | No | Rejected | Deferred by requester. | Bay | 30-Apr-2026 | 16:38 | 01-May-2026 | 13:48
RQ106918 | OCC_237 | PGCIL SR-1 | MAIN BAY (406) OF 400KV/220KV MEHBOOBNAGAR-ICT-2 AND MEHBOOBNAGAR - 400KV - BUS 2 @MEHBOOBNAGAR - 400KV | TGTRANSCO | C | Bay upgradation works uder ADDCAP- Construction works under SS-126 Package | 2026-05-04 | 09:00 | 2026-05-09 | 18:00 | Construction works under ADD-CAP. | Yes | Approved | Remaining bays shall be in service. | Bay | 30-Apr-2026 | 16:22 | 01-May-2026 | 13:54
RQ107040 | OCC_237 | PGCIL SR-2 | 400KV-GOOTY-SOMANAHALLI-1 | POWERGRID | D | AMP Works and attending shutdown nature defects in the line. | 2026-05-04 | 09:00 | 2026-05-04 | 17:00 |  | Yes | Approved | Subject to real time grid and voltage conditions. 400KV-BIDADI_PG-SOMANAHALLI D/C 25% each 400KV-PAVAGADA_PG-GOOTY D/C 18% each 400KV-NELAMANGALA-GOOTY-1 11% 400KV-TUMKUR-BIDADI_PG D/C 11% each 400KV-MYLASANDRA-KOLAR_AC-1 9% shall be in service. | Line Circuits | 30-Apr-2026 | 15:59 | 02-May-2026 | 04:28
RQ107031 | OCC_237 | PGCIL SR-2 | 220KV-PAVAGADA_PG-KSPDCL1 | KSPDCL | D | AMP of Terminal Equipments | 2026-05-04 | 18:00 | 2026-05-04 | 23:59 |  | Yes | Approved | Concurred, subject to real time grid conditions and KSPDCL concurrence. | Line Circuits | 30-Apr-2026 | 15:59 | 01-May-2026 | 14:11
RQ107032 | OCC_237 | PGCIL SR-2 | 400KV-BTPS-HIRIYUR-2 | KPTCL | D | AMP of Terminal Equipments | 2026-05-04 | 09:00 | 2026-05-04 | 17:00 |  | Yes | Approved | subject to real time grid conditions. 400KV-HIRIYUR-BTPS-1 35% 400KV-GUTTUR-BTPS-1 29% 400KV-HIRIYUR-GUTTUR D/C 15% each 400KV-PAVAGADA_PG-HIRIYUR-1 10% 400KV-RAICHUR_PG-RTPS D/C 7% each All BTPS ICTs shall be in service. | Line Circuits | 30-Apr-2026 | 15:59 | 01-May-2026 | 15:04
RQ106970 | OCC_237 | TGTRANSCO | 400KV-GAJWEL-NARSAPUR-2 | TGTRANSCO | C | For ct tan delta and relay testing by mrt wing and general maintenance works | 2026-05-04 | 10:00 | 2026-05-04 | 16:00 |  | Yes | Approved | 400KV-NARSAPUR-GAJWEL-1 38% 400KV-CHANDALAPUR-GAJWEL D/C 13% each 400KV-NARSAPUR-SHANKARAPALLY D/C 11% each shall be in service. | Line Circuits | 30-Apr-2026 | 14:54 | 01-May-2026 | 14:21
RQ106998 | OCC_237 | TGTRANSCO | 400KV-TIPPAPUR-CHANDALAPUR-2 | TGTRANSCO | C | Periodical testing of bay equipment | 2026-05-04 | 10:00 | 2026-05-05 | 18:00 |  | Yes | Approved | 400KV-TIPPAPUR-CHANDALAPUR-1 74% 400KV-JANAGAON-TIPPAPUR-2 4% 400KV-RAMADUGU-GAJWEL D/C 4% each shall be in service. | Line Circuits | 30-Apr-2026 | 14:54 | 01-May-2026 | 14:21
RQ107018 | OCC_237 | TGTRANSCO | 400KV-SRISAILAM_LEFT_BANK-DINDI-1 | TGTRANSCO | C | Annual Maintenance works at 400KV OD YARD- overhauling of operating mechanism box and cleaning of the contacts of isolator and earth switch,cleaning of porcelin insulators, replacement LS and Realy testing work | 2026-05-04 | 06:00 | 2026-05-04 | 17:00 |  | Yes | Approved | 400KV-DINDI-SRISAILAM_LEFT_BANK-2 52% 400KV-SRISAILAM_LEFT_BANK-SATTENPALLY D/C 13% each 400KV-MAHESHWARAM_TG-DINDI D/C 10% each 400KV-YEDULLA-DINDI-2 9% 400KV-MAHESHWARAM_TG-MAHESHWARAM_PG D/C 8% each All MAHESHWARAM ICTs shall be in service. | Line Circuits | 30-Apr-2026 | 14:54 | 01-May-2026 | 14:21
RQ106750 | OCC_237 | TGTRANSCO | ASUPAKA - 400KV B/R 1 | TGTRANSCO | C | PERDIOIDCAL TESTING | 2026-05-04 | 09:00 | 2026-05-04 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Bus Reactor | 30-Apr-2026 | 14:54 | 01-May-2026 | 13:54
RQ106491 | OCC_237 | kseb | A/R of 220KV-KOCHI-KALAMASSERY-1 | KSEB | D | Disc replacement work | 2026-05-04 | 09:00 | 2026-05-04 | 17:00 | Disc replacement work | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 30-Apr-2026 | 10:55 | 01-May-2026 | 13:54
RQ106462 | OCC_237 | WKTL | 765KV-WARANGAL(NEW)-CHILAKALURIPETA-1 | WKTL | C | For 24Hrs. Trail Run of NGR Bypass at Both Warangal and C'peta end | 2026-05-04 | 08:00 | 2026-05-05 | 08:00 | For 24Hrs. Trail Run of NGR Bypass at Both Warangal and C'peta end | Yes | Approved | Subject to NLDC approval and real time grid conditions. NEW-SR ATC reduction of 450 MW In SR Import. 765KV-WARANGAL(NEW)-CHILAKALURIPETA-2 44% 765kV-WARANGAL-MAHESHWARAM D/C 16% each 765kV-KURNOOL-MAHESHWARAM D/C 9% each 765kV-VEMAGIRI-C'PETA D/C 7% each All 765kV/400kV MAHESHWARAM_PG ICTs shall be in service. | Line Circuits | 30-Apr-2026 | 10:08 | 02-May-2026 | 05:01
RQ106466 | OCC_237 | WKTL | KUDGI_PG - 400KV - BUS 1 | PGCIL SR-2 | C | Extension/Interconnection of400kv Main Bus-1 from existing PGCIL Kudgi to WRSR New Narendra. | 2026-05-04 | 09:00 | 2026-05-09 | 18:00 | Extension/Interconnection of400kv Main Bus-1 from existing PGCIL Kudgi to WRSR New Narendra. | Yes | Approved | Remaining elements shall be in service. | Bus | 30-Apr-2026 | 10:08 | 01-May-2026 | 13:58
RQ106765 | OCC_237 | MTL | A/R of 400KV-NIZAMABAD-SHANKARAPALLY-1 | MTL | D | Required A/R in Non auto mode for defect rectification work | 2026-05-03 | 09:00 | 2026-05-03 | 17:00 | A/R OFF | No | Rejected | Deferred by requester. | Auto Reclosure | 30-Apr-2026 | 09:00 | 30-Apr-2026 | 10:33
RQ106828 | OCC_237 | kptcl | 400KV-TALGUPPA-HASSAN-1 | KPTCL | D | To provide LC for both NELAMANGALA-TALGUPPA-1 and 400KV-TALGUPPA-HASSAN-1to carry out stringing work of 110kV lines (4 ckt) benath existing 400 kV Dc line to execute work safely in nadamanchale station work | 2026-05-03 | 09:00 | 2026-05-03 | 18:00 |  | Yes | Approved | No Source for 400kV TALAGUPPA S/S. SHARAVATHY, and GERUSOPPA complex generation evacuation management and load management need to be done by KPTCL to keep the loadings of 220kV lines downstream within their limits. Subject to real time grid and voltage conditions. The Generation from SHARAVATHY, and GERUSOPPA complex shall be kept within 650 MW during the shutdown in order to maintain the line loadings within their thermal rating. | Line Circuits | 29-Apr-2026 | 12:06 | 30-Apr-2026 | 11:20
RQ106827 | OCC_237 | kptcl | 400KV-NELAMANGALA-TALGUPPA-1 | KPTCL | D | To provide LC for both NELAMANGALA-TALGUPPA-1 and 400KV-TALGUPPA-HASSAN-1to carry out stringing work of 110kV lines (4 ckt) benath existing 400 kV Dc line to execute work safely in nadamanchale station work | 2026-05-03 | 09:00 | 2026-05-03 | 18:00 |  | Yes | Approved | No Source for 400kV TALAGUPPA S/S. SHARAVATHY, and GERUSOPPA complex generation evacuation management and load management need to be done by KPTCL to keep the loadings of 220kV lines downstream within their limits. Subject to real time grid and voltage conditions. The Generation from SHARAVATHY, and GERUSOPPA complex shall be kept within 650 MW during the shutdown in order to maintain the line loadings within their thermal rating. | Line Circuits | 29-Apr-2026 | 12:04 | 30-Apr-2026 | 11:20
RQ106843 | OCC_237 | kptcl | 220KV-YELHANKA-YELAHANKA DG-2 | KPTCL | D | For relay calibration works by RT, conditioning monitoring tests, Quarterly maintenance works and attending hotspots | 2026-05-03 | 13:30 | 2026-05-03 | 17:30 | 220kV Manyatha station 80MW and 220kV HBR station loads of 130MW shall be changed over onto Hoody staton | Yes | Approved | Detailed load management plan submitted by KPTCL is as follows: Both 220kV Singanayakanahalli Line-1 & Line 2 Lines have 2000sq.mm UG Cable. Its current carrying capacity of each line is 1250A. Current setting in the relay is 1200A i.e 400MW. Total load on both PGCIL Singanayakanahalli Line-1 & Line 2 is 500MW (1350A) . 350MW can be managed with one of the circuits without any problem. Hence following load changeover shall be made: 220kV Manyatha 1 & 220kV Manyatha 2 Lines shall be opened at 220kV Sahakarnagar GIS station and 220kV Manyatha station 80MW and 220kV HBR station loads of 140MW shall be released and changed over onto Hoody staton on 03.05.2026 from 09:30 to 17:30hrs. The same need to be adhered prior to the shutdown. N-1 limit for 400kV/220kV HOODY ICTs is 333 MW each. N-1 limit for 220KV-YELHANKA-YELAHANKA DG D/C is 220 MW for each line and thermal rating is 450 MVA for each line. 220KV-YELHANKA-YELAHANKA DG-1 91% Line loadings are already crossing their N-1 limits. Shutdown is subjected to real time grid conditions and line loadings and adherence to load management plan by KPTCL. Shutdown to be availed one after another. | Line Circuits | 29-Apr-2026 | 12:02 | 30-Apr-2026 | 16:07
RQ106842 | OCC_237 | kptcl | 220KV-YELHANKA-YELAHANKA DG-1 | KPTCL | D | For relay calibration works by RT, conditioning monitoring tests, Quarterly maintenance works and attending hotspots | 2026-05-03 | 10:00 | 2026-05-03 | 13:30 | 220kV Manyatha station 80MW and 220kV HBR station loads of 130MW shall be changed over onto Hoody staton | Yes | Approved | Detailed load management plan submitted by KPTCL is as follows: Both 220kV Singanayakanahalli Line-1 & Line 2 Lines have 2000sq.mm UG Cable. Its current carrying capacity of each line is 1250A. Current setting in the relay is 1200A i.e 400MW. Total load on both PGCIL Singanayakanahalli Line-1 & Line 2 is 500MW (1350A) . 350MW can be managed with one of the circuits without any problem. Hence following load changeover shall be made: 220kV Manyatha 1 & 220kV Manyatha 2 Lines shall be opened at 220kV Sahakarnagar GIS station and 220kV Manyatha station 80MW and 220kV HBR station loads of 140MW shall be released and changed over onto Hoody staton on 03.05.2026 from 09:30 to 17:30hrs. The same need to be adhered prior to the shutdown. N-1 limit for 400kV/220kV HOODY ICTs is 333 MW each. N-1 limit for 220KV-YELHANKA-YELAHANKA DG D/C is 220 MW for each line and thermal rating is 450 MVA for each line. 220KV-YELHANKA-YELAHANKA DG-2 91% Line loadings are already crossing their N-1 limits. Shutdown is subjected to real time grid conditions and line loadings and adherence to load management plan by KPTCL. Shutdown to be availed one after another. | Line Circuits | 29-Apr-2026 | 12:00 | 30-Apr-2026 | 16:07
RQ106653 | OCC_237 | aptransco | 400KV/220KV HINDUPUR-ICT-3 | APTRANSCO | D | "1. Half yearly Maintenance works 2. Periodical Relay testing of ICT *Note : ICT-1,2&4 Will be in service" | 2026-05-03 | 10:00 | 2026-05-03 | 16:00 | Annual maintenance works | Yes | Approved | Load Management need to be done by AP. N-1 limit for HINDUPUR ICTs is 238 MW each. Remaining all other HINDUPUR ICTs 26% each shall be in service. | Transformer | 29-Apr-2026 | 10:12 | 30-Apr-2026 | 10:42
RQ106797 | OCC_237 | aptransco | TIE BAY (411) OF 400KV-VIJAYAWADA-SATTENPALLY-1 AND 400KV-VTPS_IV-VIJAYAWADA-1 @VIJAYAWADA - 400KV | PGCIL SR-1 | D | Replacement of old BHEL make Circuit Breakers in 411 (Tie) & 412 (main) bays of 400KV Nunna, VTPS feeder pertaining to APTRANSCO at 400KV SS, PGCIL, Nunna with 2Nos. CGL make Breakers available under PSDF-II scheme" | 2026-05-03 | 07:00 | 2026-05-03 | 18:00 | On 02.05.2026 from 07:00Hrs to 18:00Hrs, for replacement of protection Coupler at both ends of 400KV Nunna-VTPS feeder. (LC requested on both 411 & 412 bays). | Yes | Approved | Remaining bays shall be in service. FTC is required. | Bay | 29-Apr-2026 | 10:12 | 30-Apr-2026 | 10:33
RQ107086 | OCC_237 | aptransco | 400KV-SIMHADRI-KALPAKKA-4 | APTRANSCO | D | Replacement of completely rusted and damaged 7/3.66 HTGS Earth wire & OPGW Wherever existing on 400KV Kalapaka-STPP-4 feeders | 2026-05-03 | 09:00 | 2026-05-03 | 17:00 | Replacement of completely rusted and damaged 7/3.66 HTGS Earth wire & OPGW Wherever existing on 400KV Kalapaka-STPP-4 feeders | Yes | Approved | 400KV-SIMHADRI-KALPAKKA-2,3 39% each 400KV-SIMHADRI-GAZUWAKA D/C 10% each 400KV-VEMAGIRI_AP-SIMHADRI all lines shall be in service. | Line Circuits | 29-Apr-2026 | 10:12 | 30-Apr-2026 | 10:33
RQ106764 | OCC_237 | MTL | A/R of 400KV-NIZAMABAD-SHANKARAPALLY-1 | MTL | D | Required A/R in Non auto mode for defect rectification work | 2026-05-02 | 09:00 | 2026-05-02 | 17:00 | A/R OFF | No | Rejected | Deferred by requester. | Auto Reclosure | 29-Apr-2026 | 09:15 | 29-Apr-2026 | 11:01
RQ106734 | OCC_237 | KNTL | MAIN BAY (413) OF 400KV/220KV KOPPAL-ICT-5 AND KOPPAL - 400KV - BUS 2 @KOPPAL - 400KV | KNTL | D | "Yearly Bay equipment testing and preventive maintenance. " | 2026-05-02 | 09:00 | 2026-05-02 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 29-Apr-2026 | 09:01 | 29-Apr-2026 | 11:16
RQ106907 | OCC_237 | PGCIL SR-1 | 765KV/400KV KURNOOL_PG-ICT-3 | PGCIL SR-1 | D | SS126- ICT-3 augmentation taking HOt spare unit into service- spare changeover after 1 month of ICT charging at Kurnool SS | 2026-05-02 | 08:30 | 2026-05-02 | 20:00 | Construction works | No | Rejected | Deferred by requester. | Transformer | 28-Apr-2026 | 18:33 | 29-Apr-2026 | 11:01
RQ106961 | OCC_237 | TGTRANSCO | 400KV-CHOUTUPPAL-KHAMMAM_PG-2 | TGTRANSCO | C | For replacement of damaged spacers at loc No 299-384 by the agency | 2026-05-02 | 08:00 | 2026-05-04 | 18:00 |  | Yes | Approved | 400KV-CHOUTUPPAL-KHAMMAM_PG-1 26% 400KV-CHOUTUPPAL-YADADRI TPP D/C 13% each 400KV-MAHESHWARAM_TG-MAMIDAPALLI D/C 9% each 400KV-KHAMMAM_PG-VIJAYAWADA-1 9% 400KV-KTPS_VII-JULURUPADU D/C 8% each shall be in service. | Line Circuits | 28-Apr-2026 | 13:32 | 29-Apr-2026 | 14:25
RQ106964 | OCC_237 | TGTRANSCO | 400KV/220KV DICHPALLY-ICT-2 | TGTRANSCO | C | complete overhauling and replacement, to arrest oil seepages and ensure the long-term reliability of the equipment. As this activity involves complete oil draining, removal of the bell jar/main inspection doors, dismantling of 400kV, 220kV, and 33kV bushings, and extensive Hot Oil Circulation (HOC) and vacuuming, a continuous shutdown is required. of all gaskets | 2026-05-02 | 07:00 | 2026-05-13 | 16:00 |  | Yes | Approved | Load management needs to be done by TG. N-1 limit for DICHPALLY-ICTs is 219 MW for 315 MVA ICTs each and 347 MW for 500 MVA ICT. 400KV/220KV DICHPALLY-ICT-4 37% 400KV/220KV DICHPALLY-ICT-1 24% 400KV/220KV DICHPALLY-ICT-3 24% All RAMADUGU ICTs shall be in service. | Transformer | 28-Apr-2026 | 13:32 | 29-Apr-2026 | 14:25
RQ107431 | OCC_2371 | kptcl | 400KV-HEBBANAHALLI-UPCL-2 | KARNATAKA | C | "Retain the existing Tower No. 43 and removal of conductor from Tower No. 42 (DD +06) to Tower No. 44 (DC+00). At the same time providing backstay support for both Towers 42 and 44. and Erection of Tower No. 42A (DD +06), Tower No. 43,(DD+09) and Tower No. 01 (MD+00)" | 2026-05-06 | 06:00 | 2026-05-31 | 23:59 | Establishing 2X500MVA, 400/220kV sub-station at Kadandale in Moodabidre Taluk, Dakshina Kannada District. Shutdown required continuous from 02.05.2026 to 10.06.2026. | Yes | Approved | FTC is required. Shutdown to be availed during at least one unit outage of UPCL. As per mail received from KPTCL dated 04.05.2026 KPTCL submitted the following: "It is requested to approve 400kV UPCL-Hebbanally DC lines from 6th May 2026. One unit at UPCL will be taken out before availing S/D of lines. 500 MW ex-bus generation will be maintained at UPCL till restoration of lines. The LGB will be managed by KPTCL by managing the Geneartin at Varahi, SGS and STRP in real time. The Bus coupler at Kemar will be closed prior to availing S/D of 400kV Lines." Accordingly the same need to be adhered by KPTCL and proper load and generation management need to be done by KPTCL. SPS at UPCL need to be disabled. | Line Circuits | 28-Apr-2026 | 12:28 | 29-Apr-2026 | 16:00
RQ106841 | OCC_237 | kptcl | 400KV-HOODY-DEVANAHALLI-2 | KPTCL | D | To carry out tan delta test of CT, CVT and DCRM test of breakers. | 2026-05-02 | 09:00 | 2026-05-02 | 17:00 | Due to high induction tan delta for Devanahalli Line-1&2 equipment's could not be conducted by R&D and station staff. Hence requesting LC for 400KV-HOODY-DEVANAHALLI-2 | Yes | Rejected | Subject to furnishing of all detailed studies PSSE by KA & real time grid conditions | Line Circuits | 28-Apr-2026 | 12:26 | 29-Apr-2026 | 13:14
RQ106840 | OCC_237 | kptcl | 400KV-HOODY-DEVANAHALLI-1 | KPTCL | D | To carry out tan delta test of CT, CVT and DCRM test of breakers. | 2026-05-02 | 09:00 | 2026-05-02 | 17:00 | Due to high induction tan delta for Devanahalli Line-1&2 equipment's could not be conducted by R&D and station staff. Hence requesting LC for 400KV-HOODY-DEVANAHALLI-1 | Yes | Rejected | Subject to furnishing of all detailed studies PSSE by KA & real time grid conditions | Line Circuits | 28-Apr-2026 | 12:24 | 29-Apr-2026 | 13:14
RQ107386 | OCC_2371 | kptcl | 400KV-HEBBANAHALLI-UPCL-1 | KARNATAKA | C | Retain the existing Tower No. 43 and removal of conductor from Tower No. 42 (DD +06) to Tower No. 44 (DC+00). At the same time providing backstay support for both Towers 42 and 44. and Erection of Tower No. 42A (DD +06), Tower No. 43,(DD+09) and Tower No. 01 (MD+00) | 2026-05-06 | 06:00 | 2026-05-31 | 23:59 | Establishing 2X500MVA, 400/220kV sub-station at Kadandale in Moodabidre Taluk, Dakshina Kannada District. Shutdown required continuous from 02.05.2026 to 10.06.2026. | Yes | Approved | FTC is required. Shutdown to be availed during at least one unit outage of UPCL. As per mail received from KPTCL dated 04.05.2026 KPTCL submitted the following: "It is requested to approve 400kV UPCL-Hebbanally DC lines from 6th May 2026. One unit at UPCL will be taken out before availing S/D of lines. 500 MW ex-bus generation will be maintained at UPCL till restoration of lines. The LGB will be managed by KPTCL by managing the Geneartin at Varahi, SGS and STRP in real time. The Bus coupler at Kemar will be closed prior to availing S/D of 400kV Lines." Accordingly the same need to be adhered by KPTCL and proper load and generation management need to be done by KPTCL. SPS at UPCL need to be disabled. | Line Circuits | 28-Apr-2026 | 12:22 | 29-Apr-2026 | 16:00
RQ106808 | OCC_237 | kptcl | 400KV/220KV GUTTUR-ICT-1 | KPTCL | D | Submitting proposal for OLTC Bevel gear bearing to be replaced | 2026-05-02 | 10:00 | 2026-05-02 | 17:00 |  | Yes | Rejected | Load Management need to be done by KPTCL. ICT loadings are crossing their N-1 limit even on weekends. N-1 limit for GUTTUR ICTs is 202 MW each. | Transformer | 28-Apr-2026 | 12:20 | 29-Apr-2026 | 12:58
RQ106537 | OCC_237 | NTPC | 400KV-KUDGI_PG-KUDGI_NTPC-1 | KTL | C | yearly line side equipment maintenance | 2026-05-02 | 07:00 | 2026-05-03 | 19:00 |  | Yes | Approved | 400KV-KUDGI_PG-KUDGI_NTPC-2,3,4 33% each shall be in service. | Line Circuits | 28-Apr-2026 | 10:22 | 29-Apr-2026 | 14:26
RQ106552 | OCC_237 | aptransco | 132KV-ALAMPUR-KURNOOL_AP-1 | APTRANSCO,TGTRANSCO | D | Replacement of 132 KV Alampur feeder bay CTs at 132 KV SS Kurnool under RMI-22-23 | 2026-05-02 | 06:00 | 2026-05-02 | 18:00 | Replacement of 132 KV Alampur feeder bay CTs at 132 KV SS Kurnool under RMI-22-23 | Yes | Approved | Concurred, subject to load management by AP and TG. | Line Circuits | 28-Apr-2026 | 10:17 | 29-Apr-2026 | 11:01
RQ106633 | OCC_237 | aptransco | KALPAKKA - 400KV B/R 1 | APTRANSCO | D | For general maintenance of yard equipment and for periodical bay equipment and relay testing. | 2026-05-02 | 09:00 | 2026-05-02 | 17:00 | Annual maintenance works | Yes | Approved | Concurred, subject to real time voltage conditions. | Bus Reactor | 28-Apr-2026 | 10:17 | 29-Apr-2026 | 11:07
RQ106665 | OCC_237 | aptransco | 400KV/220KV NARNOOR-ICT-3 | ANDHRA PRADESH | D | For Annualy and Quarterly maintenance works(for ICT Testings) | 2026-05-02 | 10:00 | 2026-05-02 | 16:00 | Annual maintenance works | Yes | Approved | Load Management need to be done by AP. N-1 limit for NARNOOR ICTs is 200 MW for 315 MVA ICTs each and 316 MW for 500 MVA ICT. 400KV/220KV NARNOOR-ICT-1 34% 400KV/220KV NARNOOR-ICT-2 34% All GOOTY ICTs shall be in service. | Transformer | 28-Apr-2026 | 10:17 | 29-Apr-2026 | 12:58
RQ107085 | OCC_237 | aptransco | 400KV-SIMHADRI-KALPAKKA-4 | APTRANSCO | D | Replacement of completely rusted and damaged 7/3.66 HTGS Earth wire & OPGW Wherever existing on 400KV Kalapaka-STPP-4 feeders | 2026-05-02 | 09:00 | 2026-05-02 | 17:00 | Replacement of completely rusted and damaged 7/3.66 HTGS Earth wire & OPGW Wherever existing on 400KV Kalapaka-STPP-4 feeders | Yes | Approved | 400KV-SIMHADRI-KALPAKKA-2,3 39% each 400KV-SIMHADRI-GAZUWAKA D/C 10% each 400KV-VEMAGIRI_AP-SIMHADRI all lines shall be in service. | Line Circuits | 28-Apr-2026 | 10:17 | 29-Apr-2026 | 11:07
RQ107701 | PNOCC | aptransco | GUDIWADA - 400KV B/R 1 | APTRANSCO | C | For commissioning of DGA equipment | 2026-05-01 | 09:00 | 2026-05-01 | 16:00 | company personnel is coming to check all parameters | Yes | Approved | Concurred, subject to real time grid conditions. | Bus Reactor | 27-Apr-2026 | 17:42 | 29-Apr-2026 | 09:28
RQ107703 | PNOCC | aptransco | 400KV-GUDDIGUDEM-HINDUJA-2 | APTRANSCO | C | tripping’s are due to inadequate jumper clearances of the long jumper connected between the top conductor and bottom conductor at Loc. 567, Transposition Tower. | 2026-05-02 | 10:00 | 2026-05-02 | 13:00 | Elongation of the jumpers during high temperature, gale, and lightning conditions is likely causing tripping/AR operations, especially during afternoon hours. | Yes | Approved | 400KV-HINDUJA-KALPAKKA D/C 36% each 400KV-GUDDIGUDEM-HINDUJA-1 29% 400KV-KV_KOTA-VEMAGIRI_AP D/C 22% each 400KV-VEMAGIRI_PG-VEMAGIRI_AP D/C 13% each All VEMAGIRI ICTs shall be in service. Timelines of the shutdown to be adhered properly. Consecutive shutdowns at the same station. | Line Circuits | 27-Apr-2026 | 18:44 | 29-Apr-2026 | 14:17
RQ107704 | PNOCC | aptransco | 400KV-GUDDIGUDEM-HINDUJA-1 | APTRANSCO | C | tripping’s are due to inadequate jumper clearances of the long jumper connected between the top conductor and bottom conductor at Loc. 567, Transposition Tower. | 2026-05-02 | 14:00 | 2026-05-02 | 17:00 | Elongation of the jumpers during high temperature, gale, and lightning conditions is likely causing tripping/AR operations, especially during afternoon hours. | Yes | Approved | 400KV-HINDUJA-KALPAKKA D/C 36% each 400KV-GUDDIGUDEM-HINDUJA-2 29% 400KV-KV_KOTA-VEMAGIRI_AP D/C 22% each 400KV-VEMAGIRI_PG-VEMAGIRI_AP D/C 13% each All VEMAGIRI ICTs shall be in service. Timelines of the shutdown to be adhered properly. Consecutive shutdowns at the same station. | Line Circuits | 27-Apr-2026 | 18:47 | 29-Apr-2026 | 14:17
RQ106895 | OCC_237 | PGCIL SR-1 | 765KV-RAICHUR_PG-SHOLAPUR-2 | RSTCL | C | Tower erection works of AP 2/0 and AP 3/0 - 765KV KOPPAL RAICHUR LINE | 2026-05-01 | 07:00 | 2026-05-03 | 18:00 | Construction works | Yes | Approved | 765kV Raichur-Solapur-1 51%,765kV Kurnool-Maheshwaram-D/C 10%, 765kV Warora-Warangal_new-D/C 9%, 765kV Wardha-Nizamabad-D/C 8%, 765kV Angul-Srikakulam-D/C 4%, 400kV Kolhapur-Kudgi-D/C 4% and 765/400kV Nizambad ICTs 3%. Major change observed in voltages 3-2 kV at following 765kV stations :NIZAMABAD ,WARANGAL_NEW,SRIKAKULAM ,MAHESWARAM ,RAICHUR-PG ,VEMAGIRI_PG ,CPETA-PG ,KURNOOL-PG ,CUDDAPAH-PG. Remaining lines shall be in service. Tentative TTC/ATC reduction in SR import/export by 150/700MW. | Line Circuits | 27-Apr-2026 | 16:16 | 29-Apr-2026 | 09:44
RQ106904 | OCC_237 | PGCIL SR-1 | 400KV-KHAMMAM_PG-VIJAYAWADA-1 | POWERGRID | D | Oil sample of Line CT | 2026-05-01 | 10:00 | 2026-05-01 | 12:00 | Shutdown nature maintenance works. | Yes | Approved | 400KV-VTPS_IV-VIJAYAWADA-1 53% 400KV-SURYAPET-VTPS_IV D/C 18% each 400KV-KTPS_VII-JULURUPADU D/C 11% each 400KV-CHOUTUPPAL-KHAMMAM_PG D/C 10% each All KHAMMAM ICTs shall be in service. Timelines to be strictly adhered. | Line Circuits | 27-Apr-2026 | 16:16 | 29-Apr-2026 | 09:48
RQ106906 | OCC_237 | PGCIL SR-1 | 765KV/400KV KURNOOL_PG-ICT-3 | PGCIL SR-1 | D | SS126: ICT-3 related Tuning of CSD after charging in all 722,723, 414,415 CB's | 2026-05-01 | 08:00 | 2026-05-01 | 20:00 | Construction works | Yes | Approved | Subject to NLDC approval and real time grid conditions. 765KV/400KV KURNOOL_PG-ICT-1 32% 765KV/400KV KURNOOL_PG-ICT-2 32% All RAICHUR ICTs and MAHESHWARAM ICTs shall be in service. N-1 limit for 765KV/400KV KURNOOL_PG-ICTs is 1020 MW each. | Transformer | 27-Apr-2026 | 16:16 | 29-Apr-2026 | 10:42
RQ106908 | OCC_237 | PGCIL SR-1 | 400KV/220KV CUDDAPAH-ICT-1 | PGCIL SR-1 | C | Continuation of shutdown for FFPH retrofitting works under ADD CAP of 400/220 Kv ICt 1 . | 2026-05-01 | 09:00 | 2026-05-05 | 18:30 | Construction works under ADD-CAP. | Yes | Approved | Subject to ICT loadings to be within their N-1 limit. N-1 limit for 400kV / 220kV CUDDAPAH ICTs is 204 MW for 315 MVA ICT each and 324 MW for 500 MVA ICT each. Load Management need to be done by AP. 400kV/220kV CUDDAPAH ICT-2,3 25% & 39% each 400kV-CUDDAPAH-CHITTOOR 400kV-CUDDAPAH-TUMKUR D/C shall be in service along with all other lines.Due to the long shutdown prior to facilitating the shutdown the need to be informed to AP and all the downstream network shall be in service. | Transformer | 27-Apr-2026 | 16:16 | 29-Apr-2026 | 09:48
RQ106911 | OCC_237 | PGCIL SR-1 | 400KV/220KV MEHBOOBNAGAR-ICT-2 | TGTRANSCO | D | Bay upgradation works uder ADDCAP- Construction works under SS-126 Package | 2026-05-01 | 18:00 | 2026-05-01 | 23:30 | Construction works under ADD-CAP. | Yes | Approved | Load Management to be done by TG. N-1 limit for MEHBOOBNAGAR ICTs is 226 MW for 315 MVA ICT each and 358 MW for 500 MVA ICT each. 400KV/220KV MEHBOOBNAGAR-ICT-1 31% 400KV/220KV MEHBOOBNAGAR-ICT-4 31% 400KV/220KV MEHBOOBNAGAR-ICT-3 20% shall be in service. | Transformer | 27-Apr-2026 | 16:16 | 29-Apr-2026 | 09:48
RQ107513 | OCC_2371 | PGCIL SR-1 | MAIN BAY (406) OF 400KV/220KV MEHBOOBNAGAR-ICT-2 AND MEHBOOBNAGAR - 400KV - BUS 2 @MEHBOOBNAGAR - 400KV | TGTRANSCO | C | Constuction works under SS-126 for Bay upgradation under ADDCAP. | 2026-05-01 | 09:00 | 2026-05-03 | 23:00 | Construction works under ADD-CAP. | Yes | Approved | Remaining bays shall be in service. | Bay | 27-Apr-2026 | 16:16 | 29-Apr-2026 | 09:48
RQ107015 | OCC_237 | TGTRANSCO | SRISAILAM_LEFT_BANK - 400KV - BUS 1 | TGGENCO | C | Annual Maintenance works at 400KV GIS- Reconditioning of SF6 gas, repalcement of molecular absorbents in the BUS Ducts of 15 Bays | 2026-05-01 | 06:00 | 2026-05-20 | 17:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Bus | 27-Apr-2026 | 13:48 | 29-Apr-2026 | 09:44
RQ107017 | OCC_237 | TGTRANSCO | 400KV-NARNOOR-SRISAILAM_LEFT_BANK-1 | APTRANSCO,TGTRANSCO | C | Annual Maintenance works at 400KV OD YARD- overhauling of operating mechanism box and cleaning of the contacts of isolator and earth switch,cleaning of porcelin insulators and Realy testing works [From:04/05/2026 06:00 To 06/05/2026 17:00] | 2026-05-01 | 07:00 | 2026-05-02 | 17:00 | Please consider [From:04/05/2026 06:00 To 06/05/2026 17:00] | Yes | Approved | 400KV-DINDI-SRISAILAM_LEFT_BANK D/C 33% each 400KV-KURNOOL_PG-NARNOOR D/C 28% each 400KV-MAHESHWARAM_TG-MAHESHWARAM_PG D/C 17% each 400KV-YEDULA-DINDI-2 15% shall be in service. | Line Circuits | 27-Apr-2026 | 13:48 | 29-Apr-2026 | 09:44
RQ106796 | OCC_237 | aptransco | MAIN BAY (412) OF 400KV-VTPS_IV-VIJAYAWADA-1 AND VIJAYAWADA - 400KV - BUS 2 @VIJAYAWADA - 400KV | PGCIL SR-1 | C | Replacement of old BHEL make Circuit Breakers in 411 (Tie) & 412 (main) bays of 400KV Nunna, VTPS feeder pertaining to APTRANSCO at 400KV SS, PGCIL, Nunna with 2Nos. CGL make Breakers available under PSDF-II scheme" | 2026-05-01 | 08:00 | 2026-05-02 | 18:00 | Replacement of old BHEL make Circuit Breakers in 411 (Tie) & 412 (main) bays of 400KV Nunna, VTPS feeder pertaining to APTRANSCO at 400KV SS, PGCIL, Nunna with 2Nos. CGL make Breakers available under PSDF-II scheme" | Yes | Approved | Remaining bays shall be in service. FTC is required. | Bay | 27-Apr-2026 | 11:18 | 29-Apr-2026 | 09:48
RQ107084 | OCC_237 | aptransco | 400KV-SIMHADRI-KALPAKKA-4 | APTRANSCO | D | Replacement of completely rusted and damaged 7/3.66 HTGS Earth wire & OPGW Wherever existing on 400KV Kalapaka-STPP-4 feeders | 2026-05-01 | 09:00 | 2026-05-01 | 17:00 | Replacement of completely rusted and damaged 7/3.66 HTGS Earth wire & OPGW Wherever existing on 400KV Kalapaka-STPP-4 feeders | Yes | Approved | 400KV-SIMHADRI-KALPAKKA-2,3 39% each 400KV-SIMHADRI-GAZUWAKA D/C 10% each 400KV-VEMAGIRI_AP-SIMHADRI all lines shall be in service. | Line Circuits | 27-Apr-2026 | 11:18 | 29-Apr-2026 | 10:15
RQ107385 | OCC_2371 | kptcl | 220KV-KUDGI_NTPC-SAVALAGI-2 | KPTCL | C | Stringing of conductor between location 1 and 2 covering a distance of 18.5 km in bilagi taluk. | 2026-05-01 | 08:00 | 2026-05-03 | 18:00 | Establishing 2X100MVA, 220/110/11KV Sub-station at Bilagi in Bilagi Taluk, Bagalkot District, with associated 220 kV Kudagi-Vajramatti line (18.455 Kms), - on Total turnkey basis. As Krishna river crossing work of first circuit to be completed by 25.05.2026 | Yes | Rejected | Deferred by requester as per telephonic communication received from Utility. | Line Circuits | 27-Apr-2026 | 10:12 | 29-Apr-2026 | 09:58
RQ107384 | OCC_2371 | kptcl | 220KV-KUDGI_NTPC-SAVALAGI-1 | KPTCL | C | Stringing of conductor between location 1 and 2 covering a distance of 18.5 km in bilagi taluk. | 2026-05-01 | 08:00 | 2026-05-03 | 18:00 | Establishing 2X100MVA, 220/110/11KV Sub-station at Bilagi in Bilagi Taluk, Bagalkot District, with associated 220 kV Kudagi-Vajramatti line (18.455 Kms), - onTotal turnkey basis. As Krishna river crossing work of first circuit to be completed by 25.05.2026 | Yes | Rejected | Deferred by requester as per telephonic communication received from Utility. | Line Circuits | 27-Apr-2026 | 10:10 | 29-Apr-2026 | 09:58
RQ108724 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | PID scanning works old insulators. | 2026-05-19 | 08:00 | 2026-05-19 | 18:00 | PID Scanning of insulator. Please approve up to 31.05.2026 | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 08-May-2026 | 19:30 | 16-May-2026 | 11:08
RQ108761 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | Live line PID testing of insulator in line | 2026-05-19 | 07:00 | 2026-05-19 | 18:00 | Nil | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 10-May-2026 | 13:18 | 16-May-2026 | 11:08
RQ108908 | PNOCC | PGCIL SR-1 | A/R of 400KV-KHAMMAM_PG-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-19 | 07:00 | 2026-05-19 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 14-May-2026 | 18:10 | 16-May-2026 | 11:08
RQ108914 | PNOCC | PGCIL SR-1 | A/R of 400KV-KURNOOL_PG-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-19 | 07:00 | 2026-05-19 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 14-May-2026 | 18:13 | 16-May-2026 | 11:08
RQ108925 | PNOCC | PGCIL SR-1 | MAIN BAY (413) OF 400KV-VIJAYAWADA-NELLORE_AP-3 AND VIJAYAWADA - 400KV - BUS 1 @VIJAYAWADA - 400KV | PGCIL SR-1 | D | SF6 Dew point measurement | 2026-05-19 | 09:00 | 2026-05-19 | 13:00 | SF6 Dew point measurement | Yes | Approved | Remaining bays shall be in service. Consecutive shutdown. | Bay | 15-May-2026 | 17:20 | 16-May-2026 | 11:08
RQ108926 | PNOCC | PGCIL SR-1 | TIE BAY (414) OF 400KV-VIJAYAWADA-NELLORE_AP-3 AND 400KV-NELLORE_PG-VIJAYAWADA-1 @VIJAYAWADA - 400KV | PGCIL SR-1 | D | SF6 Dew point measurement | 2026-05-19 | 14:00 | 2026-05-19 | 17:30 | SF6 Dew point measurement | Yes | Approved | Remaining bays shall be in service. Consecutive shutdown. | Bay | 15-May-2026 | 17:28 | 16-May-2026 | 11:08
RQ109240 | PNOCC | KNTL | KOPPAL - 220KV - BUS 4 | INDIGRID | D | Yearly Bay equipment testing and preventive maintenance. | 2026-05-28 | 09:00 | 2026-05-28 | 17:00 |  | Yes | Approved | Remaining all elements shall be in service. | Bus | 21-May-2026 | 18:14 | 25-May-2026 | 10:49
RQ109272 | PNOCC | PGCIL SR-2 | A/R of 220KV-RENEW_SURYA_OJAS_KOPPAL_W-KOPPAL-1 | RSOPL | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 13/0 - 14/0 by Hotline Method. | 2026-05-28 | 07:00 | 2026-05-28 | 19:00 | Line Shutdowns were approved under Mid OCC_2371. However, IPP has denied to consent citing, substantial financial implication due to expected generation loss during shutdown period. In view of the commissioning target of 400 kV Gadag II - Koppal II D/C Transmission line by Mid of June 2026 and commencement of monsoon rains in North Karnataka area, it is planned to take up the powerline crossing works by hotline method. | Yes | Approved | Concurrence from the concerned RE developers is submitted by PGCIL SR-2 for taking A/R into Non-Auto mode through mail communication dated 26.05.20206. Further, there is no N-1 redundancy available for the RE generating plants connected at 400kV KOPPAL PSS. Also, it is to be duly noted that the peak wind season in the Southern Region has already commenced, and multiple line tripping have been observed in nearby grid elements during the past few days. 400kV-KOPPAL-GADAG D/C is already under shutdown due to tower collapse. | Auto Reclosure | 22-May-2026 | 22:10 | 25-May-2026 | 10:19
RQ109279 | PNOCC | PGCIL SR-2 | A/R of 220KV-KOPPAL-RENEW_SURYA_KOPPAL-1 | RENEW POWER PVT LTD | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 13/0 - 14/0 by Hotline Method. | 2026-05-28 | 07:00 | 2026-05-28 | 19:00 | Line Shutdowns were approved under Mid OCC_2371. However, IPP has denied to consent citing, substantial financial implication due to expected generation loss during shutdown period. In view of the commissioning target of 400 kV Gadag II - Koppal II D/C Transmission line by Mid of June 2026 and commencement of monsoon rains in North Karnataka area, it is planned to take up the powerline crossing works by hotline method. | Yes | Approved | Concurrence from the concerned RE developers is submitted by PGCIL SR-2 for taking A/R into Non-Auto mode through mail communication dated 26.05.20206. Further, there is no N-1 redundancy available for the RE generating plants connected at 400kV KOPPAL PSS. Also, it is to be duly noted that the peak wind season in the Southern Region has already commenced, and multiple line tripping have been observed in nearby grid elements during the past few days. 400kV-KOPPAL-GADAG D/C is already under shutdown due to tower collapse. | Auto Reclosure | 22-May-2026 | 22:10 | 25-May-2026 | 10:19
RQ109297 | PNOCC | PGCIL SR-2 | MAIN BAY (406) OF 400KV-BIDADI_PG-SOMANAHALLI-2 AND SOMANAHALLI - 400KV - BUS 2 @SOMANAHALLI - 400KV | PGCIL SR-2 | C | CB drive overhauling works | 2026-05-28 | 12:30 | 2026-05-29 | 20:00 |  | Yes | Approved | Shutdown to be availed only after 12:00 HRS or subject to voltage condition in the near vicinity. Remaining bays shall be in service. | Bay | 24-May-2026 | 17:29 | 25-May-2026 | 10:36
RQ109310 | EMERGENCY | aptransco | 400KV-KALPAKKA-VEMAGIRI_AP-1 | APTRANSCO | C | For attending redhot on Y-Phase Circuit Breaker flexible Pad Clamp in 400kV Kalapaka-Vemagiri line towards line isolator at Kalapaka SS | 2026-05-25 | 10:33 | 2026-05-25 | 13:33 |  | Yes | Approved | Other lines connected to Kalpakka & Vemagiri shall be in service | Line Circuits | 25-May-2026 | 10:54 | 25-May-2026 | 10:57
RQ109365 | EMERGENCY | TANTRANSCO | 400KV/110KV ALAMATHY-ICT-1 | TANTRANSCO | D | To attend twin moose dropper cut in ICT 1 400/110KV 200MVA LV 89D isolator y phase incoming dropper. | 2026-05-26 | 11:20 | 2026-05-26 | 15:00 | During the period of shutdown 400/110KV 200MVA ICT 1 will not be in service.Hence 400/110KV 200MVA ICT 2 and ICT 6 will be in service. | Yes | Approved | Other ICTs shall be in service. Load Management to be done by TANTRANSCO. | Transformer | 26-May-2026 | 11:28 | 26-May-2026 | 11:31
RQ109366 | EMERGENCY | TGTRANSCO | MAIN BAY (401) OF 400KV-KETHIREDDYPALLY-SHANKARAPALLY-1 AND KETHIREDDYPALLY - 400KV - BUS 1 @KETHIREDDYPALLY - 400KV | TGTRANSCO | C | LC on emergency basis on 401 Bay, for attending the CB status indication in BUSBAR relay. | 2026-05-26 | 12:30 | 2026-05-26 | 19:00 | Please issue LC. | Yes | Approved |  | Bay | 26-May-2026 | 12:21 | 26-May-2026 | 12:28
RQ109367 | EMERGENCY | NPCIL | 400KV/220KV KAIGA-ICT-1 | NPCIL | C | To attend continuous oil leak from ICT-1 R- Phase radiator fins on emergency basis. | 2026-05-26 | 14:30 | 2026-05-26 | 19:00 |  | Yes | Approved |  | Transformer | 26-May-2026 | 12:36 | 26-May-2026 | 13:01
RQ109376 | EMERGENCY | aptransco | 400KV-GUDDIGUDEM-HINDUJA-1 | APTRANSCO | C | for rectification of 417- 89A ISOLATOR which connected to the 417 tie Circuit breaker | 2026-05-26 | 17:10 | 2026-05-26 | 20:00 | No interruption | Yes | Approved | 400KV-GUDDIGUDEM-HINDUJA-2 is 29% sensitive. 400KV-HINDUJA-KALPAKKA-1 & 2 are 37% sensitive each. Load management to be done by AP. | Line Circuits | 26-May-2026 | 17:03 | 26-May-2026 | 17:16
RQ107645 | PNOCC | NLC | BUS COUPLER BAY (403) OF NEYVELI_TS1_EXP - 400KV - BUS 1 AND NEYVELI_TS2_EXP - 400KV - BUS 2 @NEYVELI_TS2_EXP - 400KV | NLC | C | To attend oil leak in CT | 2026-05-05 | 08:00 | 2026-05-05 | 18:00 | Oil leak observed in R and Y phase CTs | Yes | Approved | Remaining bays shall be in service. | Bay | 25-Apr-2026 | 17:50 | 02-May-2026 | 17:55
RQ107717 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-02 | 08:00 | 2026-05-02 | 18:00 | For Live line PID scanning of Insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 20:24 | 29-Apr-2026 | 11:16
RQ107727 | PNOCC | PGCIL SR-1 | A/R of 400KV-KURNOOL_PG-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-02 | 08:00 | 2026-05-02 | 18:00 | For Live line PID scanning of Insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 27-Apr-2026 | 20:27 | 29-Apr-2026 | 11:16
RQ107737 | PNOCC | NTPC | 400KV-KALVENDAPATTU-VALLUR-1 | POWERGRID | D | Tracking observed in gantry insulators and wave trap support insulator | 2026-05-05 | 09:00 | 2026-05-05 | 18:00 | line will be under shutdown | Yes | Rejected | Multiple Shutdowns at the same station applied by TN in 237 OCC. | Bay | 28-Apr-2026 | 09:53 | 02-May-2026 | 17:55
RQ107783 | PNOCC | PGCIL SR-1 | MAIN BAY (409) OF NP_KUNTA - 400KV - BUS 2 AND FUTURE @NP_KUNTA - 400KV | PGCIL SR-1 | D | AMP Works | 2026-05-02 | 06:30 | 2026-05-02 | 16:30 | AMP WORKS | Yes | Approved | Remaining bays shall be in service. | Bay | 28-Apr-2026 | 17:02 | 29-Apr-2026 | 11:16
RQ107800 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-02 | 06:00 | 2026-05-02 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 28-Apr-2026 | 19:02 | 29-Apr-2026 | 11:16
RQ107810 | PNOCC | PGCIL SR-1 | A/R of 400KV-GOOTY-KURNOOL_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-02 | 08:00 | 2026-05-02 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 28-Apr-2026 | 19:08 | 29-Apr-2026 | 11:16
RQ107830 | PNOCC | KSPDCL | PAVAGADA_PG - 220KV - BUS 4 | PGCIL SR-2 | C | Bay equipment erection, alignment of isolators, IPS tube erection, earthing and jumper work at Bay No.230 | 2026-05-05 | 18:00 | 2026-05-06 | 02:00 |  | Yes | Approved | Subject to real time grid conditions. | Bus | 28-Apr-2026 | 20:31 | 02-May-2026 | 17:55
RQ107932 | EMERGENCY | TANTRANSCO | 400KV-SHOLINGANALLUR-KALVENDAPATTU-2 | TANTRANSCO | D | flashed over disc insulator replacement work @ loc no 77 "R" phase | 2026-05-01 | 06:00 | 2026-05-01 | 08:33 |  | Yes | Approved | Line-1 shall be in service. Load management to be done by TNEB | Line Circuits | 30-Apr-2026 | 13:36 | 01-May-2026 | 05:55
RQ107967 | PNOCC | PGCIL SR-2 | MAIN BAY (406) OF 400KV/230KV ARASUR_PG-ICT-4 AND ARASUR_PG - 400KV - BUS 2 @ARASUR_PG - 400KV | PGCIL SR-2 | C | Bay AMP works | 2026-05-05 | 09:00 | 2026-05-05 | 17:30 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 01-May-2026 | 10:06 | 02-May-2026 | 17:55
RQ107968 | EMERGENCY | aptransco | 220KV-CHILLAKALLU-PULICHINTALA-1 | APTRANSCO,TGTRANSCO | C | needs to conduct a timer test on the AREVA make Circuit Breaker. This is necessitated due to a delayed operation observed on 30/04/2026, following which the feeder tripped on busbar protection. | 2026-05-01 | 11:30 | 2026-05-01 | 13:30 |  | Yes | Approved |  | Line Circuits | 01-May-2026 | 11:23 | 01-May-2026 | 11:27
RQ107969 | EMERGENCY | kseb | A/R of 220KV-ELAPULLY-MADAKATHARA-1 | KSEB | D | EMERGENCY; FOR THE Emergency shutdown Permit on 220kV Madakkathara -Palakkad (2MDPK) feeder conductor repairing works (on B phase conductor) on DC Tower Loc #118 at a kole paddy field near Tharoor in Palakkad Dist. | 2026-05-02 | 08:00 | 2026-05-02 | 17:00 | A/R WORK ONLY | Yes | Approved |  | Auto Reclosure | 01-May-2026 | 12:27 | 02-May-2026 | 08:28
RQ108166 | PNOCC | PGCIL SR-1 | TIE BAY (414) OF 400KV-KURNOOL_PG-NARNOOR-1 AND NARNOOR - 400KV B/R 2 @NARNOOR - 400KV | APTRANSCO | C | CB overhauling work, S/D may be approved upto 10.05.2026 | 2026-05-05 | 09:00 | 2026-05-06 | 23:59 | CB overhauling work, S/D may be approved upto 10.05.2026 | Yes | Rejected | Multiple shutdowns at the same station. | Bay | 01-May-2026 | 18:36 | 02-May-2026 | 17:55
RQ108167 | EMERGENCY | PGCIL SR-2 | 400KV-GOOTY-NELAMANGALA-1 | POWERGRID | C | For attending hotspot in 41989B- R-Ph & 42089A -B-ph Isolators | 2026-05-02 | 09:00 | 2026-05-02 | 14:00 |  | Yes | Approved | 400kV-Gooty-SOMANAHALLI and 400kV-Gooty-Pavagada D/C shall be in service. | Line Circuits | 01-May-2026 | 19:27 | 02-May-2026 | 08:36
RQ108194 | EMERGENCY | aptransco | MAIN BAY (424) OF 400KV/27KV VTPS_V-GT-1 AND VTPS_V - 400KV - BUS 2 @VTPS_V - 400KV | ANDHRA PRADESH,APTRANSCO | C | Oppertunity LC required for Hotspot rectification works on Y& B phases of GT isolator | 2026-05-02 | 07:40 | 2026-05-02 | 18:00 |  | Yes | Approved |  | Bay | 02-May-2026 | 07:32 | 02-May-2026 | 07:37
RQ108210 | EMERGENCY | kptcl | 400KV-HOODY-DEVANAHALLI-2 | KPTCL | C | to attend the red hot spot observed on Yph bus-1 isolator. | 2026-05-02 | 11:00 | 2026-05-02 | 16:00 | to attend the red hot spot observed on Yph bus-1 isolator. | Yes | Approved | Approved on emergency.Load management to be done by KPTCL | Line Circuits | 02-May-2026 | 10:35 | 02-May-2026 | 16:14
RQ108214 | EMERGENCY | kptcl | HOODY - 400KV - BUS 1 | KPTCL | C | to attend the red hot spot observed on Yph bus-1 isolator | 2026-05-02 | 11:03 | 2026-05-02 | 16:03 | to attend the red hot spot observed on Yph bus-1 isolator | Yes | Approved | Approved on emergency.Load management to be done by KPTCL. | Bus | 02-May-2026 | 11:06 | 02-May-2026 | 16:14
RQ109368 | PNOCC | TGTRANSCO | 400KV/220KV MEHBOOBNAGAR-ICT-1 | TGTRANSCO | C | Not availed in 237th OCC approved LC due to other works of MRT and TRE wings.For carrying out the periodical testings and maintenance works by MRT TRE O&M wings. [From:30/05/2026 09:00 To 30/05/2026 17:00] | 2026-05-30 | 09:00 | 2026-05-30 | 17:00 | Please approve LC | Yes | Approved | Load Management need to be done by TG. N-1 limit for MEHBOOBNAGAR ICTs is 226 MW for 315 MVA ICT each and 358 MW for 500 MVA ICT each. 400KV/220KV MEHBOOBNAGAR-ICT-4 35% 400KV/220KV MEHBOOBNAGAR-ICT-2,3 22% each All DINDI and N'SAGAR ICTs 400KV-YEDULA-MEHBOOBNAGAR D/C 400KV-MAHESHWARAM_TG-MAHESHWARAM_PG D/C 400KV-YEDULA-DINDI-2 shall be in service. | Transformer | 26-May-2026 | 15:24 | 27-May-2026 | 11:48
RQ109369 | PNOCC | TANTRANSCO | NCPS - 765KV - BUS 1 | TANTRANSCO | D | the Bay 406 is already under break down condition. to conduct open inspection in bay 406 s | 2026-05-30 | 09:00 | 2026-05-30 | 17:00 |  | Yes | Rejected | Details of work and plan need to be submitted. Proper reason need to be submitted for applying the shutdown of 409 bay, 403 bay and 765kV Bus-1 at NCPS for inspection at Bay no 406. | Bus | 26-May-2026 | 16:22 | 27-May-2026 | 12:22
RQ109370 | PNOCC | TANTRANSCO | MAIN BAY (403) OF NCPS - 400KV - BUS 1 AND FUTURE @NCPS - 400KV | TANTRANSCO | D | the Bay 406 is already under break down condition. to conduct open inspection in bay 406 | 2026-05-30 | 09:00 | 2026-05-30 | 17:00 |  | Yes | Approved | Concurred, for inspection of the break down. No network in the downstream. | Bay | 26-May-2026 | 16:31 | 27-May-2026 | 12:22
RQ109371 | PNOCC | TANTRANSCO | MAIN BAY (406) OF 400KV-NCPS-PULIYANTHOPE-2 AND PULIYANTHOPE - 400KV - BUS 2 @PULIYANTHOPE - 400KV | TANTRANSCO | D | the Bay 406 is already under break down condition. to conduct open inspection in bay 406 | 2026-05-30 | 09:00 | 2026-05-30 | 17:00 |  | Yes | Rejected | Applied element is not correct. | Bay | 26-May-2026 | 16:35 | 27-May-2026 | 12:10
RQ109372 | PNOCC | TANTRANSCO | MAIN BAY (406) OF NCPS - 400KV - BUS 1 AND FUTURE @NCPS - 400KV | TANTRANSCO | D | the Bay 406 is already under break down condition. to conduct open inspection in bay 406 | 2026-05-30 | 09:00 | 2026-05-30 | 17:00 |  | Yes | Approved | Concurred, for inspection of the break down. No network in the downstream. | Bay | 26-May-2026 | 16:38 | 27-May-2026 | 12:22
RQ109373 | PNOCC | TANTRANSCO | MAIN BAY (409) OF 765KV/400KV NCPS-ICT-1 AND NCPS - 400KV - BUS 1 @NCPS - 400KV | TANTRANSCO | D | the Bay 406 is already under break down condition. to conduct open inspection in bay 406 | 2026-05-30 | 09:00 | 2026-05-30 | 17:00 |  | Yes | Approved | Concurred, for inspection of the break down. No network in the downstream. | Bay | 26-May-2026 | 16:40 | 27-May-2026 | 12:22
RQ109416 | EMERGENCY | kptcl | MAIN BAY (407) OF 400KV-NELAMANGALA-HASSAN-1 AND NELAMANGALA - 400KV - BUS 1 @NELAMANGALA - 400KV | KPTCL | C | Testing by RT staff | 2026-05-27 | 12:30 | 2026-05-27 | 16:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 27-May-2026 | 12:21 | 27-May-2026 | 12:25
RQ109499 | EMERGENCY | PGCIL SR-2 | 400KV-NAGAPATTNAM_PS-TRICHY-2 | POWERGRID | C | To attend SF6 gas leakage at the1st stage in the GD-25Y phase of the outdoor duct. Shutdown till 18:00 hours on 30.05.2026. | 2026-05-28 | 08:00 | 2026-05-28 | 23:59 | To attend SF6 gas leakage at the1st stage in the GD-25Y phase of the outdoor duct. Shutdown till 18:00 hours on 30.05.2026 | Yes | Approved |  | Line Circuits | 27-May-2026 | 21:01 | 28-May-2026 | 08:40
RQ109564 | EMERGENCY | TGTRANSCO | 400KV-SRISAILAM_LEFT_BANK-SATTENPALLY-2 | APTRANSCO,TGTRANSCO | C | SLBHES- 400KV SSLM-STPL-2 feeder – for Reconditioning of SF6 gas and changing of molecular absorbents in Bus-B isolator section – Line clearance – Requested -Reg. | 2026-05-29 | 11:10 | 2026-05-29 | 17:30 | Please approve L.C. | Yes | Approved | 400KV-SRISAILAM_LEFT_BANK-SATTENPALLY-1 28% 400KV-SATTENPALLY-VTPS_IV-1 15% 400KV-CHILAKALURIPETA-SATTENPALLY D/C 14% each shall be in service along with All C'PETA ICTs. Concurrence from TG received regarding no generation and pump operation at SRISAILAM_LEFT_BANK through mail communication dated 16.05.2026. Approved along with Bus 2. Reason submitted by TG for simultaneously availing the bus and line shutdown: "It is to submit that in order to carry out the Reconditioning of SF6 gas and Replacement of Adsorbents in BUS-B Isolator Section of corresponding Feeder, there must be LC on BUS-B and Corresponding Feeder also. Otherwise the Reconditioning of SF6 gas and Replacement of Adsorbents cannot be carried out on BUS-B Isolator Section of Corresponding Feeder." | Line Circuits | 29-May-2026 | 11:08 | 29-May-2026 | 11:49
RQ109648 | EMERGENCY | TGTRANSCO | 400KV-SRISAILAM_LEFT_BANK-DINDI-2 | TGTRANSCO | C | SLBHES- 400KV SSLM-DINDI-2 feeder – for Reconditioning of SF6 gas and changing of molecular absorbents in Bus-B isolator section – Line clearance – Requested | 2026-05-30 | 09:00 | 2026-05-30 | 17:30 | Please approve LC | Yes | Approved | Subject to revival of 400kV SRISAILAM-SATTENPALLI-2 and no other shutdown at 400kV SRISAILAM LEFT BANK except 400kV BUS-2. | Line Circuits | 29-May-2026 | 18:05 | 29-May-2026 | 19:34
RQ109715 | EMERGENCY | PGCIL SR-2 | A/R of 400KV-KALVENDAPATTU-VALLUR-2 | POWERGRID | C | For carrying out Opportunity shutdown works in Ckt-1 and further inspection of polluted insulators in 400kV Kalivanthapattu - Vallur Line-2 | 2026-05-30 | 12:00 | 2026-05-30 | 18:00 |  | Yes | Approved | Approved | Auto Reclosure | 30-May-2026 | 11:29 | 30-May-2026 | 11:34
RQ109756 | EMERGENCY | TGTRANSCO | TIE BAY (414) OF 400KV-KTPS_VI-KHAMMAM_PG-1 AND KHAMMAM_PG - 400KV - BUS 2 @KHAMMAM_PG - 400KV | PGCIL SR-1 | C | For SF6 gas refiling work on emergency basis as low SF6 alarm is continuously persisting. | 2026-05-30 | 16:00 | 2026-05-30 | 19:00 | Please approve L.C. | Yes | Approved |  | Bay | 30-May-2026 | 15:49 | 30-May-2026 | 16:11
RQ109758 | EMERGENCY | kptcl | 220KV-MYSORE-TUBINAKERE-1 | KPTCL | C | 220KV Bastipura -Tubinkere line for Relay Main1 and Main 2 of Distance Relays, as the DC fuse blown out repeatedly. | 2026-05-30 | 16:30 | 2026-05-30 | 17:30 |  | Yes | Approved |  | Line Circuits | 30-May-2026 | 16:19 | 30-May-2026 | 16:25
RQ109759 | EMERGENCY | kptcl | 400KV-GUTTUR-BTPS-1 | KPTCL | C | hotspot found on line isolator R Phase limb of 400kV-Guttur-BTPS line arcing continuously at Guttur end | 2026-05-30 | 16:45 | 2026-05-30 | 18:45 |  | Yes | Approved | 400kV BTPS- Hiriyur D/C and BTPS-RTPS shall be in service | Line Circuits | 30-May-2026 | 16:43 | 30-May-2026 | 17:04
RQ109779 | EMERGENCY | kptcl | A/R of 400KV-HASSAN-HEBBANAHALLI-2 | KARNATAKA | C | For replacement of CLR insulator of Y phase at tower no 396B was defective in hebanahally- hassan line-1 | 2026-05-31 | 10:45 | 2026-05-31 | 18:00 |  | Yes | Approved |  | Auto Reclosure | 31-May-2026 | 10:31 | 31-May-2026 | 10:34
RQ107646 | PNOCC | NLC | NEYVELI_TS2_EXP - 400KV - BUS 2 | NLC | C | To attend Hot spot in 401 bay GT-1 Y phase isolator | 2026-05-06 | 08:00 | 2026-05-06 | 20:30 | Unit shutdown anticipated or unit will be taken in transfer bus. | Yes | Approved | Remaining all elements shall be in service. | Bus | 25-Apr-2026 | 18:02 | 03-May-2026 | 12:33
RQ107664 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-3 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-06 | 07:00 | 2026-05-06 | 14:00 |  | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 27-Apr-2026 | 16:10 | 03-May-2026 | 11:39
RQ107666 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-3 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-08 | 07:00 | 2026-05-08 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 16:10 | 05-May-2026 | 10:20
RQ107674 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-4 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-06 | 07:00 | 2026-05-06 | 14:00 |  | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 27-Apr-2026 | 16:10 | 03-May-2026 | 11:39
RQ107676 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-4 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-08 | 07:00 | 2026-05-08 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 16:10 | 05-May-2026 | 10:20
RQ107709 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-04 | 08:00 | 2026-05-04 | 18:00 | For live line PID scanning of Insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 20:20 | 01-May-2026 | 14:00
RQ107711 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-06 | 08:00 | 2026-05-06 | 18:00 | For live line PID scanning of Insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 27-Apr-2026 | 20:20 | 03-May-2026 | 12:29
RQ107714 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-09 | 08:00 | 2026-05-09 | 18:00 | For live line PID scanning of Insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 27-Apr-2026 | 20:20 | 06-May-2026 | 11:30
RQ107721 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-06 | 08:00 | 2026-05-06 | 18:00 | For Live line PID scanning of Insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 20:24 | 03-May-2026 | 12:29
RQ107724 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-09 | 08:00 | 2026-05-09 | 18:00 | For Live line PID scanning of Insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 20:24 | 06-May-2026 | 11:30
RQ107731 | PNOCC | PGCIL SR-1 | A/R of 400KV-KURNOOL_PG-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-06 | 08:00 | 2026-05-06 | 18:00 | For Live line PID scanning of Insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 27-Apr-2026 | 20:27 | 03-May-2026 | 12:29
RQ107734 | PNOCC | PGCIL SR-1 | A/R of 400KV-KURNOOL_PG-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-09 | 08:00 | 2026-05-09 | 18:00 | For Live line PID scanning of Insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 27-Apr-2026 | 20:27 | 06-May-2026 | 11:30
RQ107736 | PNOCC | NTPC | 400KV-VALLUR-ALAMATHY-2 | TANTRANSCO | D | Tracking observed in insulators. Insulators to be cleaned | 2026-05-04 | 09:00 | 2026-05-04 | 18:00 | line will be under shutdown | Yes | Rejected | TN concurrence needs to be submitted regarding load and voltage management. 400KV-VALLUR-ALAMATHY-1 36% 400KV-NCTPS_STAGE_II-ALAMATHY-1 33% 400KV-NCTPS_STAGE_II-VALLUR D/C 28% each 400KV-MANALI-NCTPS_STAGE_II-1 8% shall be in service. Subject to real time grid voltage conditions. | Bay | 28-Apr-2026 | 09:32 | 01-May-2026 | 15:27
RQ107739 | PNOCC | NTPC | 400KV-KALVENDAPATTU-VALLUR-2 | POWERGRID | D | Tracking observed. Insulator cleaning to be taken up. | 2026-05-06 | 09:00 | 2026-05-06 | 18:00 | line will be under shutdown | Yes | Approved | 400KV-KALVENDAPATTU-VALLUR-1 28% 400kV-NCTPS-VALLUR D/C 20% each 400kV-ALAMATHY-VALLUR D/C 16% each 400kV-ALAMATHY-NCTPS 13% 400kV-MANALI-NCTPS 11% 400kV-KALVENDAPATTU-THIRUVALLAM D/C 10% and remaining all other lines at 400kV KALIVEDAPATTU and VALLUR each shall be in service. | Line Circuits | 28-Apr-2026 | 10:40 | 04-May-2026 | 09:51
RQ107804 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-06 | 06:00 | 2026-05-06 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 28-Apr-2026 | 19:02 | 03-May-2026 | 12:29
RQ107807 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-09 | 06:00 | 2026-05-09 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 28-Apr-2026 | 19:02 | 06-May-2026 | 11:30
RQ107814 | PNOCC | PGCIL SR-1 | A/R of 400KV-GOOTY-KURNOOL_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-06 | 08:00 | 2026-05-06 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 28-Apr-2026 | 19:08 | 03-May-2026 | 12:29
RQ107817 | PNOCC | PGCIL SR-1 | A/R of 400KV-GOOTY-KURNOOL_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-09 | 08:00 | 2026-05-09 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 28-Apr-2026 | 19:08 | 06-May-2026 | 11:30
RQ107829 | PNOCC | KSPDCL | PAVAGADA_PG - 220KV - BUS 3 | PGCIL SR-2 | C | Bay equipment erection, alignment of isolators, IPS tube erection, earthing and jumper work at Bay No.230 | 2026-05-04 | 18:00 | 2026-05-05 | 02:00 |  | Yes | Rejected | Planned Activities to be taken into Main OCC. | Bus | 28-Apr-2026 | 20:27 | 01-May-2026 | 15:23
RQ107833 | PNOCC | KSPDCL | PAVAGADA_PG - 220KV - BUS 3 | PGCIL SR-2 | C | BUS Stability test | 2026-05-09 | 18:00 | 2026-05-10 | 02:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Bus | 28-Apr-2026 | 20:39 | 06-May-2026 | 11:30
RQ107834 | PNOCC | KSPDCL | PAVAGADA_PG - 220KV - BUS 4 | PGCIL SR-2 | C | BUS Stability test | 2026-05-10 | 18:00 | 2026-05-11 | 02:00 |  | Yes | Rejected | Multiple shutdowns at the same station. | Bus | 28-Apr-2026 | 20:42 | 07-May-2026 | 13:05
RQ107835 | PNOCC | KSPDCL | PAVAGADA_PG - 220KV - BUS 3 | PGCIL SR-2 | C | Jumper connection | 2026-05-10 | 18:00 | 2026-05-11 | 02:00 |  | Yes | Rejected | Multiple shutdowns at the same station. | Bus | 28-Apr-2026 | 20:45 | 07-May-2026 | 13:05
RQ107846 | PNOCC | kptcl | 220KV-KUDGI_NTPC-SAVALAGI-1 | KPTCL | C | Stringing of conductor between location 1 and 2 covering a distance of 18.5 km in bilagi taluk. | 2026-05-05 | 08:00 | 2026-05-06 | 23:59 | Line clear of 220kV Kudagi Savalagi line 01 and 02 (approved in mid review of OCC 237) are not able to avail from 01.05.2026 to 03.05.2026 due to ROW issue and the same is requested from 05.05.2026 to 07.05.2026. Establishing 2X100MVA, 220/110/11KV Sub-station at Bilagi in Bilagi Taluk, Bagalkot District, with associated 220 kV Kudagi-Vajramatti line (18.455 Kms), - onTotal turnkey basis. As Krishna river crossing work of first circuit to be completed by 25.05.2026 | Yes | Rejected | RoW diagrams furnished by KPTCL. All the necessary approvals / minutes are yet to be submitted. Detailed Load and generation Management details need to be submitted by KPTCL for the D/C shutdown. The shutdown of the 220 kV Kudgi–SAVALAGI D/C line has a sensitivity of approximately 15% on the 400/220 kV Narendra ICTs(2*500MVA), which have an N-1 limit of 306 MW for each ICT. Currently, the Narendra ICTs are loaded up to 420 MW and 450 MVA. Under these conditions, any tripping or reduction in generation at Nagjheri (6 × 150 MW) is likely to further aggravate the loading on the ICTs and may lead to cascading tripping. In addition, the following 220 kV lines are expected to be highly loaded and may exceed their N-1 limits: 220 kV Alamathi–Bagalkot D/C 220 kV Narendra–Ghataprabha D/C 220 kV Kanabargi–Narendra (KA) D/C 220 kV Belagavi–Kanabargi D/C Further, voltages at nearby 220 kV substations are observed to reduce by approximately 4–6 kV. In view of the above, Karnataka is requested to provide remedial measures for load and voltage management, along with an N-1 contingency action plan. The same may be supported with relevant PSS®E study files for further analysis and processing. | Line Circuits | 29-Apr-2026 | 13:18 | 03-May-2026 | 10:33
RQ107848 | PNOCC | kptcl | 220KV-KUDGI_NTPC-SAVALAGI-2 | KPTCL | C | Stringing of conductor between location 1 and 2 covering a distance of 18.5 km in bilagi taluk. | 2026-05-05 | 08:00 | 2026-05-06 | 23:59 | Line clear of 220kV Kudagi Savalagi line 01 and 02 (approved in mid review of OCC 237) are not able to avail from 01.05.2026 to 03.05.2026 due to ROW issue and the same is requested from 05.05.2026 to 07.05.2026. Establishing 2X100MVA, 220/110/11KV Sub-station at Bilagi in Bilagi Taluk, Bagalkot District, with associated 220 kV Kudagi-Vajramatti line (18.455 Kms), - onTotal turnkey basis. As Krishna river crossing work of first circuit to be completed by 25.05.2026 | Yes | Rejected | RoW diagrams furnished by KPTCL. All the necessary approvals / minutes are yet to be submitted. Detailed Load and generation Management details need to be submitted by KPTCL for the D/C shutdown. The shutdown of the 220 kV Kudgi–SAVALAGI D/C line has a sensitivity of approximately 15% on the 400/220 kV Narendra ICTs(2*500MVA), which have an N-1 limit of 306 MW for each ICT. Currently, the Narendra ICTs are loaded up to 420 MW and 450 MVA. Under these conditions, any tripping or reduction in generation at Nagjheri (6 × 150 MW) is likely to further aggravate the loading on the ICTs and may lead to cascading tripping. In addition, the following 220 kV lines are expected to be highly loaded and may exceed their N-1 limits: 220 kV Alamathi–Bagalkot D/C 220 kV Narendra–Ghataprabha D/C 220 kV Kanabargi–Narendra (KA) D/C 220 kV Belagavi–Kanabargi D/C Further, voltages at nearby 220 kV substations are observed to reduce by approximately 4–6 kV. In view of the above, Karnataka is requested to provide remedial measures for load and voltage management, along with an N-1 contingency action plan. The same may be supported with relevant PSS®E study files for further analysis and processing. | Line Circuits | 29-Apr-2026 | 13:26 | 03-May-2026 | 10:33
RQ107863 | PNOCC | KSPDCL | PAVAGADA_PG - 220KV - BUS 4 | PGCIL SR-2 | C | Bay equipment erection, alignment of isolators, IPS tube erection, earthing and jumper work at Bay No.230 | 2026-05-04 | 18:00 | 2026-05-05 | 02:00 |  | Yes | Rejected | Planned Activities to be taken into Main OCC. | Bus | 29-Apr-2026 | 16:03 | 01-May-2026 | 15:23
RQ107905 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-06 | 06:00 | 2026-05-06 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 30-Apr-2026 | 07:06 | 03-May-2026 | 11:39
RQ107910 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-11 | 06:00 | 2026-05-11 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 30-Apr-2026 | 07:06 | 08-May-2026 | 15:01
RQ107915 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-06 | 06:00 | 2026-05-06 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 30-Apr-2026 | 07:06 | 03-May-2026 | 11:39
RQ107920 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-11 | 06:00 | 2026-05-11 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 30-Apr-2026 | 07:06 | 08-May-2026 | 15:01
RQ107953 | PNOCC | kptcl | MAIN BAY (415) OF 400KV-NELAMANGALA-DEVANAHALLI-1 AND NELAMANGALA - 400KV - BUS 2 @NELAMANGALA - 400KV | KPTCL | C | Breaker testing and maintenance works. | 2026-05-04 | 11:00 | 2026-05-04 | 17:00 | As they are requesting to avail Devanahalli main breaker bay 415 instead of Hassan main breaker 407 on 04.05.2026 | Yes | Approved | Remaining bays shall be in service. | Bay | 30-Apr-2026 | 16:49 | 01-May-2026 | 14:00
RQ107955 | PNOCC | JSW_Renew_Two | 230KV-TTGS-JSW_VILATHIKULAM-1 | JINDAL | C | Minor hotspot observed to incoming 230kV-89L isolator. Rectification & alignment work | 2026-05-04 | 10:00 | 2026-05-04 | 18:00 |  | Yes | Approved | Subject to real time RE generation and grid conditions and proper revision and adherence of the schedules. | Line Circuits | 30-Apr-2026 | 17:00 | 01-May-2026 | 14:00
RQ107957 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-3 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-11 | 07:00 | 2026-05-11 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 30-Apr-2026 | 17:29 | 08-May-2026 | 15:01
RQ107960 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-4 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-11 | 07:00 | 2026-05-11 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 30-Apr-2026 | 17:29 | 08-May-2026 | 15:01
RQ108135 | PNOCC | TGTRANSCO | 400KV-YADADRI TPP-DINDI-1 | TGTRANSCO | C | For replacement of OPGW between Loc No 19/5 to 20/0 | 2026-05-06 | 08:00 | 2026-05-06 | 18:00 | Please Issue LC | Yes | Approved | 400KV-YADADRI TPP-DINDI-2 57% 400KV-CHOUTUPPAL-YADADRI TPP D/C 17% each 400KV-MAHESHWARAM_TG-DINDI D/C 11% each shall be in service. | Line Circuits | 01-May-2026 | 16:10 | 03-May-2026 | 12:42
RQ108203 | EMERGENCY | aptransco | 400KV-KALPAKKA-VEMAGIRI_AP-1 | APTRANSCO | C | For restringing of Earth wire between Loc No: 5-7 | 2026-05-02 | 10:00 | 2026-05-02 | 15:00 |  | Yes | Approved | OTHER LINES AT VEMAGIRI SHALL BE IN SERVICE. | Line Circuits | 02-May-2026 | 10:00 | 02-May-2026 | 11:29
RQ108209 | EMERGENCY | aptransco | A/R of 400KV-HINDUJA-KV_KOTA-2 | APTRANSCO | C | for testing of Telecom Digital Protection System | 2026-05-02 | 11:00 | 2026-05-02 | 17:00 |  | Yes | Approved |  | Auto Reclosure | 02-May-2026 | 10:28 | 02-May-2026 | 15:39
RQ108218 | PNOCC | PGCIL SR-2 | MAIN BAY (407) OF 400KV-GUTTUR-HIRIYUR-2 AND HIRIYUR - 400KV - BUS 1 @HIRIYUR - 400KV | PGCIL SR-2 | C | for AMP works. | 2026-05-06 | 09:30 | 2026-05-06 | 13:00 | nil | Yes | Approved | Remaining bays shall be in service. | Bay | 02-May-2026 | 11:39 | 03-May-2026 | 12:33
RQ108264 | PNOCC | kptcl | MAIN BAY (416) OF NELAMANGALA - 400KV - BUS 1 AND 400KV-YELHANKA-NELAMANGALA-1 @NELAMANGALA - 400KV | KPTCL | C | As 408 bay work (Hassan ICT2 tie breaker bay) was completed on 08.04.2026 due to emergency which was proposed on 6.5.2026 , hence instead of that they are requesting for shutdown of 400 kv yelahanka main breaker bay 416 on 06.05.2026. | 2026-05-06 | 11:00 | 2026-05-06 | 18:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 02-May-2026 | 16:56 | 03-May-2026 | 12:33
RQ108266 | PNOCC | PGCIL SR-1 | MAIN BAY (406) OF GHANAPUR - 400KV - BUS 2 AND 400KV-GHANAPUR-RAMAGUNDAM-4 @GHANAPUR - 400KV | PGCIL SR-1 | D | 406 Bay AMP works | 2026-05-06 | 08:00 | 2026-05-06 | 18:00 | 406 Bay AMP works | Yes | Approved | Remaining bays shall be in service. | Bay | 02-May-2026 | 17:03 | 03-May-2026 | 12:29
RQ108268 | PNOCC | PGCIL SR-1 | TIE BAY (411) OF 400KV-NAGARJUNASAGAR_PG-RAMAGUNDAM-1 AND 400KV-KHAMMAM_PG-NAGARJUNASAGAR_PG-1 @NAGARJUNASAGAR_PG - 400KV | PGCIL SR-1 | D | 411 Bay AMP works | 2026-05-06 | 07:00 | 2026-05-06 | 18:00 | 411 Bay AMP works | Yes | Approved | Remaining bays shall be in service. | Bay | 02-May-2026 | 17:07 | 03-May-2026 | 12:29
RQ108334 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-NELLORE_AP-3 | POWERGRID | D | Live Line Replacement of OPGW and creation of Joint Box at T0121 | 2026-05-06 | 07:00 | 2026-05-06 | 18:00 | Live Line Replacement of OPGW and creation of Joint Box at T0121 | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 02-May-2026 | 20:04 | 03-May-2026 | 12:29
RQ108335 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-NELLORE_AP-3 | POWERGRID | D | Live Line Replacement of OPGW and creation of Joint Box at T0121 | 2026-05-07 | 07:00 | 2026-05-07 | 18:00 | Live Line Replacement of OPGW and creation of Joint Box at T0121 | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 02-May-2026 | 20:04 | 04-May-2026 | 12:43
RQ108337 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-NELLORE_AP-3 | POWERGRID | D | Live Line Replacement of OPGW and creation of Joint Box at T0121 | 2026-05-09 | 07:00 | 2026-05-09 | 18:00 | Live Line Replacement of OPGW and creation of Joint Box at T0121 | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 02-May-2026 | 20:04 | 06-May-2026 | 11:30
RQ108381 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-1 | KPTCL | D | For OPGW stringing work | 2026-05-11 | 06:00 | 2026-05-11 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 03-May-2026 | 10:34 | 08-May-2026 | 15:01
RQ108391 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-2 | KPTCL | D | For OPGW stringing work | 2026-05-11 | 06:00 | 2026-05-11 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 03-May-2026 | 10:34 | 08-May-2026 | 15:01
RQ108416 | EMERGENCY | kptcl | 220KV-HASSAN-HASSAN-KA-1 | KPTCL | C | To attend the fault in Dudda - Hassan line | 2026-05-03 | 13:30 | 2026-05-03 | 15:30 |  | Yes | Approved | KPTCL to ensure no overloads post shutdown | Line Circuits | 03-May-2026 | 13:09 | 03-May-2026 | 13:15
RQ108594 | PNOCC | kptcl | 220KV-KUDGI_NTPC-SAVALAGI-1 | KPTCL | C | Stringing of conductor between location 1 and 2 covering a distance of 18.5 km in bilagi taluk. | 2026-05-08 | 06:00 | 2026-05-08 | 12:00 | In case of exigency, ICT loading at Narendra will be managed by regulating the generation at Kaali complex and load management will be done by KPTCL. | Yes | Approved | RoW diagrams furnished by KPTCL. All the necessary approvals / minutes submitted. The shutdown of the 220 kV Kudgi–SAVALAGI D/C line has a sensitivity of approximately 15% on the 400/220 kV Narendra ICTs(2*500MVA), which have an N-1 limit of 306 MW for each ICT. Currently, the Narendra ICTs are loaded up to 420 MW and 450 MVA. Under these conditions, any tripping or reduction in generation at Nagjheri (6 × 150 MW) is likely to further aggravate the loading on the ICTs and may lead to cascading tripping. In addition, the following 220 kV lines are expected to be highly loaded and may exceed their N-1 limits: 220 kV Alamathi–Bagalkot D/C 220 kV Narendra–Ghataprabha D/C 220 kV Kanabargi–Narendra (KA) D/C 220 kV Belagavi–Kanabargi D/C Further, voltages at nearby 220 kV substations are observed to reduce by approximately 4–6 kV. Load Management details furnished by KPTCL are as follows: "The S/D of the above lines is only 4-6 hours. The generation at NPH will be kept to full to an extent of 650-700 MW and also all other lines will be kept in charged condition to facilitate the above S/D to contain Narendra ICTs. The irrigation loads will be staggered to an extent of 100 MW if required at the downstream of Narendra. In case of Exigency, ICT loading at Narendra will be managed by regulating the generation at Kaali Complex and load management will be done by KPTCL." | Line Circuits | 04-May-2026 | 17:19 | 05-May-2026 | 10:37
RQ108595 | PNOCC | kptcl | 220KV-KUDGI_NTPC-SAVALAGI-2 | KPTCL | C | Stringing of conductor between location 1 and 2 covering a distance of 18.5 km in bilagi taluk. | 2026-05-08 | 06:00 | 2026-05-08 | 12:00 | In case of exigency, ICT loading at Narendra will be managed by regulating the generation at Kaali complex and load management will be done by KPTCL. | Yes | Approved | RoW diagrams furnished by KPTCL. All the necessary approvals / minutes submitted. The shutdown of the 220 kV Kudgi–SAVALAGI D/C line has a sensitivity of approximately 15% on the 400/220 kV Narendra ICTs(2*500MVA), which have an N-1 limit of 306 MW for each ICT. Currently, the Narendra ICTs are loaded up to 420 MW and 450 MVA. Under these conditions, any tripping or reduction in generation at Nagjheri (6 × 150 MW) is likely to further aggravate the loading on the ICTs and may lead to cascading tripping. In addition, the following 220 kV lines are expected to be highly loaded and may exceed their N-1 limits: 220 kV Alamathi–Bagalkot D/C 220 kV Narendra–Ghataprabha D/C 220 kV Kanabargi–Narendra (KA) D/C 220 kV Belagavi–Kanabargi D/C Further, voltages at nearby 220 kV substations are observed to reduce by approximately 4–6 kV. Load Management details furnished by KPTCL are as follows: "The S/D of the above lines is only 4-6 hours. The generation at NPH will be kept to full to an extent of 650-700 MW and also all other lines will be kept in charged condition to facilitate the above S/D to contain Narendra ICTs. The irrigation loads will be staggered to an extent of 100 MW if required at the downstream of Narendra. In case of Exigency, ICT loading at Narendra will be managed by regulating the generation at Kaali Complex and load management will be done by KPTCL." | Line Circuits | 04-May-2026 | 17:19 | 05-May-2026 | 10:37
RQ108597 | PNOCC | PGCIL SR-1 | 765KV/400KV SRIKAKULAM-ICT-2 | PGCIL SR-1 | D | OCC-237 approved the SD on 05.05.2026 but NLDC is unable to facilitate the shutdown on the date. Hence it is requested to approve SD on 08.05.2026 to complete the planned maintenance works.. | 2026-05-08 | 09:00 | 2026-05-08 | 18:00 | OCC-237 approved the SD on 05.05.2026 but NLDC is unable to facilitate the shutdown on the date. Hence it is requested to approve SD on 08.05.2026 to complete the planned maintenance works. | Yes | Approved | Subject to NLDC approval and real time grid conditions and ICT loadings within its N-1 limit. N-1 limit for 765kV/400kV SRIKAKULAM ICTs is 797 MW each. NEW-SR tentative ATC/TTC curtailment of 50 MW in SR import. 765KV/400KV SRIKAKULAM-ICT-1 78% 765KV/400KV VEMAGIRI_PG-ICT-1,2 6% each 400KV-MARADAM-KALPAKKA D/C 8% each 765KV-VEMAGIRI_PG-SRIKAKULAM D/C 7% each 400KV-VEMAGIRI_PG-VEMAGIRI_AP D/C 2% each 400KV-SIMHADRI-KALPAKKA-2,3,4 2% each shall be in service. | Transformer | 04-May-2026 | 20:08 | 05-May-2026 | 10:34
RQ108601 | PNOCC | PGCIL SR-2 | MAIN BAY (404) OF 400KV/220KV MYSORE-ICT-3 AND MYSORE - 400KV - BUS 2 @MYSORE - 400KV | PGCIL SR-2 | D | FOR BAY AMP WORKS | 2026-05-14 | 09:00 | 2026-05-14 | 17:00 | PLEASE APPROVE | Yes | Approved | Remaining bays shall be in service. | Bay | 05-May-2026 | 13:02 | 11-May-2026 | 11:15
RQ108602 | PNOCC | PGCIL SR-2 | TIE BAY (417) OF 400KV-MYSORE-KOZHIKODE-1 AND 400KV-HASSAN-MYSORE-1 @MYSORE - 400KV | PGCIL SR-2 | D | FOR BAY AMP WORKS | 2026-05-09 | 09:00 | 2026-05-09 | 17:00 | PLEASE APPROVE | Yes | Approved | Concurred, subject to real time grid conditions. Remaining bays shall be in service. | Bay | 05-May-2026 | 13:02 | 06-May-2026 | 11:30
RQ108605 | PNOCC | PGCIL SR-1 | MAIN BAY (404) OF GHANAPUR - 400KV - BUS 1 AND 400KV-GHANAPUR-NAGARJUNASAGAR_PG-1 @GHANAPUR - 400KV | PGCIL SR-1 | D | For CT Oil sample collection | 2026-05-09 | 09:00 | 2026-05-09 | 14:00 | For CT Oil sample collection | Yes | Approved | Concurred, subject to real time grid conditions. Remaining bays shall be in service. | Bay | 05-May-2026 | 15:31 | 06-May-2026 | 11:30
RQ108609 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-3 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-17 | 07:00 | 2026-05-17 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 05-May-2026 | 16:55 | 14-May-2026 | 10:43
RQ108614 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-4 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-17 | 07:00 | 2026-05-17 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 05-May-2026 | 16:55 | 14-May-2026 | 10:43
RQ108616 | EMERGENCY | TGTRANSCO | MAIN BAY (409) OF 400KV-NIZAMABAD-CHANDALAPUR-2 AND NIZAMABAD - 400KV - BUS 2 @NIZAMABAD - 400KV | PGCIL SR-1 | C | Please find the attachment showing failed Summation check meter hence Open code required for 409M-52 CB & 412M-52 (both metering bays) for replacing with new meter by TGSPDCL [From:06/05/2026 13:00 To 06/05/2026 16:00] | 2026-05-06 | 13:00 | 2026-05-06 | 16:00 | pl approve | Yes | Approved |  | Bay | 05-May-2026 | 17:04 | 06-May-2026 | 14:45
RQ108618 | EMERGENCY | TGTRANSCO | MAIN BAY (412) OF 400KV-CHANDALAPUR-CHANDALAPUR-CONS-2 AND CHANDALAPUR - 400KV - BUS 2 @CHANDALAPUR - 400KV | TGTRANSCO | C | Please find the attachment showing failed Summation check meter hence Open code required for 411-52 CB & 412-52 (both metering bays) for replacing with new meter by TGSPDCL [From:06/05/2026 13:00 To 06/05/2026 16:00] | 2026-05-06 | 13:00 | 2026-05-06 | 16:15 | pl approve | Yes | Approved |  | Bay | 05-May-2026 | 17:19 | 06-May-2026 | 14:43
RQ108619 | EMERGENCY | TGTRANSCO | TIE BAY (411) OF 400KV-BHOOPALAPALLY-CHANDALAPUR-2 AND 400KV-CHANDALAPUR-CHANDALAPUR-CONS-2 @CHANDALAPUR - 400KV | TGTRANSCO | C | Please find the attachment showing failed Summation check meter hence Open code required for 411-52 CB & 412-52 (both metering bays) for replacing with new meter by TGSPDCL [From:06/05/2026 13:00 To 06/05/2026 16:00] | 2026-05-06 | 13:00 | 2026-05-06 | 16:15 | pl approve | Yes | Approved |  | Bay | 05-May-2026 | 17:19 | 06-May-2026 | 14:43
RQ108623 | EMERGENCY | TANTRANSCO | 230KV-ARASUR_PG-ARASUR-1 | TANTRANSCO | D | To attend Glow rectification work in B Phase 230KV CT Clamp bolt of 230KV Arasur- Arasur PGCIL # 1 at Arasur TN end | 2026-05-06 | 05:30 | 2026-05-06 | 08:00 | Other 5 Nos. 230 KV Feeders will be in service to cater the station load. To limit the load, (1)110KV Arasur - Karamadai feeder2 will be kept radial from Karamadai SS end and (2)110KV Karadibavi SS load will be transferred to the nearby Othakkalmandabam 230KV SS. | Yes | Approved | Load management to be done by TANTRANSCO | Line Circuits | 05-May-2026 | 22:45 | 06-May-2026 | 05:31
RQ108631 | EMERGENCY | TGTRANSCO | 400KV/13.8KV SRISAILAM_LEFT_BANK-ST-1 | TGTRANSCO | C | 25MVA, 400KV/13.8KV STR-1 – for Reconditioning of SF6 gas and absorbents replacement in Bus-A isolator and Bus-A sections– Line clearance – Requested | 2026-05-07 | 07:00 | 2026-05-07 | 17:30 | Please approve L.C. | Yes | Approved | Approved | Transformer | 06-May-2026 | 12:03 | 07-May-2026 | 07:10
RQ108633 | EMERGENCY | PGCIL SR-1 | HVDC 500KV GAZUWAKA POLE 1 | POWERGRID | D | Emergency Shutdown for rectification of "Thyristor Redundancy Lost" alarm of Pole-1 HVDC | 2026-05-06 | 13:30 | 2026-05-06 | 17:30 | Emergency Shutdown for rectification of "Thyristor Redundancy Lost" alarm of Pole-1 HVDC | Yes | Approved |  | HVDC Pole | 06-May-2026 | 13:31 | 06-May-2026 | 16:04
RQ108635 | EMERGENCY | TGTRANSCO | MAIN BAY (409M) OF 400KV-CHANDALAPUR-CHANDALAPUR-CONS-1 AND CHANDALAPUR-CONS - 400KV - BUS 1 @CHANDALAPUR-CONS - 400KV | TGTRANSCO | C | Please find the attachment showing failed Summation check meter hence Open code required for 409M-52 CB & 412M-52 (both metering bays) for replacing with new meter by TGSPDCL [From:06/05/2026 13:00 To 06/05/2026 16:00]Please find the attachment showing failed Summation check meter hence Open code required for 409M-52 CB both metering bays) for replacing with new meter by TGSPDCL [From:06/05/2026 13:00 To 06/05/2026 17:00] | 2026-05-06 | 15:22 | 2026-05-06 | 17:00 | pl approve | Yes | Approved |  | Bay | 06-May-2026 | 15:24 | 06-May-2026 | 15:27
RQ108636 | EMERGENCY | NPCIL | 230KV-KUDANKULAM-KUDANKULAM 3&4-1 | KKNPP | C | Heavy corona discharge observed, isolation is requested on urgent basis. | 2026-05-06 | 17:30 | 2026-05-07 | 23:59 | Due to ongoing construction activities in KK-3&4, heavy dust deposition is observed on the insulators resulting in the corona discharge. | Yes | Approved |  | Line Circuits | 06-May-2026 | 15:50 | 06-May-2026 | 17:54
RQ108637 | EMERGENCY | TGTRANSCO | MAIN BAY (412M) OF 400KV-CHANDALAPUR-CHANDALAPUR-CONS-2 AND CHANDALAPUR-CONS - 400KV - BUS 1 @CHANDALAPUR-CONS - 400KV | TGTRANSCO | C | Please find the attachment showing failed Summation check meter hence Open code required for 412M-52 (both metering bays) for replacing with new meter by TGSPDCL [From:06/05/2026 16:00 To 06/05/2026 19:15] | 2026-05-06 | 16:15 | 2026-05-06 | 19:15 | pl approve | Yes | Approved |  | Bay | 06-May-2026 | 16:18 | 06-May-2026 | 16:19
RQ108638 | EMERGENCY | PGCIL SR-2 | 400KV/230KV ARASUR_PG-ICT-1 | POWERGRID | D | To attend critical hotspots in: IV Y phase bushing : 109°C, IV B phase bushing : 114°C and 41489B - Y phase:101°C | 2026-05-06 | 17:37 | 2026-05-06 | 20:30 |  | Yes | Approved |  | Transformer | 06-May-2026 | 17:44 | 06-May-2026 | 17:49
RQ108645 | EMERGENCY | aptransco | 220KV-KOTHAGUDEM_TPS-TIRUVURU-1 | APTRANSCO | C | Replacement of R-ph flashed over disc at loc no.230 | 2026-05-07 | 10:00 | 2026-05-07 | 16:00 |  | Yes | Approved |  | Line Circuits | 07-May-2026 | 09:01 | 07-May-2026 | 10:24
RQ108646 | EMERGENCY | TGTRANSCO | ASUPAKA - 400KV B/R 1 | TGTRANSCO | C | EMERGENCY LINE CLEAR FOR RECTIFICATION OF HISSING NOISE ON 406 89 A ISOLATOR B PHASE LC is needed ON BUS RECATOR TO AVOID INDUCTION | 2026-05-07 | 09:43 | 2026-05-07 | 13:43 | Pl accord the permission and issue LC opening code. | Yes | Approved |  | Bus Reactor | 07-May-2026 | 09:45 | 07-May-2026 | 09:56
RQ108647 | EMERGENCY | TGTRANSCO | 400KV/220KV ASUPAKA-ICT-2 | TGTRANSCO | C | For EMERGENCY LINE CLEAR FOR RECTIFICATION OF HISSING NOISE ON 406 89 A ISOLATOR B PHASE | 2026-05-07 | 09:47 | 2026-05-07 | 13:47 | It is requested to accord the permission and issue LC opening code. | Yes | Approved |  | Transformer | 07-May-2026 | 09:48 | 07-May-2026 | 09:56
RQ108653 | EMERGENCY | TGTRANSCO | MAIN BAY (412M) OF 400KV-TUKKAPUR-TUKKAPUR-CONS-2 AND TUKKAPUR-CONS - 400KV - BUS 2 @TUKKAPUR-CONS - 400KV | TGTRANSCO | C | In metering bay Main and Check meters display is not functioning, to remove the meters by TGSPDCL officials and hand over to the agency to rectify. | 2026-05-07 | 11:05 | 2026-05-07 | 14:05 | It is requested to accord permission and issue LC opening code. | Yes | Approved |  | Bay | 07-May-2026 | 11:08 | 07-May-2026 | 11:18
RQ108654 | EMERGENCY | TGTRANSCO | MAIN BAY (403M) OF 400KV-TUKKAPUR-TUKKAPUR-CONS-1 AND TUKKAPUR-CONS - 400KV - BUS 1 @TUKKAPUR-CONS - 400KV | TGTRANSCO | C | In metering bay Main and Check meters display is not functioning, to remove the meters by TGSPDCL officials and hand over to the agency to rectify | 2026-05-07 | 14:30 | 2026-05-07 | 17:30 | It is requested to accord permission and issue LC opening code. | Yes | Approved |  | Bay | 07-May-2026 | 11:08 | 07-May-2026 | 11:10
RQ108661 | PNOCC | kptcl | 400KV-BPS-YTPS-1 | KPTCL | C | Tightening/Fixing of spacers clamps bolts and nuts and attending repair of conductor damage (leads open) at location no’s 9-10, 11-12, 14-15, 16-17 | 2026-05-11 | 08:00 | 2026-05-11 | 18:00 | As 400KV-KALABURAGI-YTPS-1 work is approved on 11.05.2026 , it requires BPS YTPS 1 shutdown as it is multi circuit tower | Yes | Rejected | No N-1 for 400kV KALBURGY. KPTCL need to share the voltage management and load and generation management details along with PSS/E case studies for reliable operation | Line Circuits | 07-May-2026 | 16:34 | 08-May-2026 | 15:54
RQ108672 | EMERGENCY | AMGEPL_Kurnool | 400KV/33KV AMGEPL_SOLAR-ICT-2 | AMGEPL | C | LV-1 R-ph Bushing terminal connector hotspot observed around 104°C. | 2026-05-07 | 19:00 | 2026-05-08 | 04:00 | Outage proposal during non-solar hours. | Yes | Approved | Other ICTs shall be in service. | Transformer | 07-May-2026 | 17:26 | 07-May-2026 | 18:59
RQ108674 | PNOCC | PGCIL SR-1 | ANANTHPURAM - 400KV - BUS 1 | PGCIL SR-1 | D | For 419 bay equipment erection works | 2026-05-11 | 09:00 | 2026-05-11 | 18:00 |  | Yes | Approved | Remaining all elements shall be in service. | Bus | 07-May-2026 | 18:28 | 08-May-2026 | 15:12
RQ108687 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-17 | 06:00 | 2026-05-17 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 08-May-2026 | 11:12 | 14-May-2026 | 10:43
RQ108691 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-21 | 06:00 | 2026-05-21 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 08-May-2026 | 11:12 | 18-May-2026 | 10:13
RQ108695 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-17 | 06:00 | 2026-05-17 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 08-May-2026 | 11:12 | 14-May-2026 | 10:43
RQ108699 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-21 | 06:00 | 2026-05-21 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 08-May-2026 | 11:12 | 18-May-2026 | 10:13
RQ108720 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | PID scanning works old insulators. | 2026-05-15 | 08:00 | 2026-05-15 | 18:00 | PID Scanning of insulator. Please approve up to 31.05.2026 | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 08-May-2026 | 19:30 | 12-May-2026 | 15:24
RQ108726 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | PID scanning works old insulators. | 2026-05-21 | 08:00 | 2026-05-21 | 18:00 | PID Scanning of insulator. Please approve up to 31.05.2026 | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 08-May-2026 | 19:30 | 18-May-2026 | 11:55
RQ108739 | EMERGENCY | kseb | 220KV-ELAPULLY-MADAKATHARA-1 | KSEB | D | safety clearance issue.AUTORECLOSURE DISABLING ONLYFOR ARRANGING FAULT RECTIFICATION WORK ON 220 kV MADAKATHARA - PALAKKAD(2MDPK) FEEDER | 2026-05-09 | 07:00 | 2026-05-09 | 17:00 | R phase insulator flashed on tower loc 71 of 2MDPK feeder. | Yes | Approved | Approved on emergency subject to real time conditions and all 3 circuits of palakkad(Pg)-Palakkad to be in service and combined line loading to be less than 390MW | Auto Reclosure | 08-May-2026 | 23:20 | 09-May-2026 | 00:56
RQ108757 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | Live line PID testing of insulator in line | 2026-05-15 | 07:00 | 2026-05-15 | 18:00 | Nil | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 10-May-2026 | 13:18 | 12-May-2026 | 15:24
RQ108763 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | Live line PID testing of insulator in line | 2026-05-21 | 07:00 | 2026-05-21 | 18:00 | Nil | Yes | Approved | Remaining bays shall be in service. | Auto Reclosure | 10-May-2026 | 13:18 | 18-May-2026 | 11:55
RQ108768 | PNOCC | PGCIL SR-2 | A/R of 400KV-NARENDRA-GUTTUR-1 | POWERGRID | D | OPGW rectification works. | 2026-05-14 | 09:00 | 2026-05-14 | 17:00 | OPGW rectification works. | Yes | Rejected | Multiple shutdowns at the same stations. | Auto Reclosure | 10-May-2026 | 19:07 | 11-May-2026 | 11:15
RQ108771 | PNOCC | PGCIL SR-2 | A/R of 400KV-NARENDRA-GUTTUR-2 | POWERGRID | D | OPGW rectification works. | 2026-05-14 | 09:00 | 2026-05-14 | 17:00 | OPGW rectification works. | Yes | Rejected | Multiple shutdowns at the same stations. | Auto Reclosure | 10-May-2026 | 19:07 | 11-May-2026 | 11:15
RQ108782 | EMERGENCY | PGCIL SR-2 | HVDC 800KV PUGALUR HVDC POLE 1 | POWERGRID | D | To attend SF6 urgent alarm reported in 800 kV bushing of HV converter transformer. | 2026-05-11 | 07:40 | 2026-05-11 | 12:00 |  | Yes | Approved |  | HVDC Pole | 11-May-2026 | 07:35 | 11-May-2026 | 08:00
RQ108785 | PNOCC | PGCIL SR-1 | MAIN BAY (406) OF 400KV/220KV VIJAYAWADA-ICT-3 AND VIJAYAWADA - 400KV - BUS 2 @VIJAYAWADA - 400KV | PGCIL SR-1 | D | CB SF6 Gas Due point mesurement | 2026-05-15 | 09:00 | 2026-05-15 | 13:00 | CB SF6 Gas Due point mesuremen | Yes | Approved | Remaining bays shall be in service. Consecutive shutdown at the same station. | Bay | 11-May-2026 | 09:54 | 12-May-2026 | 15:24
RQ108786 | PNOCC | PGCIL SR-1 | MAIN BAY (407) OF VIJAYAWADA - 400KV B/R 3 AND VIJAYAWADA - 400KV - BUS 1 @VIJAYAWADA - 400KV | PGCIL SR-1 | D | CB SF6 Gas Due point mesuremen | 2026-05-15 | 14:00 | 2026-05-15 | 17:30 | CB SF6 Gas Due point mesuremen | Yes | Approved | Remaining bays shall be in service. Consecutive shutdown at the same station. | Bay | 11-May-2026 | 09:54 | 12-May-2026 | 15:24
RQ108791 | PNOCC | PGCIL SR-2 | MAIN BAY (415) OF 400KV-SALEM-DHARMAPURI-1 AND SALEM - 400KV - BUS 1 @SALEM - 400KV | PGCIL SR-2 | C | CB SF6 gas filtration works | 2026-05-15 | 09:30 | 2026-05-16 | 17:30 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 11-May-2026 | 12:56 | 12-May-2026 | 15:24
RQ108792 | EMERGENCY | aptransco | MAIN BAY (410) OF 400KV/21KV VTPS_IV-GT-7 AND VTPS_IV - 400KV - BUS 1 @VTPS_IV - 400KV | APGENCO | C | To attend the inspection & checking of marshalling boxes, Isolator marshalling boxes and ajustment of isloator of GT | 2026-05-11 | 14:00 | 2026-05-12 | 17:30 | Unit under shutdown due to BTL | Yes | Approved | Approved | Bay | 11-May-2026 | 13:38 | 11-May-2026 | 14:07
RQ108793 | EMERGENCY | aptransco | TIE BAY (411) OF 400KV/21KV VTPS_IV-GT-7 AND 400KV/220KV VTPS_IV-ICT-1 @VTPS_IV - 400KV | APGENCO | C | To attend the inspection & checking of marshalling boxes, Isolator marshalling boxes and ajustment of isloator of GT | 2026-05-11 | 13:45 | 2026-05-12 | 17:30 | Unit under shutdown due to BTL | Yes | Approved | Approved | Bay | 11-May-2026 | 13:41 | 11-May-2026 | 14:07
RQ108795 | EMERGENCY | PGCIL SR-2 | 400KV-NNTPP-PUDUCHERRY-1 | POWERGRID | D | Replacement of insulator string at loc. No 128 on | 2026-05-11 | 15:30 | 2026-05-11 | 19:20 | pl approve | Yes | Approved | During the shutdown following arrangement may be done. 1) 230kV Karaikal - Bahoor S/C shall be opened and kept idle charged from Bahoor side. 2) 230kV NLCTS2-Villiyanur S/C to be closed. 3) 230kV Pondy - Villiyanur S/C shall be opened and kept idle charged from the villiyanur end. | Line Circuits | 11-May-2026 | 15:23 | 11-May-2026 | 16:29
RQ108796 | EMERGENCY | PGCIL SR-2 | MAIN BAY (413) OF 400KV-UDUMALPET_PG-PALAKKAD-2 AND PALAKKAD - 400KV - BUS 1 @PALAKKAD - 400KV | PGCIL SR-2 | D | For checking SF6 gas leak issue in the breaker. | 2026-05-11 | 15:30 | 2026-05-11 | 22:00 | pl approve | Yes | Approved | Dia shall be in closed condition. | Bay | 11-May-2026 | 15:26 | 11-May-2026 | 15:49
RQ108797 | PNOCC | PGCIL SR-1 | MAIN BAY (404) OF 400KV-NPS-SEIL_P1-2 AND NPS - 400KV - BUS 1 @NPS - 400KV | PGCIL SR-1 | C | Bay AMP works and CB drive overhauling | 2026-05-15 | 06:00 | 2026-05-16 | 17:00 | Bay AMP works and CB drive overhauling | Yes | Approved | Remaining bays shall be in service. | Bay | 11-May-2026 | 16:34 | 12-May-2026 | 15:24
RQ108799 | PNOCC | PGCIL SR-2 | TIE BAY (417) OF 400KV-KALVENDAPATTU-PUGALUR-1 AND 400KV-PUGALUR HVDC-PUGALUR-2 @PUGALUR - 400KV | PGCIL SR-2 | D | FOR BAY AMP WORKS | 2026-05-15 | 09:30 | 2026-05-15 | 17:30 | PLEASE APPROVE | Yes | Approved | Remaining bays shall be in service. | Bay | 11-May-2026 | 18:22 | 12-May-2026 | 15:24
RQ108819 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-1 | KPTCL | D | For OPGW stringing work | 2026-05-17 | 06:00 | 2026-05-17 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 10:47 | 14-May-2026 | 10:43
RQ108823 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-1 | KPTCL | D | For OPGW stringing work | 2026-05-21 | 06:00 | 2026-05-21 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 10:47 | 18-May-2026 | 10:13
RQ108824 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-1 | KPTCL | D | For OPGW stringing work | 2026-05-22 | 06:00 | 2026-05-22 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 10:47 | 19-May-2026 | 10:09
RQ108828 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-2 | KPTCL | D | For OPGW stringing work | 2026-05-17 | 06:00 | 2026-05-17 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 10:47 | 14-May-2026 | 10:43
RQ108832 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-2 | KPTCL | D | For OPGW stringing work | 2026-05-21 | 06:00 | 2026-05-21 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 10:47 | 18-May-2026 | 10:13
RQ108833 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-2 | KPTCL | D | For OPGW stringing work | 2026-05-22 | 06:00 | 2026-05-22 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 10:47 | 19-May-2026 | 10:09
RQ108837 | PNOCC | NLC | 400KV/230KV NTPL-ICT-2 | NTPL | C | RTV Silicone Coating Work | 2026-05-19 | 09:00 | 2026-05-20 | 18:00 | Approved in the 237th Outage Co-ordination Meeting from 11/05 to 13/05. Request to reschedule as the contractor could not arrive on schedule due to unforeseen circumstances. | Yes | Approved | Other ICT to be in service. | Transformer | 12-May-2026 | 12:57 | 16-May-2026 | 11:11
RQ108838 | PNOCC | NLC | 400KV/230KV NTPL-ICT-2 | NTPL | C | RTV Silicone Coating Work | 2026-05-21 | 09:00 | 2026-05-21 | 18:00 | Approved in the 237th Outage Co-ordination Meeting from 11/05 to 13/05. Request to reschedule as the contractor could not arrive on schedule due to unforeseen circumstances. | Yes | Approved | Other ICT shall be in service. | Transformer | 12-May-2026 | 12:59 | 18-May-2026 | 11:51
RQ108843 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-3 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-21 | 07:00 | 2026-05-21 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 13:04 | 18-May-2026 | 10:13
RQ108844 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-3 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-22 | 07:00 | 2026-05-22 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 13:04 | 19-May-2026 | 10:09
RQ108850 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-4 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-21 | 07:00 | 2026-05-21 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 13:04 | 18-May-2026 | 10:13
RQ108851 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-4 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-22 | 07:00 | 2026-05-22 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 13:04 | 19-May-2026 | 10:09
RQ108856 | PNOCC | PGCIL SR-2 | 400KV-PALAVADI-RASIPALYAM-1 | TANTRANSCO | D | or adjusting of earth wire in 400kV Rasipalyam - Palavadi 1 & 2 lines to avoid tripping of 400KV Pugalur-Arasur lines at line crossing. | 2026-05-16 | 10:00 | 2026-05-16 | 13:00 | pl approve | Yes | Approved | Consecutive shutdown at the same station. 400KV-PALAVADI-RASIPALYAM other lines 33% each shall be in service. | Line Circuits | 12-May-2026 | 13:21 | 13-May-2026 | 10:24
RQ108857 | PNOCC | PGCIL SR-2 | 400KV-PALAVADI-RASIPALYAM-2 | TANTRANSCO | D | or adjusting of earth wire in 400kV Rasipalyam - Palavadi 1 & 2 lines to avoid tripping of 400KV Pugalur-Arasur lines at line crossing. | 2026-05-16 | 14:00 | 2026-05-16 | 17:00 | pl approve | Yes | Approved | Consecutive shutdown at the same station. 400KV-PALAVADI-RASIPALYAM other lines 33% each shall be in service. | Line Circuits | 12-May-2026 | 13:21 | 13-May-2026 | 10:24
RQ108867 | PNOCC | PGCIL SR-1 | MAHESHWARAM_PG - 765KV - BUS 2 | PGCIL SR-1 | C | S/D originally approved in OCC-237 from 11.05.2026 to 14.05.2026. Could not be availed due to S/D of Raichur-Sholapur Line-1. The same may be approved from 16.05.2026 to 19.05.2026. S/D may be extend up to 19.05.2026 | 2026-05-16 | 08:00 | 2026-05-17 | 23:59 | S/D originally approved in OCC-237 from 11.05.2026 to 14.05.2026. Could not be availed due to S/D of Raichur-Sholapur Line-1. The same may be approved from 16.05.2026 to 19.05.2026. S/D may be extend up to 19.05.2026 | Yes | Approved | Subject to NLDC approval and real time grid conditions. | Bus | 12-May-2026 | 21:40 | 13-May-2026 | 10:24
RQ108870 | EMERGENCY | aptransco | 400KV-HINDUJA-KALPAKKA-1 | APTRANSCO | C | For rectification of hot spots on Y-Ph jumper clamp | 2026-05-13 | 10:20 | 2026-05-13 | 13:15 | NO interruption to loads | Yes | Approved | Concurred on Emergency | Line Circuits | 13-May-2026 | 10:15 | 13-May-2026 | 11:34
RQ108872 | PNOCC | PGCIL SR-2 | MAIN BAY (406) OF 400KV-PAVAGADA_PG-MYSORE-1 AND MYSORE - 400KV - BUS 1 @MYSORE - 400KV | PGCIL SR-2 | D | For LBB relay retrofitting works | 2026-05-19 | 09:00 | 2026-05-19 | 17:30 | PLEASE APPROVE | Yes | Approved | Multiple shutdowns in near vicinity. | Bay | 13-May-2026 | 11:06 | 16-May-2026 | 11:36
RQ108877 | PNOCC | PGCIL SR-1 | MAHESHWARAM_PG - 765KV - BUS 2 | PGCIL SR-1 | C | S/D originally approved in OCC-237 from 11.05.2026 to 14.05.2026. Could not be availed due to S/D of Raichur-Sholapur Line-1. The same may be approved from 16.05.2026 to 19.05.2026. | 2026-05-18 | 00:01 | 2026-05-19 | 23:00 | S/D originally approved in OCC-237 from 11.05.2026 to 14.05.2026. Could not be availed due to S/D of Raichur-Sholapur Line-1. The same may be approved from 16.05.2026 to 19.05.2026 | Yes | Rejected | Multiple overlapping shutdowns. To be revived before 18.05.2026. | Bus | 13-May-2026 | 16:24 | 15-May-2026 | 11:30
RQ108879 | PNOCC | PGCIL SR-1 | 400KV-CUDDAPAH-NP_KUNTA-1 | POWERGRID | D | for facilitating Anantapur-Cuddapah line construction works | 2026-05-17 | 08:00 | 2026-05-17 | 14:00 | for facilitating Anantapur-Cuddapah line construction works | Yes | Approved | 400kV-CUDDAPAH-N P KUNTA-2,3 19% each 400kV-KOLAR- N P KUNTA 15% each 400kV-CHITTOOR-THIRUVALLAM D/C 15% each 765kV-CUDDAPAH-THIRUVALLAM D/C 400kV-CHITTOOR-RACHAGUNNERI D/C 10% each 400kV-KRISHNAPATTNAM-RACHAGUNNERI D/C 8% each 400kV-KOLAR-SRIPERUBUDUR 8% All 765kV/400kV THIRUVALLAM ICTs All 400kV/220kV CUDDAPAH ICTs shall be in service. | Line Circuits | 13-May-2026 | 17:44 | 14-May-2026 | 12:46
RQ108880 | PNOCC | PGCIL SR-1 | 400KV-CUDDAPAH-CHITTOOR-1 | POWERGRID | D | for facilitating Anantapur-Cuddapah line construction works | 2026-05-17 | 08:00 | 2026-05-17 | 14:00 | for facilitating Anantapur-Cuddapah line construction works | Yes | Approved | 400kV-CUDDAPAH-N P KUNTA-2,3 19% each 400kV-KOLAR- N P KUNTA 15% each 400kV-CHITTOOR-THIRUVALLAM D/C 15% each 765kV-CUDDAPAH-THIRUVALLAM D/C 400kV-CHITTOOR-RACHAGUNNERI D/C 10% each 400kV-KRISHNAPATTNAM-RACHAGUNNERI D/C 8% each 400kV-KOLAR-SRIPERUBUDUR 8% All 765kV/400kV THIRUVALLAM ICTs All 400kV/220kV CUDDAPAH ICTs shall be in service. | Line Circuits | 13-May-2026 | 17:44 | 14-May-2026 | 12:46
RQ108895 | PNOCC | TGTRANSCO | 400KV-YEDULA-MEHBOOBNAGAR-1 | TGTRANSCO | C | For for commissioning of line differential relay for line Yedula-Veltoor -1 | 2026-05-18 | 09:00 | 2026-05-18 | 19:00 | It is requested to accord the permission and issue LC opening code. | Yes | Approved | 400KV-YEDULA-MEHBOOBNAGAR-2 68% 400KV-MAHESHWARAM_TG-MAHESHWARAM_PG D/C 8% each 400KV-MAHESHWARAM_TG-DINDI D/C 7% each 400KV-YADADRI TPP-DINDI D/C shall be in service. | Line Circuits | 14-May-2026 | 10:51 | 15-May-2026 | 11:30
RQ108898 | EMERGENCY | APSPCL | 220KV-NP_KUNTA PSS3-NP_KUNTA-2 | APSPCL | C | Attending the isolator alignment works. | 2026-05-14 | 16:00 | 2026-05-14 | 21:00 |  | Yes | Approved |  | Line Circuits | 14-May-2026 | 13:37 | 14-May-2026 | 16:11
RQ108906 | EMERGENCY | aptransco | 400KV/220KV CHITTOOR-ICT-1 | APTRANSCO | D | For arresting oil leakage in LV Side B-PH CT stud | 2026-05-14 | 15:00 | 2026-05-14 | 17:00 | No load interuuption | Yes | Approved | ICT-2&3 to be in service. Load management to be done. | Transformer | 14-May-2026 | 15:03 | 14-May-2026 | 15:11
RQ108910 | PNOCC | PGCIL SR-1 | A/R of 400KV-KHAMMAM_PG-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-21 | 07:00 | 2026-05-21 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 14-May-2026 | 18:10 | 18-May-2026 | 11:55
RQ108916 | EMERGENCY | kseb | A/R of 220KV-ELAPULLY-MADAKATHARA-1 | KSEB | D | EMERGENCY; For the decapped Insulator Replacement / conductor repairing works (on R phase conductor) on Multi tower Loc #07 of 220kV MADAKKATHARA-ELANKUR feeder at kallayi, for urgent rectification of feeder fault. The multi tower is also carrying 220kV Madakkathara -Shornur feeder (2MDSH), 220kV Elappully - Madakkathara feeder (2ELMD) and 220kV Madakkathara - Palakkad feeder. | 2026-05-15 | 07:00 | 2026-05-15 | 17:00 | A/R WORK ONLY | Yes | Approved |  | Auto Reclosure | 15-May-2026 | 01:16 | 15-May-2026 | 06:20
RQ108921 | PNOCC | PGCIL SR-2 | HASSAN - 220KV - BUS 1 | PGCIL SR-2 | C | For AMP Works | 2026-05-19 | 09:00 | 2026-05-19 | 18:00 | 220kV Nus-1 shutdown was approved on OCC for 14.05.2026; however same could not be availed due to 201-89A isolator allignment issue. Same has been resolved | Yes | Approved | Remaining all elements shall be in service. | Bus | 15-May-2026 | 11:47 | 16-May-2026 | 11:36
RQ108924 | EMERGENCY | KSPDCL | 220KV-PAVAGADA_PG-RYCHALU2 | KSPDCL | C | To attend the hotspot on line isolator. | 2026-05-15 | 18:30 | 2026-05-15 | 21:00 |  | Yes | Approved |  | Line Circuits | 15-May-2026 | 16:04 | 15-May-2026 | 18:42
RQ108927 | EMERGENCY | UPCL | MAIN BAY (401) OF 420KV/22KV UPCL-GT-1 AND UPCL - 400KV - BUS 1 @UPCL - 400KV | ADANI | C | During switchyard conditional monitoring, 4 -152 CB Y ph CB pole minor SF6 leakge suspected and reading 0.81 bar to 0.78 bar reached and other poles are normal. Need to check leakage point and Gas top up to prevent alarming condition. | 2026-05-15 | 17:26 | 2026-05-15 | 19:30 | Kindly approve the Emergency shutdown of 401 Bay for gas filling work. Generator-1 will be service through 4-252 breaker. | Yes | Approved |  | Bay | 15-May-2026 | 17:34 | 15-May-2026 | 17:36
RQ108936 | PNOCC | PGCIL SR-2 | MAIN BAY (410) OF 400KV-ARASUR_PG-UDUMALPET_PG-2 AND ARASUR_PG - 400KV - BUS 1 @ARASUR_PG - 400KV | PGCIL SR-2 | C | for AMP works. | 2026-05-21 | 09:00 | 2026-05-21 | 18:00 | for AMP works. | Yes | Approved | Remaining bays shall be in service. | Bay | 16-May-2026 | 11:36 | 18-May-2026 | 11:55
RQ108937 | EMERGENCY | PGCIL SR-2 | 400KV/230KV TRICHY-ICT-1 | PGCIL SR-2 | D | For replacement of (IV side 216 kV) B-Ph LA due to THRC value violation. | 2026-05-16 | 12:30 | 2026-05-16 | 14:30 |  | Yes | Approved | All other ICT's shall be in service | Transformer | 16-May-2026 | 12:23 | 16-May-2026 | 12:49
RQ108938 | PNOCC | PGCIL SR-2 | MAIN BAY (427) OF 400KV-UDUMALPET_PG-PUGALUR HVDC-1 AND UDUMALPET_PG - 400KV - BUS 1 @UDUMALPET_PG - 400KV | PGCIL SR-2 | C | for AMP works. | 2026-05-21 | 09:00 | 2026-05-21 | 18:00 | for AMP works. | Yes | Approved | Remaining bays shall be in service. | Bay | 16-May-2026 | 12:25 | 18-May-2026 | 11:55
RQ108947 | PNOCC | KSPDCL | PAVAGADA_PG - 220KV - BUS 4 | PGCIL SR-2 | C | Jumper connection and isolator alignment work at newly constructed BAY-230 | 2026-05-21 | 18:00 | 2026-05-22 | 02:00 |  | Yes | Approved | Remaining all elements shall be in service. | Bus | 16-May-2026 | 15:27 | 18-May-2026 | 11:55
RQ108986 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | PID TESTING OF Porcelian disc insulator String | 2026-05-23 | 06:00 | 2026-05-23 | 18:00 | PID TESTING OF Porcelian disc insulator String | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 16-May-2026 | 19:27 | 20-May-2026 | 23:18
RQ108998 | PNOCC | TGTRANSCO | 400KV-GAJWEL-CHANDALAPUR-2 | TGTRANSCO | C | At 400KVSS Gajwel During analysis of DR and ELs for tripping of 400KV Chandulapur-2 feeder on Dt:14.04.2026, certain observations found in relay settings by Power systems wing and instructed to rectify the settings and ensure configuration of DR and ELs as per FOLD recommendations. Hence it is requested for issue of LC on 400KV Gajwel-Chandulapur-2 feeder on DT:20.05.2026 from 10 to 17Hrs for adopting the settings recommended by power systems wing. | 2026-05-20 | 10:00 | 2026-05-20 | 17:00 | please approve the LC | Yes | Approved | 400KV-CHANDALAPUR-GAJWEL-1 30% 400KV-TUKKAPUR-CHANDALAPUR D/C 13% each 400KV-TUKKAPUR-NARSAPUR D/C 13% each 400KV-RAMADUGU-GAJWEL D/C 9% each shall be in service. | Line Circuits | 17-May-2026 | 04:44 | 17-May-2026 | 15:33
RQ108999 | EMERGENCY | WKTL | KUDGI_PG - 400KV - BUS 2 | PGCIL SR-2 | C | Extension/Interconnection of400kv Main Bus-2 from existing PGCIL Kudgi to WRSR New Narendra. | 2026-05-18 | 09:00 | 2026-05-18 | 18:00 | This outage required on continuous basis from 18th-May-2026 09:00Hrs to 23rd-May-2026 18:00Hrs. | Yes | Approved | FTC is required. CEA safety approval submitted. Remaining all elements shall be in service. | Bus | 17-May-2026 | 12:03 | 18-May-2026 | 09:49
RQ109000 | EMERGENCY | WKTL | TIE BAY (420) OF 400KV-KOPPAL-KUDGI_PG-1 AND 400KV/220KV KUDGI_PG-ICT-3 @KUDGI_PG - 400KV | KNTL | C | Extension/Interconnection of400kv Main Bus-2 from existing PGCIL Kudgi to WRSR New Narendra. | 2026-05-18 | 09:00 | 2026-05-18 | 18:00 | This outage required on continuos basis from 18th-May-2026, 09:00Hrs to 23rd-May-2026, 18:00Hrs. | Yes | Approved | Approved along with Bus-2 shutdown. ICT-3 is a future element. | Bay | 17-May-2026 | 13:18 | 18-May-2026 | 09:49
RQ109001 | EMERGENCY | WKTL | MAIN BAY (421) OF 400KV/220KV KUDGI_PG-ICT-3 AND KUDGI_PG - 400KV - BUS 2 @KUDGI_PG - 400KV | KNTL | C | Extension/Interconnection of400kv Main Bus-2 from existing PGCIL Kudgi to WRSR New Narendra. | 2026-05-18 | 09:00 | 2026-05-18 | 18:00 | This outage required on continuos basis from 18th-May-2026, 09:00Hrs to 23rd-May-2026, 18:00Hrs. | Yes | Approved | Approved along with Bus-2 shutdown. ICT-3 is a future element. | Bay | 17-May-2026 | 13:25 | 18-May-2026 | 09:49
RQ109002 | EMERGENCY | WKTL | TIE BAY (423) OF 400KV-KOPPAL-KUDGI_PG-2 AND 400KV/220KV KUDGI_PG-ICT-4 @KUDGI_PG - 400KV | KTL | C | Extension/Interconnection of400kv Main Bus-2 from existing PGCIL Kudgi to WRSR New Narendra. | 2026-05-18 | 09:00 | 2026-05-18 | 18:00 | This outage required on continuos basis from 18th-May-2026, 09:00Hrs to 23rd-May-2026, 18:00Hrs. | Yes | Approved | Approved along with Bus-2 shutdown. ICT-4 is a future element. | Bay | 17-May-2026 | 13:29 | 18-May-2026 | 09:49
RQ109003 | EMERGENCY | WKTL | MAIN BAY (424) OF 400KV/220KV KUDGI_PG-ICT-4 AND KUDGI_PG - 400KV - BUS 2 @KUDGI_PG - 400KV | KTL | C | Extension/Interconnection of400kv Main Bus-2 from existing PGCIL Kudgi to WRSR New Narendra. | 2026-05-18 | 09:00 | 2026-05-18 | 18:00 | This outage required on continuos basis from 18th-May-2026, 09:00Hrs to 23rd-May-2026, 18:00Hrs. | Yes | Approved | Approved along with Bus-2 shutdown. ICT-4 is a future element. | Bay | 17-May-2026 | 13:34 | 18-May-2026 | 09:49
RQ109007 | PNOCC | PGCIL SR-1 | KURNOOL_PG - 400KV - BUS 2 | PGCIL SR-1 | C | As per OCC 237 S/D originally approved from 21.05.2026 to 22.05.2026. Due to site constraints , it is requested to postpone S/D from 23.05.2026 to 24.05.2026 on continuous basis.Kindly approve | 2026-05-23 | 07:30 | 2026-05-24 | 20:00 | As per OCC 237 S/D originally approved from 21.05.2026 to 22.05.2026. Due to site constraints , it is requested to postpone S/D from 23.05.2026 to 24.05.2026 on continuous basis.Kindly approve | Yes | Approved | Remaining all elements shall be in service. | Bus | 17-May-2026 | 16:24 | 20-May-2026 | 23:18
RQ109011 | EMERGENCY | kptcl | GUTTUR - 400KV - BUS 1 | KPTCL | C | for attending arching on ICT2 Bus-1 B phase PG isolator | 2026-05-18 | 10:37 | 2026-05-18 | 13:37 | for attending arching on ICT2 Bus-1 B phase PG isolator | Yes | Approved | Approved for 3 hrs. No N-1 for Bus-2. | Bus | 18-May-2026 | 10:38 | 18-May-2026 | 10:48
RQ109064 | PNOCC | PGCIL SR-1 | MAIN BAY (406) OF 400KV/220KV MEHBOOBNAGAR-ICT-2 AND MEHBOOBNAGAR - 400KV - BUS 2 @MEHBOOBNAGAR - 400KV | TGTRANSCO | C | Originally approved in MidOCC-237-1, from 10.05.2026 to 16.05.2026 for construction/Add CAP Bay upgradation works under SS-126.Due to site constraints, please extend the bay shutdown upto 31.05.2026. | 2026-05-22 | 00:00 | 2026-05-23 | 23:59 | Originally approved in MidOCC-237-1, from 10.05.2026 to 16.05.2026 for construction/Add CAP Bay upgradation works under SS-126.Due to site constraints, please extend the bay shutdown upto 31.05.2026. | Yes | Rejected | Multiple shutdowns at the same station. | Bay | 18-May-2026 | 16:49 | 19-May-2026 | 10:34
RQ109078 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-NAGARJUNASAGAR_PG-1 | POWERGRID | D | PID Scanning of porcelain insulators. | 2026-05-23 | 06:00 | 2026-05-23 | 18:00 | PID Scanning of porcelain insulators. | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 18-May-2026 | 17:53 | 20-May-2026 | 23:18
RQ109114 | PNOCC | PGCIL SR-2 | 400KV-GADAG_PSS-KOPPAL-1 | GADAG_II_A | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 11/0 - 12/0. | 2026-05-22 | 08:00 | 2026-05-22 | 19:00 | Approved under OCC_2371 on 19.05.2026. Rescheduling due to pendency of pre-shutdown preparatory works because of continuous rains at site. TSP/IPP concurrences will be submitted on D-2 basis. Kindly approve. | Yes | Approved | PGCIL SR-2 submitted the RE developer and KNTL concurrence through mail dated 21-05-2026. 400kV-KUDGI_PG - KOPPAL D/C 50% 400kV-KUDGI_PG - GADAG D/C each shall be in service. Subject to real time RE generation and line loadings. Subject to adherence of proper RE schedules. | Line Circuits | 18-May-2026 | 23:21 | 19-May-2026 | 10:34
RQ109116 | PNOCC | PGCIL SR-2 | 400KV-GADAG_PSS-KOPPAL-2 | GADAG_II_A | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 11/0 - 12/0. | 2026-05-22 | 08:00 | 2026-05-22 | 19:00 | Approved under OCC_2371 on 19.05.2026. Rescheduling due to pendency of pre-shutdown preparatory works because of continuous rains at site. TSP/IPP concurrences will be submitted on D-2 basis. Kindly approve. | Yes | Approved | PGCIL SR-2 submitted the RE developer and KNTL concurrence through mail dated 21-05-2026. 400kV-KUDGI_PG - KOPPAL D/C 50% 400kV-KUDGI_PG - GADAG D/C each shall be in service. Subject to real time RE generation and line loadings. Subject to adherence of proper RE schedules. | Line Circuits | 18-May-2026 | 23:24 | 19-May-2026 | 10:34
RQ109117 | PNOCC | PGCIL SR-2 | 400KV-GADAG_PSS-KOPPAL-2 | GADAG_II_A | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 11/0 - 12/0. | 2026-05-23 | 08:00 | 2026-05-23 | 19:00 | Approved under OCC_2371 on 19.05.2026. Rescheduling due to pendency of pre-shutdown preparatory works because of continuous rains at site. TSP/IPP concurrences will be submitted on D-2 basis. Kindly approve. | Yes | Rejected | Deferred by PGCIL-SR2. KNTL concurrence also need to be submitted for not availing the 220kV-BUS-4 shutdown at KOPPAL for the same date. PGCIL SR-2 submitted the RE developer concurrence through mail dated 21-05-2026. 400kV-KUDGI_PG - KOPPAL D/C 50% 400kV-KUDGI_PG - GADAG D/C each shall be in service. Subject to real time RE generation and line loadings. Subject to adherence of proper RE schedules. | Line Circuits | 18-May-2026 | 23:24 | 20-May-2026 | 23:10
RQ109119 | EMERGENCY | NTPC | 400KV/220KV RAMAGUNDAM-ICT-4 | NTPC | C | for line equipment testing | 2026-05-19 | 09:54 | 2026-05-19 | 17:30 | connected line in shutdown for maintenance works at other end | Yes | Approved | 220KV-RAMAGUNDAM-MALYALAPALLI-2 already approved for today. | Transformer | 19-May-2026 | 09:56 | 19-May-2026 | 10:41
RQ109140 | EMERGENCY | TGTRANSCO | TIE BAY (414) OF 400KV-KETHIREDDYPALLY-RAYADURG-1 AND FUTURE @KETHIREDDYPALLY - 400KV | TGTRANSCO | C | On emergency basis for top up of SF6 gas in Y ph limb | 2026-05-19 | 15:44 | 2026-05-19 | 16:30 | Please approve LC | Yes | Approved | 413,415 shall be in service. | Bay | 19-May-2026 | 15:45 | 19-May-2026 | 16:02
RQ109224 | EMERGENCY | aptransco | 400KV-TALARCHEVU-JAMMALAMADUGU-1 | APTRANSCO | C | For fixing of Isolator alignment | 2026-05-21 | 00:30 | 2026-05-21 | 01:00 |  | Yes | Approved | Other lines at JAMMALAMADUGU shall be in service. | Line Circuits | 21-May-2026 | 00:03 | 21-May-2026 | 00:48
RQ109228 | EMERGENCY | PGCIL SR-2 | TIE BAY (422) OF 400KV-MADURAI_PG-TIRUNELVELI-2 AND MADURAI_PG - 400KV - BUS 2 @MADURAI_PG - 400KV | PGCIL SR-2 | D | emergency shutdown is requested due to persisting SF6 Low Alarm in B Ph breaker. | 2026-05-21 | 08:15 | 2026-05-21 | 12:15 | pl approve | Yes | Approved | 421, 423 bays shall be in service | Bay | 21-May-2026 | 08:15 | 21-May-2026 | 08:17
RQ107809 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-11 | 06:00 | 2026-05-11 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 28-Apr-2026 | 19:02 | 08-May-2026 | 15:05
RQ107819 | PNOCC | PGCIL SR-1 | A/R of 400KV-GOOTY-KURNOOL_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-11 | 08:00 | 2026-05-11 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 28-Apr-2026 | 19:08 | 08-May-2026 | 15:05
RQ108621 | EMERGENCY | TGTRANSCO | 400KV/11KV CHANDALAPUR-CONS-ST-1 | TGTRANSCO | C | For replacing failed Summation Check Meter with new one immediately by TGSPDCL since the warranty is about to expire this month [From:06/05/2026 13:00 To 06/05/2026 16:00] | 2026-05-06 | 13:00 | 2026-05-06 | 16:00 | pl approve | Yes | Approved |  | Transformer | 05-May-2026 | 17:23 | 06-May-2026 | 14:23
RQ108622 | EMERGENCY | TGTRANSCO | 400KV/11KV CHANDALAPUR-CONS-ST-2 | TGTRANSCO | C | For replacing failed Summation Check Meter with new one immediately by TGSPDCL since the warranty is about to expire this month [From:06/05/2026 13:00 To 06/05/2026 16:00] | 2026-05-06 | 13:00 | 2026-05-06 | 16:00 | pl approve | Yes | Approved |  | Transformer | 05-May-2026 | 17:23 | 06-May-2026 | 14:23
RQ108626 | EMERGENCY | aptransco | 400KV-GUDIWADA-VEMAGIRI_AP-1 | APTRANSCO | C | for replacement of the insulator stack @ location No.221 | 2026-05-06 | 09:15 | 2026-05-06 | 15:15 | heavy sparks observed on Y-Phase insulator stack | Yes | Approved | Line-2 shall be in service. | Line Circuits | 06-May-2026 | 09:11 | 06-May-2026 | 09:38
RQ108627 | EMERGENCY | kptcl | 400KV-JINDAL-BPS-4 | KPTCL | C | to attend damaged conductor | 2026-05-06 | 09:15 | 2026-05-06 | 15:00 | emergency | Yes | Approved | APPROVED | Line Circuits | 06-May-2026 | 09:15 | 06-May-2026 | 09:28
RQ108634 | EMERGENCY | aptransco | 400KV/220KV NELLORE_AP-ICT-1 | APTRANSCO | C | for replacing damed BPl and arresting oil leak from LV B-hase CT stud. | 2026-05-06 | 14:30 | 2026-05-06 | 17:00 |  | Yes | Approved |  | Transformer | 06-May-2026 | 14:06 | 06-May-2026 | 14:34
RQ108639 | PNOCC | PGCIL SR-2 | TIE BAY (405) OF 400KV-SALEM-UDUMALPET_PG-2 AND 400KV-UDUMALPET_PG-PALAKKAD-2 @UDUMALPET_PG - 400KV | PGCIL SR-2 | D | Bay AMP works. | 2026-05-11 | 09:00 | 2026-05-11 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 06-May-2026 | 21:02 | 08-May-2026 | 15:05
RQ108652 | EMERGENCY | aptransco | 220KV-SULURPET-GUMMIDIPOONDI-1 | APTRANSCO,TANTRANSCO | C | for rectificaiton of hotspots on wave trap jumper clamp at Sullurpeta SS | 2026-05-07 | 11:02 | 2026-05-07 | 13:02 |  | Yes | Approved | TNEB CONCURRENCE RECEIVED. | Line Circuits | 07-May-2026 | 11:04 | 07-May-2026 | 14:39
RQ108657 | EMERGENCY | kptcl | 400KV/220KV MYLASANDRA-ICT-2 | KPTCL | C | LC on ICT-2 to replace faulty Winding temperature indicators (WTIs of MV & IV) . | 2026-05-07 | 14:00 | 2026-05-07 | 15:30 | emergency basis | Yes | Approved | 400KV/220KV MYLASANDRA-ICT-1 and 3 are 16% sensitive each, 200kV Somanahalli-Mylasandra D/C is having sensitivity of 25% each. 400kV- Mylasandra-Somanahalli shall be in service. System is not N-1 secure. Load management to be done by KPTCL. | Transformer | 07-May-2026 | 13:14 | 07-May-2026 | 14:12
RQ108659 | EMERGENCY | TGTRANSCO | 400KV/220KV RAMAGUNDAM-ICT-3 | NTPC | C | To attend red hot complaint on R Ph T jumper. | 2026-05-07 | 15:40 | 2026-05-07 | 18:00 | Please issue LC. | Yes | Approved |  | Transformer | 07-May-2026 | 15:37 | 07-May-2026 | 15:59
RQ108660 | EMERGENCY | PGCIL SR-1 | 765KV-RAICHUR_PG-SHOLAPUR-1 | POWERGRID | C | Tower erection works of AP 4A/0-- 765KV KOPPAL RAICHUR LINE | 2026-05-08 | 08:00 | 2026-05-14 | 18:00 | Construction works | Yes | Approved | NEW-SR - 150 Import / 700 Export MW reduction, Subject to real time grid conditions. As discussed in 237 outage co-ordination meeting, Forum approved the S/D from 5th May for 10 days. PG to strictly adhere to the timelines. 765KV-RAICHUR_PG-SHOLAPUR-2 49% 765kV-KURNOOL-MAHESHWARAM D/C 13% each 765kV-WARORA-WARANGAL D/C 11% each 765kV-WARDHA-NIZAMABAAD D/C 9% each 765kV-WARANGAL-MAHESHWARAM D/C 6% each All NIZAMABAAD ICTs shall be in service. PGCIL SR-1 is not availing the shutdown of 765kV-RAICHUR-KURNOOL-1. Postponed by requester over telephonic communication. PGCIL SR-1 requested to avail from 08.05.2026 to 14.05.2026. | Line Circuits | 07-May-2026 | 16:28 | 07-May-2026 | 16:29
RQ108666 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | PID Works | 2026-05-11 | 07:00 | 2026-05-11 | 13:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 07-May-2026 | 17:09 | 08-May-2026 | 15:05
RQ108670 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | PID Works | 2026-05-11 | 06:00 | 2026-05-11 | 13:00 |  | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 07-May-2026 | 17:13 | 08-May-2026 | 15:05
RQ108671 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-GAJWEL-1 | POWERGRID | D | PID Works | 2026-05-11 | 06:00 | 2026-05-11 | 18:00 |  | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 07-May-2026 | 17:15 | 08-May-2026 | 15:05
RQ108673 | PNOCC | PGCIL SR-1 | MAIN BAY (413) OF 400KV-SIMHADRI-GAZUWAKA-2 AND GAZUWAKA - 400KV - BUS 2 @GAZUWAKA - 400KV | PGCIL SR-1 | D | Bay AMP works. | 2026-05-11 | 09:00 | 2026-05-11 | 18:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 07-May-2026 | 17:28 | 08-May-2026 | 15:05
RQ108675 | PNOCC | PGCIL SR-1 | MAIN BAY (404) OF VIJAYAWADA - 400KV B/R 4 AND VIJAYAWADA - 400KV - BUS 1 @VIJAYAWADA - 400KV | PGCIL SR-1 | D | CB- Measurement of Sf6 gas DEW point | 2026-05-11 | 09:00 | 2026-05-11 | 13:00 |  | Yes | Approved | Remaining bays shall be in service. Consecutive shutdown at the same station. | Bay | 07-May-2026 | 18:33 | 08-May-2026 | 15:05
RQ108676 | PNOCC | PGCIL SR-1 | TIE BAY (405) OF 400KV/220KV VIJAYAWADA-ICT-3 AND VIJAYAWADA - 400KV B/R 4 @VIJAYAWADA - 400KV | PGCIL SR-1 | D | CB- Measurement of Sf6 gas DEW point | 2026-05-11 | 14:00 | 2026-05-11 | 18:00 |  | Yes | Approved | Remaining bays shall be in service. Consecutive shutdown at the same station. | Bay | 07-May-2026 | 18:33 | 08-May-2026 | 15:05
RQ108678 | PNOCC | PGCIL SR-2 | MAIN BAY (413) OF 400KV-KALVENDAPATTU-NNTPP-1 AND KALVENDAPATTU - 400KV - BUS 2 @KALVENDAPATTU - 400KV | PGCIL SR-2 | D | Bay AMP works. | 2026-05-11 | 09:00 | 2026-05-11 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 07-May-2026 | 19:53 | 08-May-2026 | 15:05
RQ108689 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-19 | 06:00 | 2026-05-19 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 08-May-2026 | 11:12 | 16-May-2026 | 11:04
RQ108697 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-19 | 06:00 | 2026-05-19 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 08-May-2026 | 11:12 | 16-May-2026 | 11:04
RQ108721 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | PID scanning works old insulators. | 2026-05-16 | 08:00 | 2026-05-16 | 18:00 | PID Scanning of insulator. Please approve up to 31.05.2026 | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 08-May-2026 | 19:30 | 13-May-2026 | 10:17
RQ108740 | EMERGENCY | kseb | 220KV-ELAPULLY-PALAKKAD(KL)-1 | KSEB | D | For opening the breakers at both ends to close the isolator at Palakkad station | 2026-05-09 | 03:37 | 2026-05-09 | 04:00 | Isolator at PALAKKAD got opened due to unknown reason. | Yes | Approved | Line-2,3 shall be in service. | Line Circuits | 09-May-2026 | 03:41 | 09-May-2026 | 03:54
RQ108741 | EMERGENCY | kptcl | 400KV-KAIGA-GUTTUR-1 | PGCIL SR-2,KPTCL | C | to replace these broken polymer insulators and replace broken spacers | 2026-05-09 | 09:04 | 2026-05-09 | 14:04 | to replace these broken polymer insulators and replace broken spacers | Yes | Approved |  | Line Circuits | 09-May-2026 | 09:06 | 09-May-2026 | 09:12
RQ108753 | EMERGENCY | PGCIL SR-2 | 400KV-NNTPP-PUDUCHERRY-1 | POWERGRID | C | Emergency shutdown required to attend damaged Middle phase Insulator at Loc:104 | 2026-05-10 | 08:00 | 2026-05-10 | 11:00 |  | Yes | Approved | Load management to be done by PONDY. No N-1 for 230 kV S/S of PONDY. | Line Circuits | 10-May-2026 | 01:43 | 10-May-2026 | 10:06
RQ108758 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | Live line PID testing of insulator in line | 2026-05-16 | 07:00 | 2026-05-16 | 18:00 | Nil | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 10-May-2026 | 13:18 | 13-May-2026 | 10:17
RQ108770 | PNOCC | PGCIL SR-2 | A/R of 400KV-NARENDRA-GUTTUR-1 | POWERGRID | D | OPGW rectification works. | 2026-05-16 | 09:00 | 2026-05-16 | 17:00 | OPGW rectification works. | Yes | Rejected | In view of tower collapse at KAIGA -GUTTUR. | Auto Reclosure | 10-May-2026 | 19:07 | 13-May-2026 | 10:17
RQ108773 | PNOCC | PGCIL SR-2 | A/R of 400KV-NARENDRA-GUTTUR-2 | POWERGRID | D | OPGW rectification works. | 2026-05-16 | 09:00 | 2026-05-16 | 17:00 | OPGW rectification works. | Yes | Rejected | In view of tower collapse at KAIGA -GUTTUR. | Auto Reclosure | 10-May-2026 | 19:07 | 13-May-2026 | 10:17
RQ108775 | PNOCC | PGCIL SR-2 | A/R of 400KV-KUDGI_PG-NARENDRA-1 | POWERGRID | D | OPGW rectification works. | 2026-05-19 | 09:00 | 2026-05-19 | 17:00 | OPGW rectification works. | Yes | Rejected | Due to 400kV KAIGA - GUTTUR D/C tower collapse. | Auto Reclosure | 10-May-2026 | 19:07 | 16-May-2026 | 11:04
RQ108778 | PNOCC | PGCIL SR-2 | A/R of 400KV-KUDGI_PG-NARENDRA-2 | POWERGRID | D | OPGW rectification works. | 2026-05-19 | 09:00 | 2026-05-19 | 17:00 | OPGW rectification works. | Yes | Rejected | Due to 400kV KAIGA - GUTTUR D/C tower collapse. | Auto Reclosure | 10-May-2026 | 19:07 | 16-May-2026 | 11:04
RQ108788 | EMERGENCY | TGTRANSCO | 220KV-WARANGAL-NAGARAM-2 | TGTRANSCO | C | For Attending red hot on R-phase line isolator fixed contact towards CT at Nagaram SS | 2026-05-11 | 11:30 | 2026-05-11 | 12:30 | Please issue LC | Yes | Approved |  | Line Circuits | 11-May-2026 | 11:30 | 11-May-2026 | 11:49
RQ108790 | PNOCC | PGCIL SR-2 | PAVAGADA_PG - 400KV - BUS 1 | PGCIL SR-2 | C | Connection of Jumpers with new Bay and Carrying out 400 kV Bus Bar-1 Stability Tests under ICT‑07 construction works. | 2026-05-15 | 17:00 | 2026-05-15 | 23:59 | The shutdown was approved in OCC 237 OCC for 12.05.2026, but due to non availability of OEM we are unable to avail the 400KV Bus-1 shutdown at Pavagada SS. Hence, it is requested to kindly reschedule the shutdown as requested. | Yes | Approved | Concurred, subject to real time grid conditions. | Bus | 11-May-2026 | 12:43 | 12-May-2026 | 15:41
RQ108794 | EMERGENCY | PGCIL SR-2 | TIE BAY (417) OF 400KV-MYSORE-KOZHIKODE-1 AND 400KV-HASSAN-MYSORE-1 @MYSORE - 400KV | PGCIL SR-2 | D | To attend TC-1 Faulty alarm in the Breaker | 2026-05-11 | 15:00 | 2026-05-11 | 18:00 | pl approve | Yes | Approved | Approved | Bay | 11-May-2026 | 14:55 | 11-May-2026 | 14:56
RQ108800 | EMERGENCY | TANTRANSCO | SHOLINGANALLUR - 400KV B/R 1 | TANTRANSCO | C | oil leak is observed in top side near R ph torret | 2026-05-11 | 18:30 | 2026-05-12 | 23:59 | Bus Reactor in open Condition | Yes | Approved |  | Bus Reactor | 11-May-2026 | 18:25 | 11-May-2026 | 20:07
RQ108801 | PNOCC | PGCIL SR-1 | A/R of 400KV-GOOTY-KURNOOL_PG-1 | POWERGRID | D | Live Line PID scanning works of Insulators. | 2026-05-16 | 07:00 | 2026-05-16 | 18:00 | NIL | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 11-May-2026 | 18:30 | 13-May-2026 | 10:17
RQ108804 | PNOCC | PGCIL SR-1 | A/R of 400KV-KHAMMAM_PG-WARANGAL-1 | POWERGRID | D | PID Scanning of Insulators | 2026-05-15 | 06:00 | 2026-05-15 | 14:00 |  | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 11-May-2026 | 19:28 | 12-May-2026 | 15:41
RQ108805 | PNOCC | PGCIL SR-1 | A/R of 400KV-KHAMMAM_PG-WARANGAL-1 | POWERGRID | D | PID Scanning of Insulators | 2026-05-16 | 06:00 | 2026-05-16 | 14:00 |  | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 11-May-2026 | 19:28 | 13-May-2026 | 10:17
RQ108821 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-1 | KPTCL | D | For OPGW stringing work | 2026-05-19 | 06:00 | 2026-05-19 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 10:47 | 16-May-2026 | 11:04
RQ108826 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-1 | KPTCL | D | For OPGW stringing work | 2026-05-24 | 06:00 | 2026-05-24 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 10:47 | 21-May-2026 | 10:07
RQ108827 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-1 | KPTCL | D | For OPGW stringing work | 2026-05-25 | 06:00 | 2026-05-25 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 10:47 | 22-May-2026 | 10:42
RQ108830 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-2 | KPTCL | D | For OPGW stringing work | 2026-05-19 | 06:00 | 2026-05-19 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 10:47 | 16-May-2026 | 11:04
RQ108835 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-2 | KPTCL | D | For OPGW stringing work | 2026-05-24 | 06:00 | 2026-05-24 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 10:47 | 21-May-2026 | 10:07
RQ108836 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-2 | KPTCL | D | For OPGW stringing work | 2026-05-25 | 06:00 | 2026-05-25 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 10:47 | 22-May-2026 | 10:42
RQ108840 | PNOCC | NLC | 400KV-NTPL-TUTICORIN_PS-2 | POWERGRID | D | RTV Silicone Coating Work | 2026-05-23 | 09:00 | 2026-05-23 | 18:00 | Approved in the 237th Outage Co-ordination Meeting from 15/05 to 16/05. Request to reschedule as the contractor could not arrive on schedule due to unforeseen circumstances. | Yes | Approved | No N-1 for NTPL. Mail communication received from NTPL to keep both units at technical minimum during the shutdown. Same need to be adhered by NTPL along with shutdown timelines. 400KV-NTPL-TUTICORIN_PS-1 100% shall be in service. | Line Circuits | 12-May-2026 | 13:03 | 20-May-2026 | 11:16
RQ108841 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-3 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-19 | 07:00 | 2026-05-19 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 13:04 | 16-May-2026 | 11:04
RQ108846 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-3 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-24 | 07:00 | 2026-05-24 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 13:04 | 21-May-2026 | 10:07
RQ108847 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-3 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-25 | 07:00 | 2026-05-25 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 13:04 | 22-May-2026 | 10:42
RQ108848 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-4 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-19 | 07:00 | 2026-05-19 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 13:04 | 16-May-2026 | 11:04
RQ108853 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-4 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-24 | 07:00 | 2026-05-24 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 13:04 | 21-May-2026 | 10:07
RQ108854 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-4 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-25 | 07:00 | 2026-05-25 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 13:04 | 22-May-2026 | 10:42
RQ108861 | EMERGENCY | PGCIL SR-2 | PAVAGADA_PG - 220KV - BUS 4 | PGCIL SR-2 | D | To rectify Alignment issue In 214-89B Isolator at Pavagada SS | 2026-05-12 | 18:00 | 2026-05-12 | 22:00 |  | Yes | Approved | All other buses shall be in service. | Bus | 12-May-2026 | 15:44 | 12-May-2026 | 19:49
RQ108862 | EMERGENCY | PGCIL SR-1 | A/R of 400KV-BHADRAVATHI-RAMAGUNDAM-1 | POWERGRID | D | For removal of foreign material (tarpaulin) was found hanging on OPGW at location: T0022. | 2026-05-12 | 17:00 | 2026-05-12 | 18:00 | For removal of foreign material (tarpaulin) was found hanging on OPGW at location: T0022. | Yes | Approved |  | Auto Reclosure | 12-May-2026 | 16:55 | 12-May-2026 | 16:59
RQ108865 | PNOCC | PGCIL SR-2 | MAIN BAY (404) OF 400KV-KOLAR_AC-THIRUVALAM-1 AND KOLAR_AC - 400KV - BUS 1 @KOLAR_AC - 400KV | PGCIL SR-2 | D | For AMP Works | 2026-05-22 | 09:00 | 2026-05-22 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 12-May-2026 | 20:32 | 19-May-2026 | 14:55
RQ108866 | PNOCC | PGCIL SR-2 | MAIN BAY (416) OF 400KV-KALVENDAPATTU-PUGALUR-1 AND KALVENDAPATTU - 400KV - BUS 2 @KALVENDAPATTU - 400KV | PGCIL SR-2 | D | For AMP Works | 2026-05-16 | 09:00 | 2026-05-16 | 18:00 |  | Yes | Rejected | Multiple shutdowns at the same station. | Bay | 12-May-2026 | 20:58 | 13-May-2026 | 10:17
RQ108897 | EMERGENCY | TANTRANSCO | 400KV-NCTPS_STAGE_II-MANALI-1 | TANTRANSCO | D | 400 KV NCTPS _ MANALI # insulator decap in loc:27, message received by consumer complaint feeder is not tripped still in service local people complaint no safety feeder to be hand trip immediately( ground to conductor clearance 5 feet only). Due to safety aspects emergency LC required to attend insulator replacement. Athipet Lines instructed to apply LC. Need LC on emergency grounds | 2026-05-14 | 14:10 | 2026-05-14 | 18:00 |  | Yes | Approved | Load managment to be done by TN if required | Line Circuits | 14-May-2026 | 13:16 | 14-May-2026 | 13:24
RQ108923 | EMERGENCY | PGCIL SR-1 | TIE BAY (717) OF RAICHUR_PG - 765KV B/R 2 AND RAICHUR_PG - 765KV - BUS 1 @RAICHUR_PG - 765KV | PGCIL SR-1 | D | To attend SF6 gas leakage issue in 71752 CB | 2026-05-15 | 12:31 | 2026-05-15 | 18:31 | To attend SF6 gas leakage issue in 71752 CB | Yes | Approved | Dia shall be in service | Bay | 15-May-2026 | 12:35 | 15-May-2026 | 13:02
RQ108940 | PNOCC | PGCIL SR-2 | TIE BAY (429) OF 400KV-UDUMALPET_PG-PUGALUR HVDC-2 AND UDUMALPET_PG - 400KV - BUS 1 @UDUMALPET_PG - 400KV | PGCIL SR-2 | C | for AMP works. | 2026-05-25 | 09:00 | 2026-05-25 | 18:00 | for AMP works. | Yes | Approved | Remaining bays shall be in service. | Bay | 16-May-2026 | 12:31 | 22-May-2026 | 12:59
RQ108943 | PNOCC | TANTRANSCO | 400KV/110KV KAYATHAR-ICT-4 | TANTRANSCO | D | Parallel operation test of newly erected 400/110KV 200MVA ICT5 with 400/110KV 200MVA ICT4 by P& C wing | 2026-05-25 | 17:30 | 2026-05-25 | 22:30 | During the LC period, there will be no supply in 400 KV Main Breaker for ICT4 (404-52), 400 KV Tie Breaker for ICT1 & ICT4 (405-52), 110KV LV Breaker (106-52) of ICT4 . 400/110KV ICT1 and other Grid feeders will be in service .Hence no SS will be affected. | Yes | Approved | In future, any planned Activities to be taken into Main OCC. Shutdown to be availed only after 17:30 HRS. N-1 limit for 400KV/110KV KAYATHAR-ICTs is 95 MW each. Load Management need to be done by TN. | Transformer | 16-May-2026 | 15:01 | 22-May-2026 | 13:19
RQ108944 | PNOCC | TANTRANSCO | 400KV-KAYATHAR-KANARPATTI-1 | TANTRANSCO | D | Bus bar Stability test for newly erected 400KV bay No 422 with 400KV Kanarpatti#1 Main Breaker (403-52) & CT and Tie breaker(402-52)and entire line | 2026-05-22 | 10:00 | 2026-05-22 | 14:00 | During the LC period, there will no supply in 400KV Kanarpatti#1 ,Main Breaker (403-52) & CT and Tie breaker(402-52)and entire line. 400KV Kanarpatti#2 will cater the 400KV Kanarpatti#1.Hence no ss will be affected. | Yes | Approved | Approval MOM for 400kV/110kV ICT-5, SLD and details of work submitted by TN. In future, any planned testing activities to be routed through Main OCC. Consecutive shutdowns at the same station. 400KV-KANARPATTI-KAYATHAR-2 87% 400KV-KAYATHAR-KARAIKUDI D/C 400kV-KANARPATTI-TIRUNELVELI shall be in service along with remaining all other lines. Line loadings to be below 50% of their thermal rating prior to the shutdown. No N-1 for 400kV KANARPATTI S/S. In case of contingency of other parallel circuit of 400KV-KAYATHAR-KANARPATTI, Load and RE generation and voltage management need to be done by TN. Sensitivities on other lines in case of N-1 contingency: 400KV-KAYATHAR-KARAIKUDI D/C 22% each 400KV-TUTICORIN_PS-TIRUNELVELI 19% each 400KV-KARAIKUDI-MADURAI_PG 17% 230KV-KAYATHAR(TN)-TIRUNELVELI 14% 400KV/230KV KAYATHAR-ICT-2 16%. Severe low voltages are expected under contingency of other line at 400kV VIRUDHUNAGAR, KAYATHAR, KARAIKUDI, THENNAMPATTY, and VELLALVIDUTHI S/S. | Line Circuits | 16-May-2026 | 15:09 | 19-May-2026 | 15:01
RQ108945 | PNOCC | TANTRANSCO | 400KV-KAYATHAR-KANARPATTI-2 | TANTRANSCO | D | Bus bar Stability test for newly erected 400KV bay No 420 with 400KV Kanarpatti#2 Main Breaker (401-52) | 2026-05-22 | 14:00 | 2026-05-22 | 18:00 | During the LC period, there will no supply in 400KV Kanarpatti#2 ,Main Breaker (401-52) & CT and Tie breaker(402-52)and entire line. 400KV Kanarpatti#1 will cater the 400KV Kanarpatti#2 load.Hence No SS will be affected. | Yes | Approved | Approval MOM for 400kV/110kV ICT-5, SLD and details of work submitted by TN. In future, any planned testing activities to be routed through Main OCC. Consecutive shutdowns at the same station. 400KV-KANARPATTI-KAYATHAR-2 87% 400KV-KAYATHAR-KARAIKUDI D/C 400kV-KANARPATTI-TIRUNELVELI shall be in service along with remaining all other lines. Line loadings to be below 50% of their thermal rating prior to the shutdown. No N-1 for 400kV KANARPATTI S/S. In case of contingency of other parallel circuit of 400KV-KAYATHAR-KANARPATTI, Load and RE generation and voltage management need to be done by TN. Sensitivities on other lines in case of N-1 contingency: 400KV-KAYATHAR-KARAIKUDI D/C 22% each 400KV-TUTICORIN_PS-TIRUNELVELI 19% each 400KV-KARAIKUDI-MADURAI_PG 17% 230KV-KAYATHAR(TN)-TIRUNELVELI 14% 400KV/230KV KAYATHAR-ICT-2 16%. Severe low voltages are expected under contingency of other line at 400kV VIRUDHUNAGAR, KAYATHAR, KARAIKUDI, THENNAMPATTY, and VELLALVIDUTHI S/S. | Line Circuits | 16-May-2026 | 15:09 | 19-May-2026 | 15:01
RQ108949 | PNOCC | KSPDCL | PAVAGADA_PG - 220KV - BUS 3 | PGCIL SR-2 | C | To conduct extended BUS 3 Stability Test | 2026-05-28 | 18:00 | 2026-05-29 | 02:00 |  | Yes | Approved | Remaining all elements shall be in service. | Bus | 16-May-2026 | 15:47 | 25-May-2026 | 10:13
RQ108952 | EMERGENCY | TGTRANSCO | 400KV/220KV SHANKARAPALLY-ICT-3 | TGTRANSCO | C | For attending hot line remarks at LV B-Ph dropping jumper clamp beside 2-8-89T isolator. | 2026-05-16 | 16:20 | 2026-05-16 | 19:30 | Please issue LC. | Yes | Approved |  | Transformer | 16-May-2026 | 16:17 | 16-May-2026 | 16:33
RQ108980 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | PID TESTING OF Porcelian disc insulator String | 2026-05-25 | 06:00 | 2026-05-25 | 18:00 | PID TESTING OF Porcelian disc insulator String | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 16-May-2026 | 19:24 | 22-May-2026 | 12:59
RQ108983 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | PID TESTING OF Porcelian disc insulator String | 2026-05-28 | 06:00 | 2026-05-28 | 18:00 | PID TESTING OF Porcelian disc insulator String | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 16-May-2026 | 19:24 | 25-May-2026 | 10:13
RQ108988 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | PID TESTING OF Porcelian disc insulator String | 2026-05-25 | 06:00 | 2026-05-25 | 18:00 | PID TESTING OF Porcelian disc insulator String | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 16-May-2026 | 19:27 | 22-May-2026 | 12:59
RQ108991 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | PID TESTING OF Porcelian disc insulator String | 2026-05-28 | 06:00 | 2026-05-28 | 18:00 | PID TESTING OF Porcelian disc insulator String | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 16-May-2026 | 19:27 | 25-May-2026 | 10:13
RQ109005 | PNOCC | PGCIL SR-1 | 400KV/220KV MEHBOOBNAGAR-ICT-2 | TGTRANSCO | D | As per OCC 237 S/D originally approved on 10.05.2026 . Due to site constraints , it is requested to postpone S/D on 25.05.2026 .Kindly approve | 2026-05-25 | 08:00 | 2026-05-25 | 13:30 | As per OCC 237 S/D originally approved on 10.05.2026 . Due to site constraints , it is requested to postpone S/D on 25.05.2026 .Kindly approve | Yes | Approved | PGCIL SR-1 shall avail the shutdown in Morning hours. As per telephonic communication, TELANGANA confirmed to facilitate in the Morning hours itself. N-1 limit for MEHBOOBNAGAR-ICTs is 226 MW for 315 MVA ICT each and 358 MW for 500 MVA ICT each. 400KV/220KV MEHBOOBNAGAR-ICT-1 31% 400KV/220KV MEHBOOBNAGAR-ICT-4 31% 400KV/220KV MEHBOOBNAGAR-ICT-3 20% All DINDI ICTs shall be in service. | Transformer | 17-May-2026 | 14:53 | 22-May-2026 | 14:59
RQ109006 | PNOCC | PGCIL SR-1 | MEHBOOBNAGAR - 400KV - BUS 2 | TGTRANSCO | C | As per OCC 237 S/D originally approved from 13.05.2026 to 14.05.2026 for Bay upgradation works uder ADDCAP- Construction works under SS-126 Package . Due to site constraints , it is requested to postpone S/D from 27.05.2026 to 28.05.2026 .Kindly approve | 2026-05-27 | 09:00 | 2026-05-28 | 18:00 | As per OCC 237 S/D originally approved from 13.05.2026 to 14.05.2026 for Bay upgradation works uder ADDCAP- Construction works under SS-126 Package . Due to site constraints , it is requested to postpone S/D from 27.05.2026 to 28.05.2026 .Kindly approve | Yes | Rejected | In case of contingency of other 400kV Bus at MEHBOOBNAGAR, tripping of 400kV-RTPS-MEHBOOBNAGAR will lead to N-1 limit violation of 400kV-RAICHUR_PG - RTPS D/C. | Bus | 17-May-2026 | 15:16 | 24-May-2026 | 11:40
RQ109014 | PNOCC | PGCIL SR-2 | A/R of 400KV-GUTTUR-HIRIYUR-1 | KPTCL | D | Auto to Non-Auto for online OPGW works | 2026-05-23 | 09:00 | 2026-05-23 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. All the necessary precautions need to be taken while work as already 400kV-KAIGA-GUTTUR is under outage due to tower collapse. | Auto Reclosure | 18-May-2026 | 12:40 | 21-May-2026 | 11:12
RQ109017 | PNOCC | PGCIL SR-2 | A/R of 400KV-GUTTUR-HIRIYUR-2 | KPTCL | D | Auto to Non-Auto for online OPGW works | 2026-05-23 | 09:00 | 2026-05-23 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. All the necessary precautions need to be taken while work as already 400kV-KAIGA-GUTTUR is under outage due to tower collapse. | Auto Reclosure | 18-May-2026 | 12:40 | 21-May-2026 | 11:12
RQ109019 | PNOCC | PGCIL SR-2 | A/R of 400KV-GUTTUR-HIRIYUR-1 | KPTCL | D | Auto to Non-Auto for online OPGW works | 2026-05-25 | 09:00 | 2026-05-25 | 18:00 |  | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 18-May-2026 | 12:42 | 22-May-2026 | 10:42
RQ109020 | PNOCC | PGCIL SR-2 | A/R of 400KV-GUTTUR-HIRIYUR-2 | KPTCL | D | Auto to Non-Auto for online OPGW works | 2026-05-25 | 09:00 | 2026-05-25 | 18:00 |  | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 18-May-2026 | 12:42 | 22-May-2026 | 10:42
RQ109059 | EMERGENCY | NTPC | 400KV-KUDGI_PG-KUDGI_NTPC-1 | KTL | C | LINE 1 R phase isolator miss alligned | 2026-05-18 | 16:38 | 2026-05-18 | 18:00 | emergency | Yes | Approved |  | Line Circuits | 18-May-2026 | 16:45 | 18-May-2026 | 17:24
RQ109060 | EMERGENCY | NTPC | 400KV-KUDGI_PG-KUDGI_NTPC-4 | KTL | C | LINE 1 R phase isolator miss alligned | 2026-05-18 | 18:38 | 2026-05-18 | 20:00 | emergency | Yes | Approved |  | Line Circuits | 18-May-2026 | 16:45 | 18-May-2026 | 17:24
RQ109073 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-GAJWEL-1 | POWERGRID | D | PID Scanning of porcelain insulators. | 2026-05-28 | 06:00 | 2026-05-28 | 18:00 | PID Scanning of porcelain insulators. | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 18-May-2026 | 17:53 | 25-May-2026 | 10:13
RQ109076 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-GAJWEL-1 | POWERGRID | D | PID Scanning of porcelain insulators. | 2026-05-31 | 06:00 | 2026-05-31 | 18:00 | PID Scanning of porcelain insulators. | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 18-May-2026 | 17:53 | 28-May-2026 | 10:33
RQ109083 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-NAGARJUNASAGAR_PG-1 | POWERGRID | D | PID Scanning of porcelain insulators. | 2026-05-28 | 06:00 | 2026-05-28 | 18:00 | PID Scanning of porcelain insulators. | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 18-May-2026 | 17:53 | 25-May-2026 | 10:13
RQ109086 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-NAGARJUNASAGAR_PG-1 | POWERGRID | D | PID Scanning of porcelain insulators. | 2026-05-31 | 06:00 | 2026-05-31 | 18:00 | PID Scanning of porcelain insulators. | Yes | Approved | Subject to revival of 400kV-NAGARJUNASAGAR BUS-1 expected on 30.05.2026. | Auto Reclosure | 18-May-2026 | 17:53 | 28-May-2026 | 10:33
RQ109087 | PNOCC | kptcl | A/R of 220KV-TUMKUR-KIADB-VNPURA-1 | KPTCL | D | For OPGW stringing work | 2026-05-22 | 06:00 | 2026-05-22 | 18:00 |  | Yes | Rejected | May be availed after revival of 400kV-PAVAGDA-TUMKUR D/C. | Auto Reclosure | 18-May-2026 | 21:56 | 19-May-2026 | 14:55
RQ109088 | PNOCC | kptcl | A/R of 220KV-TUMKUR-KIADB-VNPURA-1 | KPTCL | D | For OPGW stringing work | 2026-05-23 | 06:00 | 2026-05-23 | 18:00 |  | Yes | Rejected | May be availed after revival of 400kV-PAVAGDA-TUMKUR D/C. | Auto Reclosure | 18-May-2026 | 21:56 | 20-May-2026 | 11:18
RQ109093 | PNOCC | kptcl | A/R of 220KV-TUMKUR-KIADB-VNPURA-1 | KPTCL | D | For OPGW stringing work | 2026-05-28 | 06:00 | 2026-05-28 | 18:00 |  | Yes | Rejected | May be availed after the revival of 400kV-PAVAGDA-TUMKUR D/C. | Auto Reclosure | 18-May-2026 | 21:56 | 25-May-2026 | 10:13
RQ109095 | PNOCC | kptcl | A/R of 220KV-TUMKUR-KIADB-VNPURA-1 | KPTCL | D | For OPGW stringing work | 2026-05-30 | 06:00 | 2026-05-30 | 18:00 |  | Yes | Rejected | May be availed after revival of 400kV-PAVAGADA-TUMKUR D/C. | Auto Reclosure | 18-May-2026 | 21:56 | 27-May-2026 | 11:13
RQ109096 | PNOCC | kptcl | A/R of 220KV-TUMKUR-MADHUGIRI-1 | KPTCL | D | For OPGW stringing work | 2026-05-22 | 06:00 | 2026-05-22 | 18:00 |  | Yes | Rejected | May be availed after revival of 400kV-PAVAGDA-TUMKUR D/C. | Auto Reclosure | 18-May-2026 | 21:56 | 19-May-2026 | 14:55
RQ109097 | PNOCC | kptcl | A/R of 220KV-TUMKUR-MADHUGIRI-1 | KPTCL | D | For OPGW stringing work | 2026-05-23 | 06:00 | 2026-05-23 | 18:00 |  | Yes | Rejected | May be availed after revival of 400kV-PAVAGDA-TUMKUR D/C. | Auto Reclosure | 18-May-2026 | 21:56 | 20-May-2026 | 11:18
RQ109102 | PNOCC | kptcl | A/R of 220KV-TUMKUR-MADHUGIRI-1 | KPTCL | D | For OPGW stringing work | 2026-05-28 | 06:00 | 2026-05-28 | 18:00 |  | Yes | Rejected | May be availed after the revival of 400kV-PAVAGDA-TUMKUR D/C. | Auto Reclosure | 18-May-2026 | 21:56 | 25-May-2026 | 10:13
RQ109104 | PNOCC | kptcl | A/R of 220KV-TUMKUR-MADHUGIRI-1 | KPTCL | D | For OPGW stringing work | 2026-05-30 | 06:00 | 2026-05-30 | 18:00 |  | Yes | Rejected | May be availed after revival of 400kV-PAVAGADA-TUMKUR D/C. | Auto Reclosure | 18-May-2026 | 21:56 | 27-May-2026 | 11:13
RQ109105 | PNOCC | kptcl | A/R of 220KV-TUMKUR-MADHUGIRI-2 | KPTCL | D | For OPGW stringing work | 2026-05-22 | 06:00 | 2026-05-22 | 18:00 |  | Yes | Rejected | May be availed after revival of 400kV-PAVAGDA-TUMKUR D/C. | Auto Reclosure | 18-May-2026 | 21:56 | 19-May-2026 | 14:55
RQ109106 | PNOCC | kptcl | A/R of 220KV-TUMKUR-MADHUGIRI-2 | KPTCL | D | For OPGW stringing work | 2026-05-23 | 06:00 | 2026-05-23 | 18:00 |  | Yes | Rejected | May be availed after revival of 400kV-PAVAGDA-TUMKUR D/C. | Auto Reclosure | 18-May-2026 | 21:56 | 20-May-2026 | 11:18
RQ109111 | PNOCC | kptcl | A/R of 220KV-TUMKUR-MADHUGIRI-2 | KPTCL | D | For OPGW stringing work | 2026-05-28 | 06:00 | 2026-05-28 | 18:00 |  | Yes | Rejected | May be availed after the revival of 400kV-PAVAGDA-TUMKUR D/C. | Auto Reclosure | 18-May-2026 | 21:56 | 25-May-2026 | 10:13
RQ109113 | PNOCC | kptcl | A/R of 220KV-TUMKUR-MADHUGIRI-2 | KPTCL | D | For OPGW stringing work | 2026-05-30 | 06:00 | 2026-05-30 | 18:00 |  | Yes | Rejected | May be availed after revival of 400kV-PAVAGADA-TUMKUR D/C. | Auto Reclosure | 18-May-2026 | 21:56 | 27-May-2026 | 11:13
RQ109115 | PNOCC | PGCIL SR-2 | 400KV-GADAG_PSS-KOPPAL-1 | GADAG_II_A | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 11/0 - 12/0. | 2026-05-23 | 08:00 | 2026-05-23 | 19:00 | Approved under OCC_2371 on 19.05.2026. Rescheduling due to pendency of pre-shutdown preparatory works because of continuous rains at site. TSP/IPP concurrences will be submitted on D-2 basis. Kindly approve. | Yes | Rejected | Deferred by PGCIL-SR2. KNTL concurrence also need to be submitted for not availing the 220kV-BUS-4 shutdown at KOPPAL for the same date. PGCIL SR-2 submitted the RE developer concurrence through mail dated 21-05-2026. 400kV-KUDGI_PG - KOPPAL D/C 50% 400kV-KUDGI_PG - GADAG D/C each shall be in service. Subject to real time RE generation and line loadings. Subject to adherence of proper RE schedules. | Line Circuits | 18-May-2026 | 23:21 | 20-May-2026 | 23:10
RQ109131 | PNOCC | PGCIL SR-2 | 400KV/220KV TRIVANDRUM-ICT-1 | PGCIL SR-2 | C | AMP works | 2026-05-23 | 09:00 | 2026-05-23 | 17:00 | Shutdown was scheduled for 16.05.2026 in OCC-237 but got rejected due to multiple shutdowns in KSEB system | Yes | Approved | Load Management need to be done by KSEB. N-1 limit for TRIVANDRUM ICTs is 219 MW each. Subject to revival of KSEB shutdowns of 220kV-POTHENCOE-TRIVANDRUM 220kV-EDAMON-POTHENCODE and 220kV-TRIVANDRUM - NEW KATAKADA. The same need to be confirmed from KSEB prior to the shutdown. 400KV/220KV TRIVANDRUM-ICT-2,3 37% each All TIRUNELVELI ICTs 220KV-EDAMON-TIRUNELVELI D/C 8% each 400KV-KOTTAYAM-TIRUNELVELI D/C shall be in service. | Transformer | 19-May-2026 | 12:28 | 21-May-2026 | 10:48
RQ109148 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-24 | 06:00 | 2026-05-24 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 19-May-2026 | 16:49 | 21-May-2026 | 10:07
RQ109149 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-25 | 06:00 | 2026-05-25 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 19-May-2026 | 16:49 | 22-May-2026 | 10:42
RQ109150 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-26 | 06:00 | 2026-05-26 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 19-May-2026 | 16:49 | 23-May-2026 | 16:29
RQ109154 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-30 | 06:00 | 2026-05-30 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 19-May-2026 | 16:49 | 27-May-2026 | 11:12
RQ109157 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-24 | 06:00 | 2026-05-24 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 19-May-2026 | 16:49 | 21-May-2026 | 10:07
RQ109158 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-25 | 06:00 | 2026-05-25 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 19-May-2026 | 16:49 | 22-May-2026 | 10:42
RQ109159 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-26 | 06:00 | 2026-05-26 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 19-May-2026 | 16:49 | 23-May-2026 | 16:29
RQ109163 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-30 | 06:00 | 2026-05-30 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 19-May-2026 | 16:49 | 27-May-2026 | 11:12
RQ109169 | PNOCC | WKTL | MAIN BAY (424) OF 400KV/220KV KUDGI_PG-ICT-4 AND KUDGI_PG - 400KV - BUS 2 @KUDGI_PG - 400KV | KTL | C | Extension/Interconnection of400kv Main Bus-2 from existing PGCIL Kudgi to WRSR New Narendra. | 2026-05-26 | 09:00 | 2026-05-28 | 23:59 | Outage required from 25.05.2026 09:00Hrs to 30.05.2026 18:00Hrs on continous basis for protection wiring purpose(There will be no availability loss due to the same & now both are ideally charged as ICTS are not charged). | Yes | Approved | CEA safety approval submitted. Remaining bays shall be in service. ICT-4 is a future element. | Bay | 19-May-2026 | 17:17 | 22-May-2026 | 13:54
RQ109171 | PNOCC | PGCIL SR-2 | MAIN BAY (401) OF 400KV-KARAIKUDI-TRICHY-1 AND KARAIKUDI - 400KV - BUS 1 @KARAIKUDI - 400KV | PGCIL SR-2 | D | BAY AMP | 2026-05-25 | 09:30 | 2026-05-25 | 17:30 | pl approve | Yes | Approved | Remaining bays shall be in service. | Bay | 19-May-2026 | 19:00 | 22-May-2026 | 12:42
RQ109174 | PNOCC | PGCIL SR-2 | MAIN BAY (422) OF 400KV-PAVAGADA_PG-BPS-2 AND PAVAGADA_PG - 400KV - BUS 1 @PAVAGADA_PG - 400KV | PGCIL SR-2 | D | FOR BAY AMP WORKS | 2026-05-25 | 10:00 | 2026-05-25 | 17:00 | pl approve | Yes | Rejected | Multiple shutdowns at the same station. | Bay | 19-May-2026 | 19:05 | 22-May-2026 | 12:42
RQ109184 | PNOCC | PGCIL SR-1 | 400KV-CUDDAPAH-CHITTOOR-1 | POWERGRID | D | 400kV Ananthapuram-Kadapa D/c line construction works for OPGW diamond crossing works at locations AP77 and AP78 | 2026-05-25 | 08:00 | 2026-05-25 | 14:00 | Construction-Line over crossing works | Yes | Approved | 400kV-CUDDAPAH-N P KUNTA-2,3 19% each 400kV-KOLAR- N P KUNTA 15% each 400kV-CHITTOOR-THIRUVALLAM D/C 15% each 765kV-CUDDAPAH-THIRUVALLAM D/C 400kV-CHITTOOR-RACHAGUNNERI D/C 10% each 400kV-KRISHNAPATTNAM-RACHAGUNNERI D/C 8% each 400kV-KOLAR-SRIPERUBUDUR 8% All 765kV/400kV THIRUVALLAM ICTs All 400kV/220kV CUDDAPAH ICTs shall be in service. | Line Circuits | 20-May-2026 | 10:47 | 22-May-2026 | 15:11
RQ109185 | PNOCC | PGCIL SR-1 | 400KV-CUDDAPAH-NP_KUNTA-1 | POWERGRID | D | 400kV Ananthapuram-Kadapa D/c line construction works for OPGW diamond crossing works at locations AP77 and AP78 | 2026-05-25 | 08:00 | 2026-05-25 | 14:00 | Construction-Line over crossing works | Yes | Approved | 400kV-CUDDAPAH-N P KUNTA-2,3 19% each 400kV-KOLAR- N P KUNTA 15% each 400kV-CHITTOOR-THIRUVALLAM D/C 15% each 765kV-CUDDAPAH-THIRUVALLAM D/C 400kV-CHITTOOR-RACHAGUNNERI D/C 10% each 400kV-KRISHNAPATTNAM-RACHAGUNNERI D/C 8% each 400kV-KOLAR-SRIPERUBUDUR 8% All 765kV/400kV THIRUVALLAM ICTs All 400kV/220kV CUDDAPAH ICTs shall be in service. | Line Circuits | 20-May-2026 | 10:51 | 22-May-2026 | 15:11
RQ109198 | EMERGENCY | TGTRANSCO | 400KV/11.5KV YADADRI TPP-ST-2 | TGGENCO,TGTRANSCO | C | Please issue opening code of 135 MVA ST-2(BAY-433)for attending painting work. | 2026-05-20 | 13:45 | 2026-05-21 | 23:59 | Already bay 431(GT-4)&Tie bay 432 are under LC and station supply is feeding from ST-3,Now ST-2 is idle charged condition. | Yes | Approved | Load Management need to be done by TG. Further any planned activities to be taken into Main OCC. | Transformer | 20-May-2026 | 13:36 | 21-May-2026 | 11:27
RQ109199 | PNOCC | kptcl | 220KV-CHIKKODI-TALANGADE | KPTCL,MAHATRANSCO | C | Regarding issue of tripping on 220KV Chikodi-Talandage line at 220KV R/S Chikodi-Belagavi RT staff has informed for testing of AR scheme. | 2026-05-25 | 10:00 | 2026-05-25 | 18:00 | 220KV Talanadage line has initially AR operated and after 500msec line has tripped as informed by RT Belagavi staff, and it is necessary to check the AR scheme of the same line. | Yes | Rejected | NLDC deferred the shutdown with the reason "Not approved in WRPC" | Line Circuits | 20-May-2026 | 13:44 | 22-May-2026 | 12:59
RQ109203 | EMERGENCY | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-1 | PVG_IRCON_S | C | JSW Site Jumper Work | 2026-05-21 | 19:00 | 2026-05-21 | 23:59 |  | Yes | Approved |  | Line Circuits | 20-May-2026 | 17:01 | 21-May-2026 | 20:12
RQ109204 | EMERGENCY | PVG_IRCON_S | 220KV-PAVAGADA_PG-IRCON_PVG_S-2 | PVG_IRCON_S | C | JSW Site Jumper Work | 2026-05-21 | 19:00 | 2026-05-21 | 23:59 |  | Yes | Approved |  | Line Circuits | 20-May-2026 | 17:01 | 21-May-2026 | 20:12
RQ109226 | EMERGENCY | aptransco | 400KV-KALPAKKA-VEMAGIRI_AP-1 | APTRANSCO | C | For attending redhot rectification on jumper at Loc No: 48 (DB+0, B-PH) in 400KV Kalapaka- Vemagiri line. During night time on 20-05-26 hotspots observed at Loc No: 48 (DB+0, B-PH) on 400KV Kalapaka- Vemagiri line. Hence emergency line clear requested on 400KV Kalapaka- Vemagiri line On emergency line clear | 2026-05-21 | 07:43 | 2026-05-21 | 09:43 |  | Yes | Approved | All other lines connected to Vemagiri shall be in service. | Line Circuits | 21-May-2026 | 07:44 | 21-May-2026 | 08:25
RQ109227 | EMERGENCY | NTPC | 400KV/220KV RAMAGUNDAM-ICT-4 | NTPC | C | for line equipment testing | 2026-05-21 | 07:58 | 2026-05-21 | 17:30 | connected line is under shutdown - occ approved | Yes | Approved |  | Transformer | 21-May-2026 | 08:01 | 21-May-2026 | 08:42
RQ109229 | EMERGENCY | NTPC | 400KV/220KV RAMAGUNDAM-ICT-2 | NTPC | C | for line eqpt testing | 2026-05-21 | 08:18 | 2026-05-21 | 17:18 | connected line in under approved shutdown | Yes | Approved |  | Transformer | 21-May-2026 | 08:20 | 21-May-2026 | 20:16
RQ109235 | EMERGENCY | TGTRANSCO | MAIN BAY (412) OF 400KV/220KV GAJWEL-ICT-2 AND GAJWEL - 400KV - BUS 2 @GAJWEL - 400KV | TGTRANSCO | C | To arrest air leakage from 4-12-52 pneumatic breaker to avoid breaker going to lockout condition. Emergency lc requested on 412 bay and there will be no interruption | 2026-05-21 | 11:30 | 2026-05-21 | 12:30 | Please approve LC | Yes | Approved | other stand by bay should be in-service | Bay | 21-May-2026 | 11:20 | 21-May-2026 | 11:32
RQ109237 | EMERGENCY | PGCIL SR-1 | VEMAGIRI_PG - 400KV - BUS 2 | PGCIL SR-1 | D | Vemagiri SS has reported the severe leak of hydraulic oil from its of 40652 CB GIS chamber. Due to this CB operation lockout will happen. To attend the same, shutdowns of 400kV Bus-2 & 400kV Vemagiri-Gajuwaka feeder are necessary. Request to approve the shutdowns from 14:30 to 18:00 hrs/21.05.2026. | 2026-05-21 | 14:30 | 2026-05-21 | 18:00 | Vemagiri SS has reported the severe leak of hydraulic oil from its of 40652 CB GIS chamber. Due to this CB operation lockout will happen. To attend the same, shutdowns of 400kV Bus-2 & 400kV Vemagiri-Gajuwaka feeder are necessary. Request to approve the shutdowns from 14:30 to 18:00 hrs/21.05.2026. | Yes | Approved |  | Bus | 21-May-2026 | 14:34 | 21-May-2026 | 15:36
RQ109238 | EMERGENCY | PGCIL SR-1 | 400KV-GAZUWAKA-VEMAGIRI_PG-1 | POWERGRID | D | Vemagiri SS has reported the severe leak of hydraulic oil from its of 40652 CB GIS chamber. Due to this CB operation lockout will happen. To attend the same, shutdowns of 400kV Bus-2 & 400kV Vemagiri-Gajuwaka feeder are necessary. Request to approve the shutdowns from 14:30 to 18:00 hrs/21.05.2026. | 2026-05-21 | 14:36 | 2026-05-21 | 18:36 | Vemagiri SS has reported the severe leak of hydraulic oil from its of 40652 CB GIS chamber. Due to this CB operation lockout will happen. To attend the same, shutdowns of 400kV Bus-2 & 400kV Vemagiri-Gajuwaka feeder are necessary. Request to approve the shutdowns from 14:30 to 18:00 hrs/21.05.2026. | Yes | Approved |  | Line Circuits | 21-May-2026 | 14:37 | 21-May-2026 | 15:36
RQ109243 | EMERGENCY | NTPC | 400KV/220KV RAMAGUNDAM-ICT-3 | NTPC | C | for bay eqpt testing | 2026-05-22 | 08:00 | 2026-05-22 | 17:30 | connected line shutdowm is OCC approved | Yes | Approved | LV side is under shutdown. | Transformer | 21-May-2026 | 19:12 | 22-May-2026 | 10:25
RQ109254 | EMERGENCY | TGTRANSCO | 220KV-RAMAGUNDAM-MALYALAPALLI-1 | NTPC | C | To attend red hot on Bph Bus isolator-2 T jumper clamp | 2026-05-22 | 08:55 | 2026-05-22 | 18:55 | Please approve LC | Yes | Approved |  | Line Circuits | 22-May-2026 | 08:51 | 22-May-2026 | 10:07
RQ109256 | EMERGENCY | aptransco | 400KV/220KV NELLORE_AP-ICT-3 | APTRANSCO | C | for attending hotspot rectification on connected equipment. | 2026-05-22 | 10:45 | 2026-05-22 | 13:45 | no interruption | Yes | Approved | All other ICTs shall be in service. | Transformer | 22-May-2026 | 10:42 | 22-May-2026 | 11:20
RQ109257 | EMERGENCY | PGCIL SR-2 | BUS SECTIONALIZER BAY (425) OF KOLAR_AC - 400KV - BUS 1 AND KOLAR_AC - 400KV - BUS 3 @KOLAR_AC - 400KV | PGCIL SR-2 | C | Emergency shutdown required inspection of Black Spots observed on both Bay CTs of B-Ph | 2026-05-22 | 11:16 | 2026-05-22 | 13:16 | Bs- 426 will remain in service | Yes | Approved | approved on emergency. | Bay | 22-May-2026 | 11:20 | 22-May-2026 | 11:41
RQ109262 | EMERGENCY | aptransco | 400KV-NARNOOR-JAMMALAMADUGU-1 | APTRANSCO | C | For rectification of R-ph CVT jumper clamp | 2026-05-22 | 16:45 | 2026-05-22 | 19:45 |  | Yes | Approved |  | Line Circuits | 22-May-2026 | 16:48 | 22-May-2026 | 17:01
RQ109274 | PNOCC | PGCIL SR-2 | A/R of 220KV-RENEW_SURYA_OJAS_KOPPAL_W-KOPPAL-1 | RSOPL | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 13/0 - 14/0 by Hotline Method. | 2026-05-30 | 07:00 | 2026-05-30 | 19:00 | Line Shutdowns were approved under Mid OCC_2371. However, IPP has denied to consent citing, substantial financial implication due to expected generation loss during shutdown period. In view of the commissioning target of 400 kV Gadag II - Koppal II D/C Transmission line by Mid of June 2026 and commencement of monsoon rains in North Karnataka area, it is planned to take up the powerline crossing works by hotline method. | Yes | Approved | Concurrence from the concerned RE developers is submitted by PGCIL SR-2 for taking A/R into Non-Auto mode through mail communication dated 26.05.20206. Further, there is no N-1 redundancy available for the RE generating plants connected at 400kV KOPPAL PSS. Also, it is to be duly noted that the peak wind season in the Southern Region has already commenced, and multiple line tripping have been observed in nearby grid elements during the past few days. 400kV-KOPPAL-GADAG D/C is already under shutdown due to tower collapse. | Auto Reclosure | 22-May-2026 | 22:10 | 27-May-2026 | 11:12
RQ109281 | PNOCC | PGCIL SR-2 | A/R of 220KV-KOPPAL-RENEW_SURYA_KOPPAL-1 | RENEW POWER PVT LTD | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 13/0 - 14/0 by Hotline Method. | 2026-05-30 | 07:00 | 2026-05-30 | 19:00 | Line Shutdowns were approved under Mid OCC_2371. However, IPP has denied to consent citing, substantial financial implication due to expected generation loss during shutdown period. In view of the commissioning target of 400 kV Gadag II - Koppal II D/C Transmission line by Mid of June 2026 and commencement of monsoon rains in North Karnataka area, it is planned to take up the powerline crossing works by hotline method. | Yes | Approved | Concurrence from the concerned RE developers is submitted by PGCIL SR-2 for taking A/R into Non-Auto mode through mail communication dated 26.05.20206. Further, there is no N-1 redundancy available for the RE generating plants connected at 400kV KOPPAL PSS. Also, it is to be duly noted that the peak wind season in the Southern Region has already commenced, and multiple line tripping have been observed in nearby grid elements during the past few days. 400kV-KOPPAL-GADAG D/C is already under shutdown due to tower collapse. | Auto Reclosure | 22-May-2026 | 22:10 | 27-May-2026 | 11:12
RQ109285 | PNOCC | PGCIL SR-2 | 400KV-HOSUR_PG-KOLAR_AC-2 | POWERGRID | D | for AMP works. | 2026-05-27 | 09:00 | 2026-05-27 | 18:00 | Kolar-Hosur 2 SD was approved in 237th OCC for 07.05.2026. But the same was rejected by SRLDC citing "Severe Low voltages at Hosur End". | Yes | Rejected | Low voltages up to 380kV are still observed at HOSUR S/S. Shutdown may preferably be availed on weekend and after 12:00 HRS subject to no other overlapping shutdown and real time grid conditions. | Line Circuits | 23-May-2026 | 13:29 | 24-May-2026 | 11:40
RQ109286 | EMERGENCY | aptransco | 400KV/220KV JAMMALAMADUGU-ICT-1 | APTRANSCO | C | To removal of bird nest on 400/22OKV 315MVA ICT | 2026-05-23 | 15:30 | 2026-05-23 | 16:30 | no interruption | Yes | Approved | OTHER ICTS SHALL BE IN SERVICE. NO RE CURTAILMENT TO BE DONE. | Transformer | 23-May-2026 | 15:22 | 23-May-2026 | 15:49
RQ109291 | PNOCC | PGCIL SR-2 | A/R of 400KV-HOSUR_PG-KOLAR_AC-1 | POWERGRID | C | 400KV HOSUR - KOLAR is double circuit line, 400KV-HOSUR_PG-KOLAR_AC-2 Shutdown approved on 27.05.2026.. to work safe in 400KV-HOSUR_PG-KOLAR_AC-2 A/R DISABLE REQUIRED | 2026-05-27 | 09:00 | 2026-05-27 | 18:00 | 400KV HOSUR - KOLAR is double circuit line, 400KV-HOSUR_PG-KOLAR_AC-2 Shutdown approved on 27.05.2026.. to work safe in 400KV-HOSUR_PG-KOLAR_AC-2 A/R DISABLE REQUIRED | Yes | Rejected | Low voltages up to 380kV are still observed at HOSUR S/S. Shutdown may preferably be availed on weekend and after 12:00 HRS subject to no other overlapping shutdown and real time grid conditions. | Auto Reclosure | 23-May-2026 | 18:45 | 24-May-2026 | 11:40
RQ109298 | EMERGENCY | PGCIL SR-1 | 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | C | To remove foreign material | 2026-05-24 | 18:00 | 2026-05-24 | 20:00 |  | Yes | Approved |  | Line Circuits | 24-May-2026 | 18:02 | 24-May-2026 | 18:06
RQ109326 | PNOCC | PGCIL SR-2 | A/R of 400KV-NNTPP-PUDUCHERRY-1 | POWERGRID | D | PID scanning of complete line due to frequent failure of porcelain insulators | 2026-05-31 | 09:00 | 2026-05-31 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 25-May-2026 | 17:14 | 28-May-2026 | 10:33
RQ109335 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | PID TESTING OF 120 KN AND 160 KN Porcelain insulator String | 2026-05-31 | 08:00 | 2026-05-31 | 18:00 | PID TESTING OF 120 KN AND 160 KN Porcelain insulator String | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 25-May-2026 | 18:28 | 28-May-2026 | 10:33
RQ109337 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | For carrying PID scanning of 400kV Vijayawada-Vemagiri SC Line | 2026-05-31 | 08:00 | 2026-05-31 | 18:00 | For carrying PID scanning of 400kV Vijayawada-Vemagiri SC Line | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 25-May-2026 | 18:34 | 28-May-2026 | 10:33
RQ109344 | EMERGENCY | TGTRANSCO | 220KV-WARANGAL-BOMMAKAL-1 | TGTRANSCO | C | safety LC for removal of earth wire fallen on breakdown feeder 220kv ogulapur-huzurabad feeder | 2026-05-25 | 19:10 | 2026-05-25 | 21:00 | Please issue LC | Yes | Approved |  | Line Circuits | 25-May-2026 | 19:11 | 25-May-2026 | 19:19
RQ109374 | EMERGENCY | TANTRANSCO | 400KV-TIRUNELVELI-KANARPATTI-1 | TANTRANSCO | C | To replace of failed hardware fittings in B Phase at location no.2 of 400 KV Kanarpatti - Abisekapatti feeder 1 | 2026-05-26 | 18:00 | 2026-05-27 | 06:00 | 400 KV Supply will be fed through 400 KV Kayathar Feeder -1 & 2 .Hence no ss will be affected. | Yes | Approved | Line to be returned on time. | Line Circuits | 26-May-2026 | 16:44 | 26-May-2026 | 18:58
RQ109485 | PNOCC | TANTRANSCO | 400KV/110KV SRIPERUMBADUR_TN-ICT-5 | TANTRANSCO | D | To attend glow observed in LV 5 R phase breaker top clamp | 2026-05-31 | 06:00 | 2026-05-31 | 09:00 |  | Yes | Approved | Load Management need to be done by TN. N-1 limit for 400KV/110KV SRIPERUMBADUR_TN-ICTs is 144 MW each. Subject to ICT loadings within their N-1 limits. | Transformer | 27-May-2026 | 19:28 | 28-May-2026 | 10:35
RQ109500 | EMERGENCY | kptcl | 400KV-JINDAL-BPS-4 | KPTCL | C | for checking and replacement of the 400kV GIS Line #4 breaker trip coil and pole discrepancy operation timer. | 2026-05-28 | 08:00 | 2026-05-28 | 18:30 | for checking and replacement of the 400kV GIS Line #4 breaker trip coil and pole discrepancy operation timer. | Yes | Rejected |  | Line Circuits | 28-May-2026 | 07:53 | 28-May-2026 | 10:45
RQ109503 | EMERGENCY | kseb | 220KV-POTHENCODE-TRIVANDRUM-1 | KSEB | D | The optic fiber link from Trivandrum PGCIL to Trivandrum (Pothencode) KSEBL has been damaged due to arcing outside the Pothencode KSEBL substation gantry. Out of the total 24 fibers, around 10 fibers have been identified as faulty..For carrying out the fault rectification work, POWERGRID has requested live line permit for the four numbers of 220 kV lines from Trivandrum Powergrid Substation on 29th and 30th May 2026 . The probable fault location is assessed to be between the first and second towers from the Pothencode end.Since PNOCC window for 29.05.26 is already expired, live line permit of Trivandrum Pothencode 1,2,3 feeders and Trivandrum -New Kattakkada feeders are applied as emergency. | 2026-05-29 | 08:00 | 2026-05-29 | 17:00 | LIVE LINE PERMIT | Yes | Rejected | Only A/R need to be applied. | Auto Reclosure | 28-May-2026 | 11:31 | 29-May-2026 | 18:56
RQ109508 | EMERGENCY | kseb | 220KV-POTHENCODE-TRIVANDRUM-3 | KSEB | D | The optic fiber link from Trivandrum PGCIL to Trivandrum (Pothencode) KSEBL has been damaged due to arcing outside the Pothencode KSEBL substation gantry. Out of the total 24 fibers, around 10 fibers have been identified as faulty..For carrying out the fault rectification work, POWERGRID has requested live line permit for the four numbers of 220 kV lines from Trivandrum Powergrid Substation on 29th and 30th May 2026 . The probable fault location is assessed to be between the first and second towers from the Pothencode end.Since PNOCC window for 29.05.26 is already expired, live line permit of Trivandrum Pothencode 1,2,3 feeders and Trivandrum -New Kattakkada feeders are applied as emergency. | 2026-05-29 | 08:00 | 2026-05-29 | 17:00 | LIVE LINE WORK | Yes | Rejected | Only A/R need to be applied. | Auto Reclosure | 28-May-2026 | 11:59 | 29-May-2026 | 18:56
RQ109509 | EMERGENCY | PGCIL SR-1 | ANANTHPURAM - 400KV - BUS 2 | PGCIL SR-1 | C | M/S Renew bays commissioning works at Ananthapuram SS | 2026-05-29 | 14:00 | 2026-05-30 | 17:59 | M/S Renew bays commissioning works at Ananthapuram SS | Yes | Approved | No generation in down stream network | Bus | 28-May-2026 | 13:05 | 29-May-2026 | 14:06
RQ109538 | EMERGENCY | kseb | 220KV-KOCHI-KALAMASSERY-1 | KSEB | D | for carrying out emergency tree cutting works between location 34 & 35 | 2026-05-29 | 09:00 | 2026-05-29 | 13:00 | Load will be mananged by KSEBL | Yes | Approved | 220KV-KOCHI-KALAMASSERY-2, 220KV-IDUKKI-KALAMASSERY D/C shall be in service. Idukki generation may be increased to regulate flow on 220KV-KOCHI-KALAMASSERY-2. LGB management to be done by KSEB. | Line Circuits | 29-May-2026 | 01:02 | 29-May-2026 | 09:23
RQ109579 | EMERGENCY | PGCIL SR-2 | 400KV-PAVAGADA_PG-BPS-1 | POWERGRID | D | Hotspot is observed at Gantry Tower in Y-Ph of Pavagada-Gooty Line -2 at Pavagada SS. Also the feeder of 400KV-PAVAGADA_PG-BPS-1 is below the above mentioned Gooty feeder. Thus to attend the Hotspot safely , shutdown of 400KV-PAVAGADA_PG-BPS-1 is required. | 2026-05-29 | 14:00 | 2026-05-29 | 18:00 | pl approve | Yes | Approved | 400kV BPS-Pavagada-2 line shall be in service. | Line Circuits | 29-May-2026 | 12:26 | 29-May-2026 | 14:14
RQ109581 | EMERGENCY | PGCIL SR-2 | 400KV-GOOTY-PAVAGADA_PG-2 | POWERGRID | D | To attend Hotspot in Gantry Tower in Y-Ph of Pavagada-Gooty Line -2 at Pavagada SS. | 2026-05-29 | 14:00 | 2026-05-29 | 18:00 | pl approve | Yes | Approved | 400kV BPS-Pavagada-2 line shall be in service. | Line Circuits | 29-May-2026 | 12:30 | 29-May-2026 | 14:14
RQ109587 | EMERGENCY | kseb | A/R of 220KV-TRIVANDRUM-NEWKATAKADA-1 | KSEB | D | The optic fiber link from Trivandrum PGCIL to Trivandrum (Pothencode) KSEBL has been damaged due to arcing outside the Pothencode KSEBL substation gantry. Out of the total 24 fibers, around 10 fibers have been identified as faulty.Since the feeder is an ISTS line and the optic fiber network is being extensively utilized by KSEBL, ULDC, as well as PowerTel, immediate rectification of the damaged fiber is highly essential to restore reliable communication connectivity.For carrying out the fault rectification work, POWERGRID has requested live line permit for the four numbers of 220 kV lines from Trivandrum Powergrid Substation on 29th and 30th May 2026 vide Email dtd 26.05.26 . The probable fault location is assessed to be between the first and second towers from the Pothencode end.Since PNOCC window for 29.05.26 is already expired, live line permit of Trivandrum Pothencode 1,2,3 feeders and Trivandrum -New Kattakkada feeders are applied as emergency. Also on 30th shutdown of Trivandrum Pothencode 1 feeder is applied instead of live line permit and Trivandrum -New Kattakkada feeder was not integrated Trivandrum Pothencode 4 feeder was applied. In order to correct the mistake same will be be applied in emergency . Kindly concur the live line permit of Trivandrum Pothencode 1,2,3 feeders and Trivandrum -New Kattakkada feeders on 29.05.26 & 30.05.26. | 2026-05-30 | 08:00 | 2026-05-30 | 17:00 | LIVE LINE PERMIT | Yes | Approved | Concurred, subject to real time grid conditions. Load Management need to be done by KSEB in case of any contingency. | Auto Reclosure | 29-May-2026 | 12:49 | 29-May-2026 | 18:56
RQ109588 | EMERGENCY | kseb | A/R of 220KV-POTHENCODE-TRIVANDRUM-1 | KSEB | D | The optic fiber link from Trivandrum PGCIL to Trivandrum (Pothencode) KSEBL has been damaged due to arcing outside the Pothencode KSEBL substation gantry. Out of the total 24 fibers, around 10 fibers have been identified as faulty.Since the feeder is an ISTS line and the optic fiber network is being extensively utilized by KSEBL, ULDC, as well as PowerTel, immediate rectification of the damaged fiber is highly essential to restore reliable communication connectivity.For carrying out the fault rectification work, POWERGRID has requested live line permit for the four numbers of 220 kV lines from Trivandrum Powergrid Substation on 29th and 30th May 2026. The probable fault location is assessed to be between the first and second towers from the Pothencode endSince PNOCC window for 29.05.26 is already expired, live line permit of Trivandrum Pothencode 1,2,3 feeders and Trivandrum -New Kattakkada feeders are applied as emergency. Also on 30th shutdown of Trivandrum Pothencode 1 feeder is applied instead of live line permit and Trivandrum -New Kattakkada feeder was not integrated Trivandrum Pothencode 4 feeder was applied. In order to correct the mistake same will be be applied in emergency . Kindly concur the live line permit of Trivandrum Pothencode 1,2,3 feeders and Trivandrum -New Kattakkada feeders on 29.05.26 & 30.05.26. . | 2026-05-30 | 08:00 | 2026-05-30 | 17:00 | LIVE LINE PERMIT | Yes | Approved | Concurred, subject to real time grid conditions. Load Management need to be done by KSEB in case of any contingency. | Auto Reclosure | 29-May-2026 | 13:00 | 29-May-2026 | 18:56
RQ109591 | EMERGENCY | aptransco | 400KV-SIMHADRI-KALPAKKA-4 | APTRANSCO | D | For replacement of opened jumper T Loc 4 | 2026-05-29 | 13:40 | 2026-05-29 | 16:30 |  | Yes | Approved |  | Line Circuits | 29-May-2026 | 13:28 | 29-May-2026 | 13:47
RQ109680 | EMERGENCY | CEPL | 400KV-CEPL-TUTICORIN_PS-2 | COASTAL | D | In Tower Location No:1 one number Y Phase suspension insulator got broken and hanging , shutdown required to replace the same | 2026-05-30 | 07:30 | 2026-05-30 | 17:00 | Nil | Yes | Approved |  | Line Circuits | 30-May-2026 | 05:42 | 30-May-2026 | 06:41
RQ109681 | EMERGENCY | CEPL | A/R of 400KV-CEPL-TUTICORIN_PS-1 | COASTAL | D | Due to Line #2 shutdown auto recloser to be put at non auto mode | 2026-05-30 | 07:30 | 2026-05-30 | 17:00 | Nil | Yes | Approved |  | Auto Reclosure | 30-May-2026 | 05:45 | 30-May-2026 | 06:41
RQ109682 | EMERGENCY | aptransco | 400KV-GUDDIGUDEM-HINDUJA-2 | APTRANSCO | C | for increasing jumper clearance with respect to Tower of bottom conductor at Loc. 524 | 2026-05-30 | 08:00 | 2026-05-30 | 12:00 | the bottom conductor jumper during heavy gale condition comes into the vicinity of induction zone due to swing towards the Tower | Yes | Approved | At Hinduja S/S, Guddigudm-1, Kalpakka D/C shall be in service. | Line Circuits | 30-May-2026 | 07:31 | 30-May-2026 | 08:07
RQ109699 | EMERGENCY | kptcl | 400KV/220KV NELAMANGALA-ICT-2 | KPTCL | C | to attend female contact in isolator issue | 2026-05-30 | 10:45 | 2026-05-30 | 16:00 | emergency | Yes | Approved | ICT-1,3 each has 27% sensitivity and these shall be in service. Load management to be done by KPTCL. | Transformer | 30-May-2026 | 10:34 | 30-May-2026 | 11:19
RQ109749 | EMERGENCY | aptransco | 220KV-KOTHAGUDEM_TPS-TIRUVURU-1 | APTRANSCO | D | To rectify Red hot rectification in Y-ph at Loc.227(C.P) near Vallampatla village in NTR Dist | 2026-05-30 | 13:40 | 2026-05-30 | 16:40 | alternate to Tiruvuru available | Yes | Approved |  | Line Circuits | 30-May-2026 | 13:38 | 30-May-2026 | 14:07
RQ109750 | EMERGENCY | aptransco | TIE BAY (417) OF 400KV-VEMAGIRI_AP-SATTENPALLY-2 AND 400KV-VEMAGIRI_AP-KV_KOTA-2 @VEMAGIRI_AP - 400KV | APTRANSCO | D | air leak on the B-Phase of air chamber of C.B | 2026-05-30 | 14:00 | 2026-05-30 | 16:00 | without interruption | Yes | Approved |  | Bay | 30-May-2026 | 13:56 | 30-May-2026 | 14:08
RQ109754 | EMERGENCY | HIRIYUR_ZREPL | 220KV-HIRIYUR-ZENATARIS_PSS-1 | HIRIYUR_ZREPL | C | Rectification of pilot insulator removed in 220KV line Tower No-81 | 2026-05-31 | 16:00 | 2026-05-31 | 18:00 |  | Yes | Approved |  | Line Circuits | 30-May-2026 | 15:24 | 31-May-2026 | 15:43
RQ109757 | EMERGENCY | AMGEPL_Kurnool | 400KV/33KV AMGEPL_SOLAR-ICT-3 | AMGEPL | C | FOR ATTEND HOTSPOT RECTIFICATION WORK IN PTR-3 Y-PH LV BUSHING | 2026-05-30 | 19:00 | 2026-05-31 | 06:00 |  | Yes | Approved | No generation shall be effected | Transformer | 30-May-2026 | 15:54 | 30-May-2026 | 17:23
RQ107651 | PNOCC | TGTRANSCO | 220KV-WARANGAL-NAGARAM-2 | TGTRANSCO | C | Overhead stringing of power conductor between location No.22-23 of new 220KV DC line from existing 220KV SS Pulukurthy to proposed 220KV Kakatiya Mega textile park | 2026-05-02 | 08:00 | 2026-05-03 | 00:00 | Please approve L.C. | Yes | Approved | Load Management need to be done by TG as per the submitted details which are as follows: 1) the below lines may load about 150-180 MW/ckt during above shutdown. a) 220kV KTPP-Pulakurthy-S/C, 220kV KTPP-Salivagu-Pulakurthy S/C b) 220kV Nagaram-Warangal-D/C c) 220kV Buddiampadu-Mahbubabad-D/C d) 2x100 MVA Ammavaripet PTRs e) 220kV Oglapur-Huzurabad-S/C 2) During shutdown, following diversions may be planned to contain N-1. a) 132kV Narsampet SS (45 MW) may be fed radially from 220kV Mahabubabad (via 132kV Gudur). b) 132kV Geesukonda(55-60 MW), 132kV Wardhannapet(45 MW) will be fed radially from 220kV Ammavaripet SS. c) 132kV Warangal-Geeskonda-S/C may be kept open. d) 132kV Nekkonda-Wardhannapet-D/C may be kept open. e) 132kV Ammavaripet-Inavole-/DC may be fed from 220kV Waddekothapally(via 132kV Palakurthy) f) If required 132KV Nekkonda-Geesukonda may be kept Open g) If required based on power flows, 132kV Husnabad-Mnakondur-D/C and 220kV Huzurbabad-Durshed-S/C may be kept open to limit loading on 220kV Oglapur-Huzurabad(limit to 150-160 MW only). The same need to be coordinated and followed by TG subject to real time grid conditions. The same shutdown is having following sensitivities: 1. 400kV-BHOOPALAPALLY-WARANGAL D/C 24% each 2. 400kV-KHAMMAM-WARANGAL 8% 3. 400kV/220kV BHOOPALAPALLY ICT-1,2 25% each TG need to manage the BHOOPALAPALLY (KAKATIYA) generation prior to the shutdown in order to keep the downstream 220kV line loadings within their N-1 limit. Prior to the shutdown, KAKATIYA generation has -1% sensitivity on each line of 220kV-WARANGAL-NAGARAM D/C. Remaining all other 220kV lines at NAGARAM and WARANGAL need to be in service during the shutdown. | Line Circuits | 26-Apr-2026 | 18:33 | 29-Apr-2026 | 11:07
RQ107652 | PNOCC | TGTRANSCO | 220KV-WARANGAL-NAGARAM-1 | TGTRANSCO | C | Overhead stringing of power conductor between location No.22-23 of new 220KV DC line from existing 220KV SS Pulukurthy to proposed 220KV Kakatiya Mega textile park | 2026-05-02 | 08:00 | 2026-05-03 | 18:00 | Please approve L.C. | Yes | Approved | Load Management need to be done by TG as per the submitted details which are as follows: 1) the below lines may load about 150-180 MW/ckt during above shutdown. a) 220kV KTPP-Pulakurthy-S/C, 220kV KTPP-Salivagu-Pulakurthy S/C b) 220kV Nagaram-Warangal-D/C c) 220kV Buddiampadu-Mahbubabad-D/C d) 2x100 MVA Ammavaripet PTRs e) 220kV Oglapur-Huzurabad-S/C 2) During shutdown, following diversions may be planned to contain N-1. a) 132kV Narsampet SS (45 MW) may be fed radially from 220kV Mahabubabad (via 132kV Gudur). b) 132kV Geesukonda(55-60 MW), 132kV Wardhannapet(45 MW) will be fed radially from 220kV Ammavaripet SS. c) 132kV Warangal-Geeskonda-S/C may be kept open. d) 132kV Nekkonda-Wardhannapet-D/C may be kept open. e) 132kV Ammavaripet-Inavole-/DC may be fed from 220kV Waddekothapally(via 132kV Palakurthy) f) If required 132KV Nekkonda-Geesukonda may be kept Open g) If required based on power flows, 132kV Husnabad-Mnakondur-D/C and 220kV Huzurbabad-Durshed-S/C may be kept open to limit loading on 220kV Oglapur-Huzurabad(limit to 150-160 MW only). The same need to be coordinated and followed by TG subject to real time grid conditions. The same shutdown is having following sensitivities: 1. 400kV-BHOOPALAPALLY-WARANGAL D/C 24% each 2. 400kV-KHAMMAM-WARANGAL 8% 3. 400kV/220kV BHOOPALAPALLY ICT-1,2 25% each TG need to manage the BHOOPALAPALLY (KAKATIYA) generation prior to the shutdown in order to keep the downstream 220kV line loadings within their N-1 limit. Prior to the shutdown, KAKATIYA generation has -1% sensitivity on each line of 220kV-WARANGAL-NAGARAM D/C. Remaining all other 220kV lines at NAGARAM and WARANGAL need to be in service during the shutdown. | Line Circuits | 26-Apr-2026 | 18:38 | 29-Apr-2026 | 11:07
RQ107659 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-3 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-01 | 07:00 | 2026-05-01 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 16:10 | 29-Apr-2026 | 09:28
RQ107660 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-3 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-02 | 07:00 | 2026-05-02 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 16:10 | 29-Apr-2026 | 11:01
RQ107661 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-3 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-03 | 07:00 | 2026-05-03 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 16:10 | 30-Apr-2026 | 10:33
RQ107665 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-3 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-07 | 07:00 | 2026-05-07 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 16:10 | 04-May-2026 | 12:28
RQ107669 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-4 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-01 | 07:00 | 2026-05-01 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 16:10 | 29-Apr-2026 | 09:28
RQ107670 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-4 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-02 | 07:00 | 2026-05-02 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 16:10 | 29-Apr-2026 | 11:01
RQ107671 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-4 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-03 | 07:00 | 2026-05-03 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 16:10 | 30-Apr-2026 | 10:33
RQ107675 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-4 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-07 | 07:00 | 2026-05-07 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 16:10 | 04-May-2026 | 12:28
RQ107702 | PNOCC | PGCIL SR-1 | MAIN BAY (407) OF NP_KUNTA - 400KV B/R 1 AND NP_KUNTA - 400KV - BUS 1 @NP_KUNTA - 400KV | PGCIL SR-1 | D | For attending Bay maintenance work. | 2026-05-01 | 06:30 | 2026-05-01 | 16:30 | For attending Bay AMP works. | Yes | Approved | Remaining bays shall be in service. | Bay | 27-Apr-2026 | 17:59 | 29-Apr-2026 | 09:28
RQ107706 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-01 | 08:00 | 2026-05-01 | 18:00 | For live line PID scanning of Insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 27-Apr-2026 | 20:20 | 29-Apr-2026 | 09:28
RQ107707 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-02 | 08:00 | 2026-05-02 | 18:00 | For live line PID scanning of Insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 27-Apr-2026 | 20:20 | 29-Apr-2026 | 13:13
RQ107708 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-03 | 08:00 | 2026-05-03 | 18:00 | For live line PID scanning of Insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 27-Apr-2026 | 20:20 | 30-Apr-2026 | 10:33
RQ107712 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-07 | 08:00 | 2026-05-07 | 18:00 | For live line PID scanning of Insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 20:20 | 04-May-2026 | 12:28
RQ107716 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-01 | 08:00 | 2026-05-01 | 18:00 | For Live line PID scanning of Insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 20:24 | 29-Apr-2026 | 09:28
RQ107718 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-03 | 08:00 | 2026-05-03 | 18:00 | For Live line PID scanning of Insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 20:24 | 30-Apr-2026 | 10:33
RQ107722 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-07 | 08:00 | 2026-05-07 | 18:00 | For Live line PID scanning of Insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 20:24 | 04-May-2026 | 12:28
RQ107726 | PNOCC | PGCIL SR-1 | A/R of 400KV-KURNOOL_PG-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-01 | 08:00 | 2026-05-01 | 18:00 | For Live line PID scanning of Insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 20:27 | 29-Apr-2026 | 09:28
RQ107728 | PNOCC | PGCIL SR-1 | A/R of 400KV-KURNOOL_PG-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-03 | 08:00 | 2026-05-03 | 18:00 | For Live line PID scanning of Insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 27-Apr-2026 | 20:27 | 30-Apr-2026 | 10:33
RQ107732 | PNOCC | PGCIL SR-1 | A/R of 400KV-KURNOOL_PG-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-07 | 08:00 | 2026-05-07 | 18:00 | For Live line PID scanning of Insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 27-Apr-2026 | 20:27 | 04-May-2026 | 12:22
RQ107733 | PNOCC | PGCIL SR-1 | A/R of 400KV-KURNOOL_PG-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-08 | 08:00 | 2026-05-08 | 18:00 | For Live line PID scanning of Insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 27-Apr-2026 | 20:27 | 05-May-2026 | 10:30
RQ107801 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-03 | 06:00 | 2026-05-03 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 28-Apr-2026 | 19:02 | 30-Apr-2026 | 10:33
RQ107805 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-07 | 06:00 | 2026-05-07 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 28-Apr-2026 | 19:02 | 04-May-2026 | 12:22
RQ107806 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-08 | 06:00 | 2026-05-08 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 28-Apr-2026 | 19:02 | 05-May-2026 | 10:30
RQ107811 | PNOCC | PGCIL SR-1 | A/R of 400KV-GOOTY-KURNOOL_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-03 | 08:00 | 2026-05-03 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 28-Apr-2026 | 19:08 | 30-Apr-2026 | 10:33
RQ107815 | PNOCC | PGCIL SR-1 | A/R of 400KV-GOOTY-KURNOOL_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-07 | 08:00 | 2026-05-07 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 28-Apr-2026 | 19:08 | 04-May-2026 | 12:28
RQ107847 | PNOCC | kptcl | 220KV-KUDGI_NTPC-SAVALAGI-1 | KPTCL | C | Stringing of conductor between location 1 and 2 covering a distance of 18.5 km in bilagi taluk. | 2026-05-07 | 00:00 | 2026-05-07 | 18:00 | Line clear of 220kV Kudagi Savalagi line 01 and 02 (approved in mid review of OCC 237) are not able to avail from 01.05.2026 to 03.05.2026 due to ROW issue and the same is requested from 05.05.2026 to 07.05.2026. Establishing 2X100MVA, 220/110/11KV Sub-station at Bilagi in Bilagi Taluk, Bagalkot District, with associated 220 kV Kudagi-Vajramatti line (18.455 Kms), - onTotal turnkey basis. As Krishna river crossing work of first circuit to be completed by 25.05.2026 | Yes | Rejected | RoW diagrams furnished by KPTCL. All the necessary approvals / minutes are yet to be submitted. Detailed Load and generation Management details need to be submitted by KPTCL for the D/C shutdown. The shutdown of the 220 kV Kudgi–SAVALAGI D/C line has a sensitivity of approximately 15% on the 400/220 kV Narendra ICTs(2*500MVA), which have an N-1 limit of 306 MW for each ICT. Currently, the Narendra ICTs are loaded up to 420 MW and 450 MVA. Under these conditions, any tripping or reduction in generation at Nagjheri (6 × 150 MW) is likely to further aggravate the loading on the ICTs and may lead to cascading tripping. In addition, the following 220 kV lines are expected to be highly loaded and may exceed their N-1 limits: 220 kV Alamathi–Bagalkot D/C 220 kV Narendra–Ghataprabha D/C 220 kV Kanabargi–Narendra (KA) D/C 220 kV Belagavi–Kanabargi D/C Further, voltages at nearby 220 kV substations are observed to reduce by approximately 4–6 kV. In view of the above, Karnataka is requested to provide remedial measures for load and voltage management, along with an N-1 contingency action plan. The same may be supported with relevant PSS®E study files for further analysis and processing. | Line Circuits | 29-Apr-2026 | 13:21 | 04-May-2026 | 12:14
RQ107849 | PNOCC | kptcl | 220KV-KUDGI_NTPC-SAVALAGI-2 | KPTCL | C | Stringing of conductor between location 1 and 2 covering a distance of 18.5 km in bilagi taluk. | 2026-05-07 | 00:00 | 2026-05-07 | 18:00 | Line clear of 220kV Kudagi Savalagi line 01 and 02 (approved in mid review of OCC 237) are not able to avail from 01.05.2026 to 03.05.2026 due to ROW issue and the same is requested from 05.05.2026 to 07.05.2026. Establishing 2X100MVA, 220/110/11KV Sub-station at Bilagi in Bilagi Taluk, Bagalkot District, with associated 220 kV Kudagi-Vajramatti line (18.455 Kms), - onTotal turnkey basis. As Krishna river crossing work of first circuit to be completed by 25.05.2026 | Yes | Rejected | RoW diagrams furnished by KPTCL. All the necessary approvals / minutes are yet to be submitted. Detailed Load and generation Management details need to be submitted by KPTCL for the D/C shutdown. The shutdown of the 220 kV Kudgi–SAVALAGI D/C line has a sensitivity of approximately 15% on the 400/220 kV Narendra ICTs(2*500MVA), which have an N-1 limit of 306 MW for each ICT. Currently, the Narendra ICTs are loaded up to 420 MW and 450 MVA. Under these conditions, any tripping or reduction in generation at Nagjheri (6 × 150 MW) is likely to further aggravate the loading on the ICTs and may lead to cascading tripping. In addition, the following 220 kV lines are expected to be highly loaded and may exceed their N-1 limits: 220 kV Alamathi–Bagalkot D/C 220 kV Narendra–Ghataprabha D/C 220 kV Kanabargi–Narendra (KA) D/C 220 kV Belagavi–Kanabargi D/C Further, voltages at nearby 220 kV substations are observed to reduce by approximately 4–6 kV. In view of the above, Karnataka is requested to provide remedial measures for load and voltage management, along with an N-1 contingency action plan. The same may be supported with relevant PSS®E study files for further analysis and processing. | Line Circuits | 29-Apr-2026 | 13:29 | 04-May-2026 | 12:14
RQ107859 | PNOCC | KSPDCL | PAVAGADA_PG - 220KV - BUS 3 | PGCIL SR-2 | C | Bay equipment erection, alignment of isolators, IPS tube erection, earthing and jumper work at Bay No.230 | 2026-05-03 | 18:00 | 2026-05-04 | 02:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Bus | 29-Apr-2026 | 16:00 | 30-Apr-2026 | 10:33
RQ107906 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-07 | 06:00 | 2026-05-07 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 30-Apr-2026 | 07:06 | 04-May-2026 | 12:28
RQ107916 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-07 | 06:00 | 2026-05-07 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 30-Apr-2026 | 07:06 | 04-May-2026 | 12:28
RQ107959 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-3 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-13 | 07:00 | 2026-05-13 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 30-Apr-2026 | 17:29 | 10-May-2026 | 11:11
RQ107962 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-4 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-13 | 07:00 | 2026-05-13 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 30-Apr-2026 | 17:29 | 10-May-2026 | 11:11
RQ107963 | PNOCC | TGTRANSCO | 400KV-YEDULA-MEHBOOBNAGAR-1 | TGTRANSCO | C | LC on 04.05.2026 on 400kv Veltoor-yedula line -1along with bays at veltoor ss and yedula ss for commissioning of line differential relay of veltoor-yedula line-1 | 2026-05-04 | 09:00 | 2026-05-04 | 19:00 | Please issue LC. | Yes | Rejected | Multiple shutdowns at the same station. | Line Circuits | 30-Apr-2026 | 20:03 | 01-May-2026 | 13:58
RQ107964 | PNOCC | PGCIL SR-1 | TIE BAY (402) OF 400KV-KHAMMAM_PG-NAGARJUNASAGAR_PG-3 AND 400KV-KHAMMAM_PG-NAGARJUNASAGAR_PG-2 @NAGARJUNASAGAR_PG - 400KV | PGCIL SR-1 | C | Bay AMP works. | 2026-05-04 | 09:00 | 2026-05-04 | 18:00 | Bay AMP works | Yes | Approved | Remaining bays shall be in service. | Bay | 30-Apr-2026 | 20:06 | 01-May-2026 | 13:58
RQ107966 | EMERGENCY | TANTRANSCO | 400KV-OTTAPIDARAM-UDANGUDI-2 | TANTRANSCO | D | For safe working clearance to carryout tree cutting works in between location 39&40 in 400 KV Ottapidaram – Udankudi line 1 which is already under outage . | 2026-05-01 | 10:00 | 2026-05-01 | 13:00 | Udangudi unit 1 is already under shut down | Yes | Approved |  | Line Circuits | 01-May-2026 | 09:52 | 01-May-2026 | 10:10
RQ108233 | EMERGENCY | TANTRANSCO | 400KV-ENNORE SEZ-SUNGAVARACHATRAM-1 | TANTRANSCO | D | to attend glow in B phase isolator | 2026-05-03 | 06:00 | 2026-05-03 | 08:00 | during the period of LC 400KV SUNGAVARACHATRAM - NCTPS feeder will cater the load. It is necessary to attend the glow immediately | Yes | Approved |  | Line Circuits | 02-May-2026 | 15:14 | 03-May-2026 | 06:29
RQ108317 | EMERGENCY | PGCIL SR-1 | 400KV-NELLORE_PG-THIRUVALAM-1 | POWERGRID | C | For attending hotspot at LOC No. 351 | 2026-05-03 | 10:00 | 2026-05-03 | 12:00 | For attending hotspot at LOC No. 351 | Yes | Approved | Shutdown to be returned on time. Sensitivity on other line is 25-30%. | Line Circuits | 02-May-2026 | 19:31 | 03-May-2026 | 10:21
RQ108376 | EMERGENCY | aptransco | 400KV-VTPS_IV-VIJAYAWADA-1 | ANDHRA PRADESH | C | for replacing protection couplers of the feeder and for attending protection coupler testings | 2026-05-03 | 10:00 | 2026-05-03 | 18:00 | LC on 411 bay was approved in OCC | Yes | Approved |  | Line Circuits | 03-May-2026 | 09:52 | 03-May-2026 | 10:22
RQ108377 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-1 | KPTCL | D | For OPGW stringing work | 2026-05-07 | 06:00 | 2026-05-07 | 18:00 |  | Yes | Approved | Load Management need to be done by KPTCL in case of any contingency. | Auto Reclosure | 03-May-2026 | 10:34 | 04-May-2026 | 12:22
RQ108383 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-1 | KPTCL | D | For OPGW stringing work | 2026-05-13 | 06:00 | 2026-05-13 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 03-May-2026 | 10:34 | 10-May-2026 | 11:11
RQ108385 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-1 | KPTCL | D | For OPGW stringing work | 2026-05-15 | 06:00 | 2026-05-15 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 03-May-2026 | 10:34 | 12-May-2026 | 10:17
RQ108387 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-2 | KPTCL | D | For OPGW stringing work | 2026-05-07 | 06:00 | 2026-05-07 | 18:00 |  | Yes | Approved | Load Management need to be done by KPTCL in case of any contingency. | Auto Reclosure | 03-May-2026 | 10:34 | 04-May-2026 | 12:22
RQ108393 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-2 | KPTCL | D | For OPGW stringing work | 2026-05-13 | 06:00 | 2026-05-13 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 03-May-2026 | 10:34 | 10-May-2026 | 11:11
RQ108395 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-2 | KPTCL | D | For OPGW stringing work | 2026-05-15 | 06:00 | 2026-05-15 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 03-May-2026 | 10:34 | 12-May-2026 | 10:17
RQ108454 | PNOCC | PGCIL SR-1 | MAIN BAY (413) OF 400KV-NAGARJUNASAGAR_PG-RAMAGUNDAM-2 AND NAGARJUNASAGAR_PG - 400KV - BUS 1 @NAGARJUNASAGAR_PG - 400KV | PGCIL SR-1 | D | Bay AMP works. | 2026-05-07 | 07:00 | 2026-05-07 | 18:00 | Bay AMP works. | Yes | Approved | Remaining bays shall be in service. | Bay | 03-May-2026 | 15:41 | 04-May-2026 | 12:22
RQ108455 | PNOCC | PGCIL SR-1 | TIE BAY (408) OF NP_KUNTA - 400KV B/R 1 AND FUTURE @NP_KUNTA - 400KV | PGCIL SR-1 | D | Bay AMP works. | 2026-05-07 | 06:30 | 2026-05-07 | 16:30 | Bay AMP works. | Yes | Approved | Remaining bays shall be in service. | Bay | 03-May-2026 | 15:45 | 04-May-2026 | 12:22
RQ108586 | EMERGENCY | PGCIL SR-2 | TIE BAY (420) OF 400KV/230KV UDUMALPET_PG-ICT-3 AND FUTURE @UDUMALPET_PG - 400KV | PGCIL SR-2 | D | To rectify 42089B B phase isolator which is partially opened | 2026-05-04 | 10:30 | 2026-05-04 | 13:30 | To rectify 42089B B phase isolator which is partially opened | Yes | Approved |  | Bay | 04-May-2026 | 10:10 | 04-May-2026 | 10:13
RQ108588 | PNOCC | kptcl | MAIN BAY (418) OF 400KV/220KV NELAMANGALA-ICT-1 AND NELAMANGALA - 400KV - BUS 2 @NELAMANGALA - 400KV | KPTCL | C | Dure to operational constraints ICT2 main breaker 409 shutdown was not availed instead they have requested for 400 kv ICT1 Main breaker bay 418 on 08.05.2026. Kindly approve shutdown of 400 kv ICT1 Main breaker bay 418. | 2026-05-08 | 11:00 | 2026-05-08 | 17:00 | Due to operational constraints not availing ICT2 main breaker bay 409 shutdown on 08.05.2026. | Yes | Approved | Remaining bays shall be in service. | Bay | 04-May-2026 | 12:28 | 05-May-2026 | 10:30
RQ108589 | PNOCC | PGCIL SR-2 | MAIN BAY (409) OF 400KV-NEYVELI_TS_II-SALEM-2 AND SALEM - 400KV - BUS 2 @SALEM - 400KV | PGCIL SR-2 | D | Dew Point measurement of CB | 2026-05-08 | 10:00 | 2026-05-08 | 11:30 | Dew Point measurement of CB | Yes | Approved | Remaining bays shall be in service. Consecutive shutdowns at the same station. | Bay | 04-May-2026 | 12:39 | 05-May-2026 | 10:30
RQ108592 | PNOCC | PGCIL SR-2 | TIE BAY (416) OF 400KV-SALEM-DHARMAPURI-2 AND 400KV-SALEM-DHARMAPURI-1 @SALEM - 400KV | PGCIL SR-2 | D | Critical CB dew point measurement | 2026-05-08 | 15:00 | 2026-05-08 | 16:30 | Critical CB dew point measurement | Yes | Approved | Remaining bays shall be in service. Consecutive shutdowns at the same station. | Bay | 04-May-2026 | 12:48 | 05-May-2026 | 10:30
RQ108593 | PNOCC | PGCIL SR-2 | MAIN BAY (415) OF 400KV-SALEM-DHARMAPURI-1 AND SALEM - 400KV - BUS 1 @SALEM - 400KV | PGCIL SR-2 | D | Critical CB dew point measurement | 2026-05-08 | 11:30 | 2026-05-08 | 13:00 | Critical CB dew point measurement | Yes | Approved | Remaining bays shall be in service. Consecutive shutdowns at the same station. | Bay | 04-May-2026 | 12:51 | 05-May-2026 | 10:30
RQ108596 | PNOCC | PGCIL SR-1 | MAIN BAY (406) OF GHANAPUR - 400KV - BUS 2 AND 400KV-GHANAPUR-RAMAGUNDAM-4 @GHANAPUR - 400KV | PGCIL SR-1 | D | For attending Bay maintenance work. | 2026-05-08 | 09:00 | 2026-05-08 | 18:00 | For attending Bay AMP works. | Yes | Approved | Remaining bays shall be in service. | Bay | 04-May-2026 | 17:20 | 05-May-2026 | 10:30
RQ108607 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-3 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-15 | 07:00 | 2026-05-15 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 05-May-2026 | 16:55 | 12-May-2026 | 10:17
RQ108610 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-3 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-18 | 07:00 | 2026-05-18 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 05-May-2026 | 16:55 | 15-May-2026 | 10:38
RQ108612 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-4 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-15 | 07:00 | 2026-05-15 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 05-May-2026 | 16:55 | 12-May-2026 | 10:17
RQ108615 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-4 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-18 | 07:00 | 2026-05-18 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 05-May-2026 | 16:55 | 15-May-2026 | 10:38
RQ108624 | EMERGENCY | TANTRANSCO | 400KV-ARIYALUR-KALVENDAPATTU-1 | TANTRANSCO | D | earth wire had been snapped and fallen down in between location no.552 and 553 | 2026-05-06 | 02:15 | 2026-05-06 | 05:00 | 400KV Ariyalur - Kalivanthapattu 2 in service | Yes | Approved |  | Line Circuits | 06-May-2026 | 02:18 | 06-May-2026 | 02:23
RQ108625 | EMERGENCY | PGCIL SR-2 | TIE BAY (428) OF 400KV/230KV MADURAI_PG-ICT-3 AND 400KV-MADURAI_PG-TUTICORIN_PS-1 @MADURAI_PG - 400KV | PGCIL SR-2 | C | For attending CB lockout alarm. | 2026-05-06 | 03:15 | 2026-05-06 | 06:15 |  | Yes | Approved |  | Bay | 06-May-2026 | 03:07 | 06-May-2026 | 03:08
RQ108643 | PNOCC | PGCIL SR-2 | TIE BAY (423) OF 400KV-TIRUNELVELI-UDUMALPET_PG-1 AND 400KV/37KV UDUMALPET_PG-STATCOM COUPLER-1 @UDUMALPET_PG - 400KV | PGCIL SR-2 | C | CB operating mechanism overhauling works | 2026-05-18 | 08:00 | 2026-05-19 | 20:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 06-May-2026 | 21:02 | 15-May-2026 | 10:44
RQ108656 | EMERGENCY | TGTRANSCO | MAIN BAY (412) OF MANUGURU - 400KV B/R 1 AND MANUGURU - 400KV - BUS 1 @MANUGURU - 400KV | TGGENCO | C | for topup the SF6 gas of 412-52 CB | 2026-05-07 | 11:20 | 2026-05-07 | 13:20 | It is requested to accord permission and issue LC opening code. | Yes | Approved |  | Bay | 07-May-2026 | 11:23 | 07-May-2026 | 11:34
RQ108683 | EMERGENCY | aptransco | 400KV-MARADAM-KALPAKKA-2 | APTRANSCO | C | For replacement of broken 1 No: Y-Ph SRC insulator, which was broken at loc No: 141(DD+0), with new src insulators | 2026-05-08 | 10:30 | 2026-05-08 | 16:30 |  | Yes | Approved |  | Line Circuits | 08-May-2026 | 10:27 | 08-May-2026 | 11:03
RQ108685 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-15 | 06:00 | 2026-05-15 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 08-May-2026 | 11:12 | 12-May-2026 | 10:17
RQ108688 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-18 | 06:00 | 2026-05-18 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 08-May-2026 | 11:12 | 15-May-2026 | 10:38
RQ108690 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-20 | 06:00 | 2026-05-20 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 08-May-2026 | 11:12 | 17-May-2026 | 10:24
RQ108693 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-15 | 06:00 | 2026-05-15 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 08-May-2026 | 11:12 | 12-May-2026 | 10:17
RQ108696 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-18 | 06:00 | 2026-05-18 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 08-May-2026 | 11:12 | 15-May-2026 | 10:38
RQ108698 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-20 | 06:00 | 2026-05-20 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 08-May-2026 | 11:12 | 17-May-2026 | 10:24
RQ108701 | EMERGENCY | PGCIL SR-2 | 400KV-VALLUR-ALAMATHY-2 | POWERGRID | C | Emergency shutdown required to facilitate the shutdown of 400kV Vallur-Alamathy-1 | 2026-05-08 | 12:11 | 2026-05-08 | 15:11 |  | Yes | Approved |  | Line Circuits | 08-May-2026 | 12:12 | 08-May-2026 | 12:13
RQ108723 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | PID scanning works old insulators. | 2026-05-18 | 08:00 | 2026-05-18 | 18:00 | PID Scanning of insulator. Please approve up to 31.05.2026 | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 08-May-2026 | 19:30 | 15-May-2026 | 10:44
RQ108725 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | PID scanning works old insulators. | 2026-05-20 | 08:00 | 2026-05-20 | 18:00 | PID Scanning of insulator. Please approve up to 31.05.2026 | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 08-May-2026 | 19:30 | 17-May-2026 | 10:33
RQ108744 | EMERGENCY | aptransco | 400KV-MARADAM-KALPAKKA-1 | APTRANSCO | C | For replacement of broken 1 No: Y-Ph SRC insulator with new src insulator at loc No: 127(DB+0) in 400KV Kalapaka- Maradam line-1 | 2026-05-09 | 11:15 | 2026-05-09 | 17:15 |  | Yes | Approved | 400KV-MARADAM-KALPAKKA-2, 400KV-VEMAGIRI-KALPAKKA and KALPAKKA ICTs shall be in service. | Line Circuits | 09-May-2026 | 11:12 | 09-May-2026 | 11:41
RQ108747 | PNOCC | PGCIL SR-2 | 765KV/400KV THIRUVALAM-ICT-2 | PGCIL SR-2 | C | AMP works of ICT-2 | 2026-05-15 | 09:00 | 2026-05-15 | 15:00 | The shutdown was approved in OCC 237 OCC for 14.05.2026, but due to non availability of OEM we are unable to avail the ICT-2 shutdown at Thiruvalam SS. Hence, it is requested to kindly reschedule the shutdown as requested. | Yes | Approved | Subject to real time grid conditions and ICT loadings. Subject to NLDC approval. N-1 limit for THIRUVALLAM ICTs is 897 MW each. 765KV/400KV THIRUVALAM-ICT-1 57% All 765kV/400kV ARIYALUR and CUDDAPAH ICTs 765kV-ARIYALUR-THIRUVALLAM D/C 7% each 400KV-THIRUVALAM-NPS D/C shall be in service. | Transformer | 09-May-2026 | 17:31 | 12-May-2026 | 10:20
RQ108760 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | Live line PID testing of insulator in line | 2026-05-18 | 07:00 | 2026-05-18 | 18:00 | Nil | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 10-May-2026 | 13:18 | 15-May-2026 | 10:44
RQ108762 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | Live line PID testing of insulator in line | 2026-05-20 | 07:00 | 2026-05-20 | 18:00 | Nil | Yes | Approved | Concurred, subject to real time grid conditions. Approved along with S/D of 400kV-GAJWEL-CHANDALAPUR-2. | Auto Reclosure | 10-May-2026 | 13:18 | 17-May-2026 | 10:29
RQ108769 | PNOCC | PGCIL SR-2 | A/R of 400KV-NARENDRA-GUTTUR-1 | POWERGRID | D | OPGW rectification works. | 2026-05-15 | 09:00 | 2026-05-15 | 17:00 | OPGW rectification works. | Yes | Rejected | In view of tower collapse at KAIGA -GUTTUR. | Auto Reclosure | 10-May-2026 | 19:07 | 12-May-2026 | 15:45
RQ108772 | PNOCC | PGCIL SR-2 | A/R of 400KV-NARENDRA-GUTTUR-2 | POWERGRID | D | OPGW rectification works. | 2026-05-15 | 09:00 | 2026-05-15 | 17:00 | OPGW rectification works. | Yes | Rejected | In view of tower collapse at KAIGA -GUTTUR. | Auto Reclosure | 10-May-2026 | 19:07 | 12-May-2026 | 15:45
RQ108774 | PNOCC | PGCIL SR-2 | A/R of 400KV-KUDGI_PG-NARENDRA-1 | POWERGRID | D | OPGW rectification works. | 2026-05-18 | 09:00 | 2026-05-18 | 17:00 | OPGW rectification works. | Yes | Rejected | Due to tower collapse at KAIGA GUTTUR. | Auto Reclosure | 10-May-2026 | 19:07 | 15-May-2026 | 10:38
RQ108776 | PNOCC | PGCIL SR-2 | A/R of 400KV-KUDGI_PG-NARENDRA-1 | POWERGRID | D | OPGW rectification works. | 2026-05-20 | 09:00 | 2026-05-20 | 17:00 | OPGW rectification works. | Yes | Rejected | Due to 400kV-KAIGA-GUTTUR D/C tower collapse. | Auto Reclosure | 10-May-2026 | 19:07 | 17-May-2026 | 10:24
RQ108777 | PNOCC | PGCIL SR-2 | A/R of 400KV-KUDGI_PG-NARENDRA-2 | POWERGRID | D | OPGW rectification works. | 2026-05-18 | 09:00 | 2026-05-18 | 17:00 | OPGW rectification works. | Yes | Rejected | Due to tower collapse at KAIGA GUTTUR. | Auto Reclosure | 10-May-2026 | 19:07 | 15-May-2026 | 10:38
RQ108779 | PNOCC | PGCIL SR-2 | A/R of 400KV-KUDGI_PG-NARENDRA-2 | POWERGRID | D | OPGW rectification works. | 2026-05-20 | 09:00 | 2026-05-20 | 17:00 | OPGW rectification works. | Yes | Rejected | Due to 400kV-KAIGA-GUTTUR D/C tower collapse. | Auto Reclosure | 10-May-2026 | 19:07 | 17-May-2026 | 10:24
RQ108781 | EMERGENCY | PGCIL SR-1 | 400KV-KHAMMAM_PG-WARANGAL-1 | POWERGRID | D | To attend insulator De-Cap | 2026-05-11 | 06:15 | 2026-05-11 | 12:30 |  | Yes | Approved |  | Line Circuits | 11-May-2026 | 06:17 | 11-May-2026 | 06:22
RQ108815 | EMERGENCY | NLC | 400KV/230KV NEYVELI_TS_II-ICT-2 | NLC | C | For attending SF6 low alarm in B phase SF6 CT | 2026-05-12 | 10:30 | 2026-05-12 | 11:30 | ICT-1 will be in service. | Yes | Approved | Approved on emergency. | Transformer | 12-May-2026 | 09:46 | 12-May-2026 | 11:43
RQ108817 | EMERGENCY | WKTL | 765KV-MAHESHWARAM_PG-WARANGAL(NEW)-1 | WKTL | D | we had observed the insulator broken on 765kV Warangal (NEW) - Maheswaram (PG) CKT- 1 Tower No.320 Bottom Phase.We require the emergency outage of for 765kV Warangal (NEW) - Maheswaram (PG) CKT- 1 for replacement of broken insulator. | 2026-05-12 | 12:00 | 2026-05-12 | 17:00 |  | Yes | Approved | Subject to NLDC concurrence. | Line Circuits | 12-May-2026 | 09:58 | 12-May-2026 | 14:14
RQ108820 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-1 | KPTCL | D | For OPGW stringing work | 2026-05-18 | 06:00 | 2026-05-18 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 10:47 | 15-May-2026 | 10:38
RQ108822 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-1 | KPTCL | D | For OPGW stringing work | 2026-05-20 | 06:00 | 2026-05-20 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 10:47 | 17-May-2026 | 10:24
RQ108829 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-2 | KPTCL | D | For OPGW stringing work | 2026-05-18 | 06:00 | 2026-05-18 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 10:47 | 15-May-2026 | 10:38
RQ108831 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-2 | KPTCL | D | For OPGW stringing work | 2026-05-20 | 06:00 | 2026-05-20 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 10:47 | 17-May-2026 | 10:24
RQ108842 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-3 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-20 | 07:00 | 2026-05-20 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 13:04 | 17-May-2026 | 10:24
RQ108849 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-4 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-20 | 07:00 | 2026-05-20 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 13:04 | 17-May-2026 | 10:24
RQ108859 | PNOCC | NPCIL | 220KV-KAIGA-KADRA-1 | KPTCL | C | Preventive maintenance work of bay equipment | 2026-05-16 | 08:00 | 2026-05-17 | 20:00 | Shutdown required for 3 days i.e. up to 18/05/2026, 20.00Hrs | Yes | Rejected | KPTCL concurrence need to be submitted along with load and generation management at KAIGA, KADRA, and KODASALLY. As the requested shutdown period exceed two days, SRPC consent also need to be submitted. | Line Circuits | 12-May-2026 | 15:33 | 13-May-2026 | 10:29
RQ108860 | PNOCC | NPCIL | KAIGA - 220KV - BUS 1 | NPCIL_KAIGA | C | String Insulator replacement and Cleaning | 2026-05-16 | 08:00 | 2026-05-17 | 20:00 | Preventive maintenance | Yes | Rejected | KPTCL concurrence need to be submitted along with load and generation management at KAIGA, KADRA, and KODASALLY. | Bus | 12-May-2026 | 15:38 | 13-May-2026 | 10:29
RQ108864 | PNOCC | PGCIL SR-2 | TIE BAY (402) OF 400KV/220KV KOLAR_AC-ICT-1 AND 400KV/220KV KOLAR_AC-ICT-2 @KOLAR_AC - 400KV | PGCIL SR-2 | D | For AMP Works | 2026-05-20 | 09:00 | 2026-05-20 | 17:00 |  | Yes | Rejected | Multiple shutdowns at the same station. | Bay | 12-May-2026 | 20:30 | 17-May-2026 | 10:29
RQ108871 | PNOCC | PGCIL SR-2 | MAIN BAY (403) OF 400KV-HIRIYUR-MYSORE-1 AND MYSORE - 400KV - BUS 1 @MYSORE - 400KV | PGCIL SR-2 | D | For LBB relay retrofitting works | 2026-05-18 | 09:00 | 2026-05-18 | 17:30 | PLEASE APPROVE | Yes | Approved | Remaining bays shall be in service. | Bay | 13-May-2026 | 11:06 | 15-May-2026 | 10:44
RQ108873 | PNOCC | NTPC | TIE BAY (421) OF 400KV/220KV RAMAGUNDAM-ICT-2 AND 400KV/220KV RAMAGUNDAM-ICT-3 @RAMAGUNDAM - 400KV | NTPC | C | bay maintenance works | 2026-05-18 | 08:00 | 2026-05-18 | 19:00 | connected line will be in charged condition through main bay | Yes | Approved | Remaining bays shall be in service. | Bay | 13-May-2026 | 11:41 | 15-May-2026 | 10:44
RQ108874 | PNOCC | PGCIL SR-2 | TIE BAY (416) OF 400KV-SALEM-DHARMAPURI-2 AND 400KV-SALEM-DHARMAPURI-1 @SALEM - 400KV | PGCIL SR-2 | C | For filtering SF6 Gas of the breaker due to low/poor dew point. | 2026-05-18 | 09:30 | 2026-05-19 | 17:30 | pl approve | Yes | Approved | Remaining bays shall be in service. | Bay | 13-May-2026 | 11:46 | 15-May-2026 | 10:44
RQ108903 | EMERGENCY | TANTRANSCO | MAIN BAY (403) OF 400KV/110KV VELLALAVIDUTHI-ICT-2 AND VELLALAVIDUTHI - 400KV - BUS 2 @VELLALAVIDUTHI - 400KV | TANTRANSCO | D | IN ICT-2 MAIN BREAKER 403-52 CB DC CONTROL CABLE 20 COREX 2.5 SQ MM TO BE REPLACE FOR ARRESTING OF DC LEAKAGE. | 2026-05-15 | 10:00 | 2026-05-15 | 17:00 | ICT 2 will be in service through Tie breaker | Yes | Approved |  | Bay | 14-May-2026 | 14:42 | 15-May-2026 | 10:19
RQ108907 | PNOCC | PGCIL SR-1 | A/R of 400KV-KHAMMAM_PG-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-18 | 07:00 | 2026-05-18 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Rejected | Multiple shutdowns at the same stations. | Auto Reclosure | 14-May-2026 | 18:10 | 15-May-2026 | 11:05
RQ108909 | PNOCC | PGCIL SR-1 | A/R of 400KV-KHAMMAM_PG-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-20 | 07:00 | 2026-05-20 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 14-May-2026 | 18:10 | 17-May-2026 | 10:29
RQ108913 | PNOCC | PGCIL SR-1 | A/R of 400KV-KURNOOL_PG-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-18 | 07:00 | 2026-05-18 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Rejected | Multiple shutdowns at the same stations. | Auto Reclosure | 14-May-2026 | 18:13 | 15-May-2026 | 11:05
RQ108922 | PNOCC | NTPC | MAIN BAY (426) OF RAMAGUNDAM - 400KV - BUS 4 AND 400KV/220KV RAMAGUNDAM-ICT-4 @RAMAGUNDAM - 400KV | NTPC | C | Bay Pm Works And Testing Equipments | 2026-05-20 | 08:00 | 2026-05-20 | 18:00 | Bay Pm Works And Testing Equipments | Yes | Approved | Remaining bays shall be in service. | Bay | 15-May-2026 | 12:16 | 17-May-2026 | 10:29
RQ108956 | PNOCC | PGCIL SR-2 | MAIN BAY (415) OF 400KV-HOSUR_PG-SALEM-2 AND HOSUR_PG - 400KV - BUS 2 @HOSUR_PG - 400KV | PGCIL SR-2 | C | Bay AMP works | 2026-05-20 | 09:00 | 2026-05-20 | 17:30 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 16-May-2026 | 17:30 | 17-May-2026 | 10:33
RQ108957 | PNOCC | PGCIL SR-1 | KURNOOL_PG - 400KV - BUS 1 | PGCIL SR-1 | C | As per OCC 237 S/D originally approved from 23.05.2026 to 24.05.2026. Due to site constraints , it is requested to prepone S/D from 20.05.2026 to 21.05.2026 on continuous basis.Kindly approve | 2026-05-20 | 07:30 | 2026-05-21 | 20:00 | As per OCC 237 S/D originally approved from 23.05.2026 to 24.05.2026. Due to site constraints , it is requested to prepone S/D from 20.05.2026 to 21.05.2026 on continuous basis.Kindly approve | Yes | Approved | Remaining all elements shall be in service. | Bus | 16-May-2026 | 17:47 | 17-May-2026 | 10:29
RQ108958 | PNOCC | PGCIL SR-1 | MAIN BAY (407) OF 400KV-MEPL-NPS-1 AND NPS - 400KV - BUS 1 @NPS - 400KV | PGCIL SR-1 | C | Overhauling of Spring Spring Drive Mechanism of Alstom CB (Model: GL316) and AMP works | 2026-05-20 | 06:00 | 2026-05-21 | 18:00 | Overhauling of Spring Spring Drive Mechanism of Alstom CB (Model: GL316) and AMP works | Yes | Approved | Remaining bays shall be in service. | Bay | 16-May-2026 | 18:07 | 17-May-2026 | 10:33
RQ108995 | PNOCC | PGCIL SR-1 | MAIN BAY (416) OF 400KV/220KV VIJAYAWADA-ICT-1 AND VIJAYAWADA - 400KV - BUS 1 @VIJAYAWADA - 400KV | PGCIL SR-1 | C | 416 Bay Y & B-Ph CTs Replacement under Addcap along with precommissioining testing | 2026-05-20 | 09:00 | 2026-05-21 | 23:59 | 416 Bay Y & B-Ph CTs Replacement under Addcap along with precommissioining testing..Please approve S/D up to 23.05.2026 | Yes | Approved | FTC is required. Remaining bays shall be in service. | Bay | 16-May-2026 | 20:08 | 17-May-2026 | 10:33
RQ108997 | PNOCC | PGCIL SR-2 | MAIN BAY (416) OF 400KV-KALVENDAPATTU-PUGALUR-1 AND KALVENDAPATTU - 400KV - BUS 2 @KALVENDAPATTU - 400KV | PGCIL SR-2 | C | For Bay AMP works. | 2026-05-20 | 09:00 | 2026-05-20 | 18:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 16-May-2026 | 21:01 | 17-May-2026 | 10:33
RQ109129 | EMERGENCY | TGTRANSCO | 400KV/27KV YADADRI TPP-GT-4 | TGGENCO,TGTRANSCO | C | To attend the works of SPVT , LAVT PT fuse limit switches and to replace the cooling fan of GT-4B phase GCB ,431 ,432 Breakers to be isolated | 2026-05-19 | 13:00 | 2026-05-20 | 23:59 | Unit-4 is under shut down please issue LC | Yes | Approved |  | Transformer | 19-May-2026 | 11:31 | 19-May-2026 | 11:41
RQ109165 | PNOCC | WKTL | KUDGI_PG - 400KV - BUS 2 | PGCIL SR-2 | C | Extension/Interconnection of400kv Main Bus-2 from existing PGCIL Kudgi to WRSR New Narendra. | 2026-05-26 | 09:00 | 2026-05-28 | 23:59 | This outage not taken due to ongoing BUS-1 outage so we are rescheduling this outage from 25.05.2026 09:00Hrs to 30.05.2026 18:00Hrs on continous basis. | Yes | Approved | Concurred for ICT-3 and ICT-4 Interconnection works. All elements shall be in service. | Bus | 19-May-2026 | 17:06 | 22-May-2026 | 13:54
RQ109166 | PNOCC | WKTL | TIE BAY (420) OF 400KV-KOPPAL-KUDGI_PG-1 AND 400KV/220KV KUDGI_PG-ICT-3 @KUDGI_PG - 400KV | KNTL | C | Extension/Interconnection of400kv Main Bus-2 from existing PGCIL Kudgi to WRSR New Narendra. | 2026-05-26 | 09:00 | 2026-05-28 | 23:59 | Outage required from 25.05.2026 09:00Hrs to 30.05.2026 18:00Hrs on continous basis for protection wiring purpose(There will be no availability loss due to the same & now both are ideally charged as ICTS are not charged). | Yes | Approved | CEA safety approval submitted. Remaining bays shall be in service. ICT-3 is a future element. | Bay | 19-May-2026 | 17:11 | 22-May-2026 | 13:54
RQ109167 | PNOCC | WKTL | MAIN BAY (421) OF 400KV/220KV KUDGI_PG-ICT-3 AND KUDGI_PG - 400KV - BUS 2 @KUDGI_PG - 400KV | KNTL | C | Extension/Interconnection of400kv Main Bus-2 from existing PGCIL Kudgi to WRSR New Narendra. | 2026-05-26 | 09:00 | 2026-05-28 | 23:59 | Outage required from 25.05.2026 09:00Hrs to 30.05.2026 18:00Hrs on continous basis for protection wiring purpose(There will be no availability loss due to the same & now both are ideally charged as ICTS are not charged). | Yes | Approved | CEA safety approval submitted. Remaining bays shall be in service. ICT-3 is a future element. | Bay | 19-May-2026 | 17:13 | 22-May-2026 | 13:54
RQ109168 | PNOCC | WKTL | TIE BAY (423) OF 400KV-KOPPAL-KUDGI_PG-2 AND 400KV/220KV KUDGI_PG-ICT-4 @KUDGI_PG - 400KV | KTL | C | Extension/Interconnection of400kv Main Bus-2 from existing PGCIL Kudgi to WRSR New Narendra. | 2026-05-26 | 09:00 | 2026-05-28 | 23:59 | Outage required from 25.05.2026 09:00Hrs to 30.05.2026 18:00Hrs on continous basis for protection wiring purpose(There will be no availability loss due to the same & now both are ideally charged as ICTS are not charged). | Yes | Approved | CEA safety approval submitted. Remaining bays shall be in service. ICT-4 is a future element. | Bay | 19-May-2026 | 17:15 | 22-May-2026 | 13:54
RQ109186 | EMERGENCY | TGTRANSCO | 400KV/13.8KV SRISAILAM_LEFT_BANK-ST-2 | TGTRANSCO | C | Request to issue LC on 400/13.8KV, 25MVA Station Transformer-2 for arresting SF6 gas leakage at 400 KV GIS | 2026-05-20 | 11:00 | 2026-05-20 | 20:00 | Please issue LC | Yes | Approved | ST-1 shall be in service. | Transformer | 20-May-2026 | 11:00 | 20-May-2026 | 14:58
RQ109201 | EMERGENCY | kptcl | 400KV/220KV BTPS-ICT-1 | KPCL | C | arcing is observed at 400KV R phase CVT of ICT-1. | 2026-05-20 | 16:00 | 2026-05-20 | 18:00 | Emergency | Yes | Approved | ICT-2 shall be in service | Transformer | 20-May-2026 | 15:45 | 20-May-2026 | 16:14
RQ109230 | EMERGENCY | aptransco | 400KV-SIMHADRI-VEMAGIRI_AP-1 | APTRANSCO | D | For attending redhot rectification on jumper at Loc No: 48 (DB+0, Y-PH) in 400KV STPP- Vemagiri line | 2026-05-21 | 10:00 | 2026-05-21 | 12:00 |  | Yes | Approved | Approved on emergency basis | Line Circuits | 21-May-2026 | 09:41 | 21-May-2026 | 10:43
RQ107662 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-3 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-04 | 07:00 | 2026-05-04 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 16:10 | 01-May-2026 | 13:48
RQ107663 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-3 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-05 | 07:00 | 2026-05-05 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 16:10 | 02-May-2026 | 17:45
RQ107667 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-3 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-09 | 07:00 | 2026-05-09 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 16:10 | 06-May-2026 | 11:26
RQ107668 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-3 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-10 | 07:00 | 2026-05-10 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 16:10 | 07-May-2026 | 10:45
RQ107672 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-4 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-04 | 07:00 | 2026-05-04 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 16:10 | 01-May-2026 | 13:48
RQ107673 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-4 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-05 | 07:00 | 2026-05-05 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 16:10 | 02-May-2026 | 17:45
RQ107677 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-4 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-09 | 07:00 | 2026-05-09 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 16:10 | 06-May-2026 | 11:26
RQ107678 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-4 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-10 | 07:00 | 2026-05-10 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 16:10 | 07-May-2026 | 10:45
RQ107710 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-05 | 08:00 | 2026-05-05 | 18:00 | For live line PID scanning of Insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 20:20 | 02-May-2026 | 18:11
RQ107713 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-08 | 08:00 | 2026-05-08 | 18:00 | For live line PID scanning of Insulators | Yes | Approved | Concurred,. | Auto Reclosure | 27-Apr-2026 | 20:20 | 05-May-2026 | 10:24
RQ107715 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-10 | 08:00 | 2026-05-10 | 18:00 | For live line PID scanning of Insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 20:20 | 07-May-2026 | 10:51
RQ107719 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-04 | 08:00 | 2026-05-04 | 18:00 | For Live line PID scanning of Insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 20:24 | 01-May-2026 | 13:54
RQ107720 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-05 | 08:00 | 2026-05-05 | 18:00 | For Live line PID scanning of Insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 20:24 | 02-May-2026 | 18:11
RQ107723 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-08 | 08:00 | 2026-05-08 | 18:00 | For Live line PID scanning of Insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 20:24 | 05-May-2026 | 10:24
RQ107725 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-10 | 08:00 | 2026-05-10 | 18:00 | For Live line PID scanning of Insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 27-Apr-2026 | 20:24 | 07-May-2026 | 10:51
RQ107729 | PNOCC | PGCIL SR-1 | A/R of 400KV-KURNOOL_PG-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-04 | 08:00 | 2026-05-04 | 18:00 | For Live line PID scanning of Insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 27-Apr-2026 | 20:27 | 01-May-2026 | 13:54
RQ107730 | PNOCC | PGCIL SR-1 | A/R of 400KV-KURNOOL_PG-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For Live line PID scanning of Insulators | 2026-05-05 | 08:00 | 2026-05-05 | 18:00 | For Live line PID scanning of Insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 27-Apr-2026 | 20:27 | 02-May-2026 | 18:11
RQ107802 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-04 | 06:00 | 2026-05-04 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 28-Apr-2026 | 19:02 | 01-May-2026 | 13:54
RQ107803 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-05 | 06:00 | 2026-05-05 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 28-Apr-2026 | 19:02 | 02-May-2026 | 18:11
RQ107808 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-10 | 06:00 | 2026-05-10 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 28-Apr-2026 | 19:02 | 07-May-2026 | 10:51
RQ107812 | PNOCC | PGCIL SR-1 | A/R of 400KV-GOOTY-KURNOOL_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-04 | 08:00 | 2026-05-04 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 28-Apr-2026 | 19:08 | 01-May-2026 | 13:54
RQ107813 | PNOCC | PGCIL SR-1 | A/R of 400KV-GOOTY-KURNOOL_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-05 | 08:00 | 2026-05-05 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 28-Apr-2026 | 19:08 | 02-May-2026 | 18:11
RQ107816 | PNOCC | PGCIL SR-1 | A/R of 400KV-GOOTY-KURNOOL_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-08 | 08:00 | 2026-05-08 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 28-Apr-2026 | 19:08 | 05-May-2026 | 10:24
RQ107818 | PNOCC | PGCIL SR-1 | A/R of 400KV-GOOTY-KURNOOL_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-10 | 08:00 | 2026-05-10 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 28-Apr-2026 | 19:08 | 07-May-2026 | 10:51
RQ107831 | PNOCC | KSPDCL | PAVAGADA_PG - 220KV - BUS 4 | PGCIL SR-2 | C | Bay equipment erection, alignment of isolators, IPS tube erection, earthing and jumper work at Bay No.230 | 2026-05-06 | 18:00 | 2026-05-07 | 02:00 |  | Yes | Approved | subject to real time grid conditions. | Bus | 28-Apr-2026 | 20:34 | 03-May-2026 | 12:20
RQ107832 | PNOCC | KSPDCL | PAVAGADA_PG - 220KV - BUS 3 | PGCIL SR-2 | C | Bay equipment erection, alignment of isolators, IPS tube erection, earthing and jumper work at Bay No.230 | 2026-05-08 | 18:00 | 2026-05-09 | 02:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Bus | 28-Apr-2026 | 20:37 | 05-May-2026 | 10:24
RQ107903 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-04 | 06:00 | 2026-05-04 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. Load Management need to be done by KPTCL in case of any contingency. | Auto Reclosure | 30-Apr-2026 | 07:06 | 01-May-2026 | 13:54
RQ107904 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-05 | 06:00 | 2026-05-05 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. Load Management need to be done by KPTCL in case of any contingency. | Auto Reclosure | 30-Apr-2026 | 07:06 | 02-May-2026 | 17:45
RQ107907 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-08 | 06:00 | 2026-05-08 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 30-Apr-2026 | 07:06 | 05-May-2026 | 10:24
RQ107908 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-09 | 06:00 | 2026-05-09 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 30-Apr-2026 | 07:06 | 06-May-2026 | 11:26
RQ107909 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-10 | 06:00 | 2026-05-10 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 30-Apr-2026 | 07:06 | 07-May-2026 | 10:45
RQ107911 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-12 | 06:00 | 2026-05-12 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 30-Apr-2026 | 07:06 | 09-May-2026 | 16:27
RQ107912 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-13 | 06:00 | 2026-05-13 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 30-Apr-2026 | 07:06 | 10-May-2026 | 11:11
RQ107913 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-04 | 06:00 | 2026-05-04 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. Load Management need to be done by KPTCL in case of any contingency. | Auto Reclosure | 30-Apr-2026 | 07:06 | 01-May-2026 | 13:54
RQ107914 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-05 | 06:00 | 2026-05-05 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. Load Management need to be done by KPTCL in case of any contingency. | Auto Reclosure | 30-Apr-2026 | 07:06 | 02-May-2026 | 17:45
RQ107917 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-08 | 06:00 | 2026-05-08 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 30-Apr-2026 | 07:06 | 05-May-2026 | 10:24
RQ107918 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-09 | 06:00 | 2026-05-09 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 30-Apr-2026 | 07:06 | 06-May-2026 | 11:26
RQ107919 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-10 | 06:00 | 2026-05-10 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 30-Apr-2026 | 07:06 | 07-May-2026 | 10:45
RQ107921 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-12 | 06:00 | 2026-05-12 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 30-Apr-2026 | 07:06 | 09-May-2026 | 16:27
RQ107922 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-13 | 06:00 | 2026-05-13 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 30-Apr-2026 | 07:06 | 10-May-2026 | 11:11
RQ107954 | PNOCC | PGCIL SR-1 | 765KV-NIZAMABAD-WARDHA-1 | POWERGRID | C | For DSLP strengthening work (Laying of earth‑wire on unprotected area at Wardha SS | 2026-05-05 | 07:00 | 2026-05-05 | 10:00 | For DSLP strengthening work (Laying of earth‑wire on unprotected area at Wardha SS | Yes | Approved | In real time, Shutdown to be facilitated only after revival of 765kV-SOLAPUR-RAICHUR-2. Timelines need to be strictly adhered. SRPC consent received. Subject to NLDC approval and real time grid conditions. NEW-SR ATC/TTC curtailment of 600 MW in SR import. 765KV-NIZAMABAD-WARDHA-2 44% 765kV-WARORA-WARANGAL D/C 11% each 765kV-WARANGAL-MAHESHWARAM D/C 9% each 765kV-RAICHUR-KURNOOL D/C 8% each shall be in service. All other NEW-SR Inter regional lines shall be in service. Note: Shutdown of 765kV-SOLAPUR-RAICHUR-1 and 765kV-RAICHUR-KURNOOL-1 shall only be facilitated after the revival of 765KV-NIZAMABAD-WARDHA-1. | Line Circuits | 30-Apr-2026 | 16:53 | 02-May-2026 | 18:11
RQ107956 | PNOCC | PGCIL SR-2 | MAIN BAY (419) OF 400KV-MADURAI_PG-TIRUNELVELI-1 AND TIRUNELVELI - 400KV - BUS 1 @TIRUNELVELI - 400KV | PGCIL SR-2 | C | For Bay AMP works | 2026-05-04 | 09:00 | 2026-05-04 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 30-Apr-2026 | 17:24 | 01-May-2026 | 13:54
RQ107958 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-3 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-12 | 07:00 | 2026-05-12 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 30-Apr-2026 | 17:29 | 09-May-2026 | 16:27
RQ107961 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-4 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-12 | 07:00 | 2026-05-12 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 30-Apr-2026 | 17:29 | 09-May-2026 | 16:27
RQ108132 | PNOCC | PGCIL SR-1 | MAIN BAY (430) OF NAGARJUNASAGAR_PG - 400KV B/R 1 AND NAGARJUNASAGAR_PG - 400KV - BUS 2 @NAGARJUNASAGAR_PG - 400KV | PGCIL SR-1 | D | Bay AMP works. | 2026-05-05 | 07:00 | 2026-05-05 | 18:00 | Bay AMP works. | Yes | Approved | Remaining bays shall be in service. | Bay | 01-May-2026 | 15:55 | 02-May-2026 | 18:11
RQ108202 | PNOCC | PGCIL SR-2 | A/R of 400KV-KUDANKULAM-TUTICORIN_PS-2 | POWERGRID | D | To work in 400 kV Tirunelveli – Kudankulam-3 line | 2026-05-05 | 07:00 | 2026-05-05 | 18:00 | To work in 400 kV Tirunelveli – Kudankulam-3 line | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 02-May-2026 | 09:57 | 02-May-2026 | 18:11
RQ108336 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-NELLORE_AP-3 | POWERGRID | D | Live Line Replacement of OPGW and creation of Joint Box at T0121 | 2026-05-08 | 07:00 | 2026-05-08 | 18:00 | Live Line Replacement of OPGW and creation of Joint Box at T0121 | Yes | Rejected | as requested by SR1 | Auto Reclosure | 02-May-2026 | 20:04 | 05-May-2026 | 10:24
RQ108338 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-NELLORE_AP-3 | POWERGRID | D | Live Line Replacement of OPGW and creation of Joint Box at T0121 | 2026-05-10 | 07:00 | 2026-05-10 | 18:00 | Live Line Replacement of OPGW and creation of Joint Box at T0121 | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 02-May-2026 | 20:04 | 07-May-2026 | 10:51
RQ108378 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-1 | KPTCL | D | For OPGW stringing work | 2026-05-08 | 06:00 | 2026-05-08 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 03-May-2026 | 10:34 | 05-May-2026 | 10:24
RQ108379 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-1 | KPTCL | D | For OPGW stringing work | 2026-05-09 | 06:00 | 2026-05-09 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 03-May-2026 | 10:34 | 06-May-2026 | 11:26
RQ108380 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-1 | KPTCL | D | For OPGW stringing work | 2026-05-10 | 06:00 | 2026-05-10 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 03-May-2026 | 10:34 | 07-May-2026 | 10:45
RQ108382 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-1 | KPTCL | D | For OPGW stringing work | 2026-05-12 | 06:00 | 2026-05-12 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 03-May-2026 | 10:34 | 09-May-2026 | 16:27
RQ108384 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-1 | KPTCL | D | For OPGW stringing work | 2026-05-14 | 06:00 | 2026-05-14 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 03-May-2026 | 10:34 | 11-May-2026 | 10:33
RQ108386 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-1 | KPTCL | D | For OPGW stringing work | 2026-05-16 | 06:00 | 2026-05-16 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 03-May-2026 | 10:34 | 13-May-2026 | 10:12
RQ108388 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-2 | KPTCL | D | For OPGW stringing work | 2026-05-08 | 06:00 | 2026-05-08 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 03-May-2026 | 10:34 | 05-May-2026 | 10:24
RQ108389 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-2 | KPTCL | D | For OPGW stringing work | 2026-05-09 | 06:00 | 2026-05-09 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 03-May-2026 | 10:34 | 06-May-2026 | 11:26
RQ108390 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-2 | KPTCL | D | For OPGW stringing work | 2026-05-10 | 06:00 | 2026-05-10 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 03-May-2026 | 10:34 | 07-May-2026 | 10:45
RQ108392 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-2 | KPTCL | D | For OPGW stringing work | 2026-05-12 | 06:00 | 2026-05-12 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 03-May-2026 | 10:34 | 09-May-2026 | 16:27
RQ108394 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-2 | KPTCL | D | For OPGW stringing work | 2026-05-14 | 06:00 | 2026-05-14 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 03-May-2026 | 10:34 | 11-May-2026 | 10:33
RQ108396 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-2 | KPTCL | D | For OPGW stringing work | 2026-05-16 | 06:00 | 2026-05-16 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 03-May-2026 | 10:34 | 13-May-2026 | 10:12
RQ108456 | PNOCC | PGCIL SR-1 | 400KV-DONI-MUNIRABAD-1 | KPTCL | D | Line Terminal Equipment AMP Works | 2026-05-07 | 09:00 | 2026-05-07 | 18:00 | Line Terminal Equipment AMP Works | Yes | Rejected | Severe low voltages are observed at both 400kV DONI and 400kV MUNIRABAAD S/S. No N-1 for both 400kV DONI and 400kV MUNIRABAAD S/S. S/D may be availed during nominal voltage period or during weekends (Sunday) subject to no other overlapping shutdown. Planned Activities to be taken into Main OCC. | Line Circuits | 03-May-2026 | 15:50 | 04-May-2026 | 15:32
RQ108502 | PNOCC | PGCIL SR-1 | MAIN BAY (420) OF 400KV-CUDDAPAH-ANANTHPURAM-2 AND FUTURE @CUDDAPAH - 400KV | PGCIL SR-1 | C | To facilitate stringing work from AP78 to Kadapa Gantry of kadapa-Anathapur line costruction works. please extend S/D up to 9.05.2026 . | 2026-05-07 | 08:00 | 2026-05-08 | 23:59 | To facilitate stringing work from AP78 to Kadapa Gantry of kadapa-Anathapur line costruction works. please extend S/D up to 9.05.2026 . | Yes | Approved | Remaining bays shall be in service. Element under idle charged condition. Extension of any shutdown beyond two days requires prior approval from SRPC. | Bay | 03-May-2026 | 19:52 | 04-May-2026 | 13:20
RQ108503 | PNOCC | PGCIL SR-1 | MAIN BAY (419) OF 400KV-CUDDAPAH-ANANTHPURAM-2 AND CUDDAPAH - 400KV - BUS 1 @CUDDAPAH - 400KV | POWERGRID | C | To facilitate stringing work from AP78 to Kadapa Gantry of kadapa-Anathapur line costruction works. please extend S/D up to 9.05.2026 . | 2026-05-07 | 08:00 | 2026-05-08 | 23:59 | To facilitate stringing work from AP78 to Kadapa Gantry of kadapa-Anathapur line costruction works. please extend S/D up to 9.05.2026 . | Yes | Approved | Remaining bays shall be in service. Element under idle charged condition. Extension of any shutdown beyond two days requires prior approval from SRPC. | Bay | 03-May-2026 | 19:55 | 04-May-2026 | 13:20
RQ108505 | PNOCC | PGCIL SR-1 | MAIN BAY (409) OF 400KV-CUDDAPAH-ANANTHPURAM-1 AND CUDDAPAH - 400KV - BUS 2 @CUDDAPAH - 400KV | POWERGRID | C | To facilitate stringing work from AP78 to Kadapa Gantry of kadapa-Anathapur line costruction works. please extend S/D up to 9.05.2026 . | 2026-05-07 | 08:00 | 2026-05-08 | 23:59 | To facilitate stringing work from AP78 to Kadapa Gantry of kadapa-Anathapur line costruction works. please extend S/D up to 9.05.2026 . | Yes | Approved | Remaining bays shall be in service. Element under idle charged condition. Extension of any shutdown beyond two days requires prior approval from SRPC. | Bay | 03-May-2026 | 20:07 | 04-May-2026 | 13:20
RQ108506 | PNOCC | PGCIL SR-1 | TIE BAY (408) OF 400KV-CUDDAPAH-CHITTOOR-1 AND CUDDAPAH - 400KV - BUS 2 @CUDDAPAH - 400KV | PGCIL SR-1 | C | To facilitate stringing work from AP78 to Kadapa Gantry of kadapa-Anathapur line costruction works. please extend S/D up to 9.05.2026 . | 2026-05-07 | 08:00 | 2026-05-08 | 23:59 | To facilitate stringing work from AP78 to Kadapa Gantry of kadapa-Anathapur line costruction works. please extend S/D up to 9.05.2026 . | Yes | Approved | No N-1 for Main Bay 407 of 400kV-CUDDAPAH-CHITTOOR. Extension of any shutdown beyond two days requires prior approval from SRPC. | Bay | 03-May-2026 | 20:11 | 04-May-2026 | 13:20
RQ108587 | EMERGENCY | PGCIL SR-2 | 400KV-TUTICORIN_PS-DHARMAPURI-1 | POWERGRID | D | Emergency shutdown required for replacement of melted N&B at tower no 999 Y-Top ph. | 2026-05-04 | 11:45 | 2026-05-04 | 14:45 | pl approve | Yes | Approved |  | Line Circuits | 04-May-2026 | 11:33 | 04-May-2026 | 11:43
RQ108598 | EMERGENCY | PGCIL SR-1 | TIE BAY (411) OF 400KV-KURNOOL_PG-NARNOOR-1 AND 400KV-GREENKO_CPSS-KURNOOL_PG-2 @KURNOOL_PG - 400KV | PGCIL SR-1 | C | For attending air leakage from Y-Ph CB | 2026-05-05 | 09:00 | 2026-05-05 | 13:00 | For attending air leakage from Y-Ph CB | Yes | Approved | 410 and 412 bays shall be in service. | Bay | 05-May-2026 | 09:00 | 05-May-2026 | 09:07
RQ108600 | PNOCC | PGCIL SR-2 | MAIN BAY (407) OF 400KV/220KV MYSORE-ICT-2 AND MYSORE - 400KV - BUS 2 @MYSORE - 400KV | PGCIL SR-2 | D | FOR BAY AMP WORKS | 2026-05-12 | 09:00 | 2026-05-12 | 17:00 | PLEASE APPROVE | Yes | Approved | Remaining bays shall be in service. | Bay | 05-May-2026 | 13:02 | 09-May-2026 | 16:40
RQ108606 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-3 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-14 | 07:00 | 2026-05-14 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 05-May-2026 | 16:55 | 11-May-2026 | 10:33
RQ108608 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-3 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-16 | 07:00 | 2026-05-16 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 05-May-2026 | 16:55 | 13-May-2026 | 10:12
RQ108611 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-4 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-14 | 07:00 | 2026-05-14 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 05-May-2026 | 16:55 | 11-May-2026 | 10:33
RQ108613 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-4 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-16 | 07:00 | 2026-05-16 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 05-May-2026 | 16:55 | 13-May-2026 | 10:12
RQ108620 | EMERGENCY | KSPDCL | 220KV-PAVAGADA_PG-TIRUMANI2 | KSPDCL | C | To attend the hotspots on 220kV line bay isolator | 2026-05-05 | 18:00 | 2026-05-05 | 21:00 |  | Yes | Approved |  | Line Circuits | 05-May-2026 | 17:19 | 05-May-2026 | 18:45
RQ108628 | EMERGENCY | aptransco | 400KV-GUDDIGUDEM-HINDUJA-1 | APTRANSCO | C | For replacement of Broken SRC at loc No: 56(DD+12) | 2026-05-06 | 10:30 | 2026-05-06 | 16:30 | it was observed that 1N: Y-Ph SRC insulator was broken at loc No: 56(DD+12) in 400KV HNPCL-Guddigudem line-1. | Yes | Approved | Line-2 shall be in service. | Line Circuits | 06-May-2026 | 10:26 | 06-May-2026 | 10:49
RQ108629 | EMERGENCY | PGCIL SR-2 | A/R of 400KV-KALVENDAPATTU-VALLUR-1 | POWERGRID | D | AR in Non-Auto required for working in Line-2 Opportunity SD Works | 2026-05-06 | 11:09 | 2026-05-06 | 18:09 | Line-2 PNOCC SD aken by NTPC- Opportunity works in Line-2 planned for safety reasons Line-1 AR to be kept in NON_Auto. | Yes | Approved | APPROVED | Auto Reclosure | 06-May-2026 | 11:12 | 06-May-2026 | 11:21
RQ108640 | PNOCC | PGCIL SR-2 | MAIN BAY (406) OF 400KV-UDUMALPET_PG-PALAKKAD-2 AND UDUMALPET_PG - 400KV - BUS 1 @UDUMALPET_PG - 400KV | PGCIL SR-2 | D | Bay AMP works. | 2026-05-12 | 09:00 | 2026-05-12 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 06-May-2026 | 21:02 | 09-May-2026 | 16:40
RQ108641 | PNOCC | PGCIL SR-2 | MAIN BAY (412) OF 400KV-TIRUNELVELI-UDUMALPET_PG-2 AND UDUMALPET_PG - 400KV - BUS 1 @UDUMALPET_PG - 400KV | PGCIL SR-2 | C | CB operating mechanism overhauling works | 2026-05-14 | 08:00 | 2026-05-15 | 20:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 06-May-2026 | 21:02 | 11-May-2026 | 10:57
RQ108642 | PNOCC | PGCIL SR-2 | MAIN BAY (422) OF 400KV-TIRUNELVELI-UDUMALPET_PG-1 AND UDUMALPET_PG - 400KV - BUS 2 @UDUMALPET_PG - 400KV | PGCIL SR-2 | D | Bay AMP works. | 2026-05-13 | 09:00 | 2026-05-13 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 06-May-2026 | 21:02 | 10-May-2026 | 11:21
RQ108644 | EMERGENCY | kptcl | 400KV-JINDAL-BPS-4 | KPTCL | C | To replace damaged conductor between Location No.23 & 24 | 2026-05-07 | 07:00 | 2026-05-07 | 17:00 |  | Yes | Approved |  | Line Circuits | 07-May-2026 | 06:37 | 07-May-2026 | 10:09
RQ108648 | EMERGENCY | PGCIL SR-2 | TIE BAY (402) OF 400KV-KARAIKUDI-TRICHY-1 AND 400KV/230KV KARAIKUDI-ICT-1 @KARAIKUDI - 400KV | PGCIL SR-2 | C | For removal of kite thread entangled on the IPS tube of 402 89A Isolator. | 2026-05-07 | 10:00 | 2026-05-07 | 10:30 |  | Yes | Approved |  | Bay | 07-May-2026 | 09:52 | 07-May-2026 | 10:11
RQ108651 | PNOCC | PGCIL SR-2 | A/R of 400KV-KUDANKULAM-TIRUNELVELI-1 | POWERGRID | D | A/R off required for shutdown works in 400kV Tirunelveli - Kudankualm Line-II | 2026-05-12 | 07:00 | 2026-05-12 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 07-May-2026 | 10:59 | 09-May-2026 | 16:40
RQ108662 | PNOCC | kptcl | A/R of 400KV-BPS-YTPS-1 | KPTCL | D | For reconnection of copper bond from location 33 to 37 and location 28 by hotline method | 2026-05-12 | 08:00 | 2026-05-12 | 16:00 |  | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 07-May-2026 | 16:43 | 09-May-2026 | 16:43
RQ108663 | PNOCC | kptcl | A/R of 400KV-BPS-YTPS-2 | KPTCL | D | For reconnection of copper bond from location 33 to 37 and location 28 by hotline method | 2026-05-12 | 08:00 | 2026-05-12 | 16:00 |  | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 07-May-2026 | 16:43 | 09-May-2026 | 16:43
RQ108664 | PNOCC | kptcl | A/R of 400KV-BPS-YTPS-1 | KPTCL | D | For reconnection of copper bond from location 33 to 37 and location 28 by hotline method | 2026-05-13 | 08:00 | 2026-05-13 | 16:00 |  | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 07-May-2026 | 16:47 | 10-May-2026 | 11:21
RQ108665 | PNOCC | kptcl | A/R of 400KV-BPS-YTPS-2 | KPTCL | D | For reconnection of copper bond from location 33 to 37 and location 28 by hotline method | 2026-05-13 | 08:00 | 2026-05-13 | 16:00 |  | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 07-May-2026 | 16:47 | 10-May-2026 | 11:21
RQ108667 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | PID Works | 2026-05-12 | 07:00 | 2026-05-12 | 13:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 07-May-2026 | 17:09 | 09-May-2026 | 16:48
RQ108668 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | PID Works | 2026-05-13 | 07:00 | 2026-05-13 | 13:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 07-May-2026 | 17:09 | 10-May-2026 | 11:21
RQ108669 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | PID Works | 2026-05-14 | 07:00 | 2026-05-14 | 13:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 07-May-2026 | 17:09 | 11-May-2026 | 10:57
RQ108679 | PNOCC | PGCIL SR-2 | MAIN BAY (415) OF 400KV-SHOLINGANALLUR-KALVENDAPATTU-2 AND KALVENDAPATTU - 400KV - BUS 1 @KALVENDAPATTU - 400KV | PGCIL SR-2 | D | Bay AMP works. | 2026-05-13 | 09:00 | 2026-05-13 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 07-May-2026 | 19:53 | 10-May-2026 | 11:28
RQ108680 | EMERGENCY | PGCIL SR-2 | 400KV-VALLUR-ALAMATHY-1 | POWERGRID | C | Emergency SD required to replace insulator at Loc MC121 | 2026-05-08 | 10:00 | 2026-05-08 | 15:00 |  | Yes | Approved |  | Line Circuits | 08-May-2026 | 08:47 | 08-May-2026 | 12:03
RQ108682 | EMERGENCY | PGCIL SR-1 | MAIN BAY (419) OF 400KV/220KV GHANAPUR-ICT-2 AND GHANAPUR - 400KV - BUS 2 @GHANAPUR - 400KV | PGCIL SR-1 | D | To attend Hot Spot | 2026-05-08 | 10:30 | 2026-05-08 | 16:00 | To attend Hot Spot | Yes | Approved |  | Bay | 08-May-2026 | 10:19 | 08-May-2026 | 10:33
RQ108684 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-14 | 06:00 | 2026-05-14 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 08-May-2026 | 11:12 | 11-May-2026 | 10:33
RQ108686 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-16 | 06:00 | 2026-05-16 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 08-May-2026 | 11:12 | 13-May-2026 | 10:12
RQ108692 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-14 | 06:00 | 2026-05-14 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 08-May-2026 | 11:12 | 11-May-2026 | 10:33
RQ108694 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-16 | 06:00 | 2026-05-16 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 08-May-2026 | 11:12 | 13-May-2026 | 10:12
RQ108702 | PNOCC | PGCIL SR-2 | TIE BAY (417) OF 400KV-NAGAPATTNAM_PS-DHARMAPURI-1 AND DHARMAPURI - 400KV - BUS 2 @DHARMAPURI - 400KV | PGCIL SR-2 | C | Bay AMP works | 2026-05-12 | 09:30 | 2026-05-12 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 08-May-2026 | 12:40 | 09-May-2026 | 16:40
RQ108717 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | PID scanning works old insulators. | 2026-05-12 | 08:00 | 2026-05-12 | 18:00 | PID Scanning of insulator. Please approve up to 31.05.2026 | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 08-May-2026 | 19:30 | 09-May-2026 | 16:48
RQ108718 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | PID scanning works old insulators. | 2026-05-13 | 08:00 | 2026-05-13 | 18:00 | PID Scanning of insulator. Please approve up to 31.05.2026 | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 08-May-2026 | 19:30 | 10-May-2026 | 11:21
RQ108719 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | PID scanning works old insulators. | 2026-05-14 | 08:00 | 2026-05-14 | 18:00 | PID Scanning of insulator. Please approve up to 31.05.2026 | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 08-May-2026 | 19:30 | 11-May-2026 | 11:01
RQ108722 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | PID scanning works old insulators. | 2026-05-17 | 08:00 | 2026-05-17 | 18:00 | PID Scanning of insulator. Please approve up to 31.05.2026 | Yes | Approved | Concurred, subject to real time grid conditions | Auto Reclosure | 08-May-2026 | 19:30 | 14-May-2026 | 10:48
RQ108727 | PNOCC | PGCIL SR-1 | A/R of 400KV-KURNOOL_PG-NAGARJUNASAGAR_PG-1 | POWERGRID | D | Loc:75-237 Cleaning of Pollution and Bird excreta on Insulators | 2026-05-12 | 08:00 | 2026-05-12 | 18:00 | Loc:75-237 Cleaning of Pollution and Bird excreta on Insulators.Please approve up to 31.05.2026 | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 08-May-2026 | 19:34 | 09-May-2026 | 16:48
RQ108728 | PNOCC | PGCIL SR-1 | A/R of 400KV-KURNOOL_PG-NAGARJUNASAGAR_PG-1 | POWERGRID | D | Loc:75-237 Cleaning of Pollution and Bird excreta on Insulators | 2026-05-13 | 08:00 | 2026-05-13 | 18:00 | Loc:75-237 Cleaning of Pollution and Bird excreta on Insulators.Please approve up to 31.05.2026 | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 08-May-2026 | 19:34 | 10-May-2026 | 11:34
RQ108729 | PNOCC | PGCIL SR-1 | A/R of 400KV-KURNOOL_PG-NAGARJUNASAGAR_PG-1 | POWERGRID | D | Loc:75-237 Cleaning of Pollution and Bird excreta on Insulators | 2026-05-14 | 08:00 | 2026-05-14 | 18:00 | Loc:75-237 Cleaning of Pollution and Bird excreta on Insulators.Please approve up to 31.05.2026 | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 08-May-2026 | 19:34 | 11-May-2026 | 11:01
RQ108737 | PNOCC | PGCIL SR-1 | MAIN BAY (419) OF 400KV/220KV GHANAPUR-ICT-2 AND GHANAPUR - 400KV - BUS 2 @GHANAPUR - 400KV | PGCIL SR-1 | D | CT OIL SAMPLE COLLECTION FOR DGA | 2026-05-12 | 09:00 | 2026-05-12 | 14:00 | CT OIL SAMPLE COLLECTION FOR DGA | Yes | Approved | Remaining bays shall be in service. | Bay | 08-May-2026 | 19:37 | 09-May-2026 | 16:48
RQ108738 | PNOCC | PGCIL SR-2 | MAIN BAY (409) OF 400KV-NEYVELI_TS_II-SALEM-2 AND SALEM - 400KV - BUS 2 @SALEM - 400KV | PGCIL SR-2 | C | For replacement of SF6 Gas due SO2 content | 2026-05-12 | 09:30 | 2026-05-13 | 17:30 | nil | Yes | Approved | Remaining bays shall be in service. | Bay | 08-May-2026 | 20:45 | 09-May-2026 | 16:40
RQ108742 | PNOCC | NLC | NEYVELI_TS_II - 230KV - BUS 2 | NLC | C | For ST-4.ST-4 & TAQA Feeder 89B isolator rectification works | 2026-05-13 | 07:00 | 2026-05-14 | 18:00 | 230kV Bus-1 will be in service. Already shutdown was approved in Apr 22 to 24 due to assembly election could not be availed | Yes | Rejected | Planned Activities to be taken into Main OCC. | Bus | 09-May-2026 | 10:36 | 10-May-2026 | 11:49
RQ108743 | PNOCC | NLC | 230KV/6.6KV NEYVELI TS II-ST-3 | NLC | C | For attending bus isolators in ST-3 Bays | 2026-05-13 | 09:00 | 2026-05-14 | 17:00 | ST-3 is already in Transfer Bus due to Bus isolator issue | Yes | Approved | Concurred, subject to real time grid conditions. | Transformer | 09-May-2026 | 10:40 | 10-May-2026 | 11:49
RQ108745 | PNOCC | PGCIL SR-1 | MAIN BAY (418) OF 400KV/220KV GHANAPUR-ICT-1 AND GHANAPUR - 400KV - BUS 1 @GHANAPUR - 400KV | PGCIL SR-1 | D | CT OIL SAMPLE COLLECTION FOR DGA | 2026-05-13 | 09:00 | 2026-05-13 | 14:00 | CT OIL SAMPLE COLLECTION FOR DGA | Yes | Approved | Remaining bays shall be in service. | Bay | 09-May-2026 | 15:15 | 10-May-2026 | 11:21
RQ108746 | PNOCC | TGTRANSCO | 132KV-RAMAGUNDAM-MALYALAPALLI-1 | NTPC | C | For testings and bus bar commissioning works at 132kv RSS | 2026-05-13 | 10:00 | 2026-05-13 | 13:00 | Please approve L.C. | Yes | Approved | Load Management to be done by TG. | Line Circuits | 09-May-2026 | 15:57 | 10-May-2026 | 11:34
RQ108749 | PNOCC | PGCIL SR-1 | MAIN BAY (409) OF 400KV-CUDDAPAH-ANANTHPURAM-1 AND CUDDAPAH - 400KV - BUS 2 @CUDDAPAH - 400KV | POWERGRID | C | shutdown of Ananthapur #1 line bays at Kadapa for line termination works | 2026-05-13 | 08:00 | 2026-05-14 | 18:00 | shutdown of Ananthapur #1 line bays at Kadapa for line termination works | Yes | Approved | Concurred, element under idle charged condition. | Bay | 09-May-2026 | 20:19 | 10-May-2026 | 11:24
RQ108750 | PNOCC | PGCIL SR-1 | TIE BAY (408) OF 400KV-CUDDAPAH-CHITTOOR-1 AND CUDDAPAH - 400KV - BUS 2 @CUDDAPAH - 400KV | PGCIL SR-1 | C | shutdown of Ananthapur #1 line bays at Kadapa for line termination works | 2026-05-13 | 08:00 | 2026-05-14 | 18:00 | shutdown of Ananthapur #1 line bays at Kadapa for line termination works | Yes | Approved | Concurred, other element in dia under idle charged condition. | Bay | 09-May-2026 | 20:21 | 10-May-2026 | 11:24
RQ108751 | PNOCC | PGCIL SR-1 | MAIN BAY (409) OF 400KV/220KV VIJAYAWADA-ICT-2 AND VIJAYAWADA - 400KV - BUS 2 @VIJAYAWADA - 400KV | PGCIL SR-1 | D | Dewpoint measurement | 2026-05-13 | 14:00 | 2026-05-13 | 17:30 | Dewpoint measurement | Yes | Approved | Remaining bays shall be in service. Consecutive shutdowns. | Bay | 09-May-2026 | 20:56 | 10-May-2026 | 11:28
RQ108752 | PNOCC | PGCIL SR-1 | TIE BAY (408) OF 400KV/220KV VIJAYAWADA-ICT-2 AND VIJAYAWADA - 400KV B/R 3 @VIJAYAWADA - 400KV | PGCIL SR-1 | D | Dewpoint measurement | 2026-05-13 | 09:00 | 2026-05-13 | 13:00 | Dewpoint measurement | Yes | Approved | Remaining bays shall be in service. Consecutive shutdowns | Bay | 09-May-2026 | 20:56 | 10-May-2026 | 11:28
RQ108754 | EMERGENCY | aptransco | 400KV-CHITTOOR-RACHAGUNNERI-1 | APTRANSCO | C | at Loc. 302 B-ph 1No. suspension string(Double Suspension) got flashover and flashover insulator(Porcelain insulators) string fallen on ground. There is no interruption to loads as the Quad moose conductor is hanging on other string. The replacement of flashover insulators has to carried out immediately as the B-ph Quad moose conductor is hanging on single string. | 2026-05-10 | 07:45 | 2026-05-10 | 14:30 |  | Yes | Approved |  | Line Circuits | 10-May-2026 | 07:37 | 10-May-2026 | 07:52
RQ108755 | PNOCC | PGCIL SR-1 | MAIN BAY (420) OF 400KV-CUDDAPAH-ANANTHPURAM-2 AND FUTURE @CUDDAPAH - 400KV | PGCIL SR-1 | C | Shutdown of ananthapuram 2 line bay at Kadapa for line termination works | 2026-05-13 | 08:00 | 2026-05-14 | 18:00 | Shutdown of ananthapuram 2 line bay at Kadapa for line termination works | Yes | Approved | Concurred, element under idle charged condition. | Bay | 10-May-2026 | 08:59 | 10-May-2026 | 11:24
RQ108756 | PNOCC | PGCIL SR-1 | MAIN BAY (419) OF 400KV-CUDDAPAH-ANANTHPURAM-2 AND CUDDAPAH - 400KV - BUS 1 @CUDDAPAH - 400KV | POWERGRID | C | Shutdown of ananthapuram 2 line bay at Kadapa for line termination works | 2026-05-13 | 08:00 | 2026-05-14 | 18:00 | Shutdown of ananthapuram 2 line bay at Kadapa for line termination works | Yes | Approved | Concurred, element under idle charged condition. | Bay | 10-May-2026 | 08:59 | 10-May-2026 | 11:24
RQ108759 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | Live line PID testing of insulator in line | 2026-05-17 | 07:00 | 2026-05-17 | 18:00 | Nil | Yes | Approved | Concurred, subject to real time grid conditions | Auto Reclosure | 10-May-2026 | 13:18 | 14-May-2026 | 10:48
RQ108764 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | Live line PID testing of insulator in line | 2026-05-22 | 07:00 | 2026-05-22 | 18:00 | Nil | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 10-May-2026 | 13:18 | 19-May-2026 | 10:24
RQ108765 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | Live line PID testing of insulator in line | 2026-05-23 | 07:00 | 2026-05-23 | 18:00 | Nil | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 10-May-2026 | 13:18 | 20-May-2026 | 10:35
RQ108766 | EMERGENCY | aptransco | 400KV-CHITTOOR-RACHAGUNNERI-2 | APTRANSCO | C | For replacement of flashed over insulator at Loc No.302 | 2026-05-10 | 14:00 | 2026-05-10 | 19:00 |  | Yes | Approved |  | Line Circuits | 10-May-2026 | 14:00 | 10-May-2026 | 14:15
RQ108767 | PNOCC | PGCIL SR-1 | TIE BAY (420) OF 400KV/220KV GHANAPUR-ICT-2 AND 400KV/220KV GHANAPUR-ICT-4 @GHANAPUR - 400KV | PGCIL SR-1 | C | CT OIL SAMPLE COLLECTION FOR DGA | 2026-05-14 | 09:00 | 2026-05-14 | 14:00 | CT OIL SAMPLE COLLECTION FOR DGA | Yes | Approved | Remaining bays shall be in service. | Bay | 10-May-2026 | 15:34 | 11-May-2026 | 10:57
RQ108783 | EMERGENCY | PGCIL SR-2 | TIE BAY (405) OF 400KV/220KV TRIVANDRUM-ICT-3 AND TRIVANDRUM - 400KV - BUS 1 @TRIVANDRUM - 400KV | PGCIL SR-2 | C | For attending SF6 low alarm on 40552CB. | 2026-05-11 | 09:11 | 2026-05-11 | 13:15 | nil | Yes | Approved | Other Bays to remain in Service | Bay | 11-May-2026 | 09:12 | 11-May-2026 | 09:28
RQ108787 | EMERGENCY | NLC | NEYVELI_TS2_EXP - 400KV - BUS 2 | NLC | C | To attend hot spot in 401 bay GT-1 Y phase isolator. | 2026-05-11 | 10:12 | 2026-05-11 | 17:12 |  | Yes | Approved | Approved on emergency.Generation should not affected | Bus | 11-May-2026 | 10:14 | 11-May-2026 | 10:23
RQ108789 | EMERGENCY | TGTRANSCO | 400KV/13.8KV SRISAILAM_LEFT_BANK-ST-1 | TGTRANSCO | C | As all units are under LC and HTR water is emptying hence cooling water for STR-1 will not be available | 2026-05-11 | 12:45 | 2026-05-12 | 23:59 | please issue LC on STR-1 | Yes | Approved |  | Transformer | 11-May-2026 | 12:38 | 11-May-2026 | 12:47
RQ108798 | EMERGENCY | TGTRANSCO | 400KV-MAHESHWARAM_TG-SHANKARAPALLY-1 | TGTRANSCO | C | Requesting to issue emergency LC to remove the rope fallen on the line. Photo is herewith attached. | 2026-05-11 | 17:35 | 2026-05-11 | 18:00 | Please approve L.C. | Yes | Approved |  | Line Circuits | 11-May-2026 | 17:28 | 11-May-2026 | 18:06
RQ108806 | PNOCC | PGCIL SR-1 | A/R of 400KV-KHAMMAM_PG-WARANGAL-1 | POWERGRID | D | PID Scanning of Insulators | 2026-05-17 | 06:00 | 2026-05-17 | 14:00 |  | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 11-May-2026 | 19:28 | 14-May-2026 | 10:48
RQ108814 | EMERGENCY | PGCIL SR-2 | 400KV/220KV KOZHIKODE-ICT-3 | POWERGRID | C | Resin leakage is found from IV side R-ph RIP bushing. For Replacement of IV side R-ph bushing. | 2026-05-12 | 06:00 | 2026-05-12 | 23:59 | Shutdown is required upto 19.05.2026 at 22:00 Hrs. | Yes | Approved | Load management to be done by KSEB. S3 import ATC reduction of 500 MW. | Transformer | 11-May-2026 | 22:02 | 12-May-2026 | 06:01
RQ108816 | EMERGENCY | PGCIL SR-2 | 400KV-MYSORE-KOZHIKODE-2 | POWERGRID | D | Replacement of tension insulator string with CLR | 2026-05-12 | 10:00 | 2026-05-12 | 15:00 | Replacement of tension insulator string with CLR | Yes | Approved | timing to be adhered | Line Circuits | 12-May-2026 | 09:48 | 12-May-2026 | 09:51
RQ108818 | EMERGENCY | PGCIL SR-2 | A/R of 400KV-MYSORE-KOZHIKODE-1 | POWERGRID | D | to facilitate SD nature work in the other circuit | 2026-05-12 | 10:04 | 2026-05-12 | 14:02 | pl approve | Yes | Approved |  | Auto Reclosure | 12-May-2026 | 10:04 | 12-May-2026 | 10:12
RQ108825 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-1 | KPTCL | D | For OPGW stringing work | 2026-05-23 | 06:00 | 2026-05-23 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 10:47 | 20-May-2026 | 10:27
RQ108834 | PNOCC | kptcl | A/R of 220KV-MYSORE-HUNSUR-2 | KPTCL | D | For OPGW stringing work | 2026-05-23 | 06:00 | 2026-05-23 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 10:47 | 20-May-2026 | 10:27
RQ108839 | PNOCC | NLC | 400KV-NTPL-TUTICORIN_PS-2 | POWERGRID | D | RTV Silicone Coating Work | 2026-05-22 | 09:00 | 2026-05-22 | 18:00 | Approved in the 237th Outage Co-ordination Meeting from 15/05 to 16/05. Request to reschedule as the contractor could not arrive on schedule due to unforeseen circumstances. | Yes | Approved | No N-1 for NTPL. Mail communication received from NTPL to keep both units at technical minimum during the shutdown. Same need to be adhered by NTPL along with shutdown timelines. 400KV-NTPL-TUTICORIN_PS-1 100% shall be in service. | Line Circuits | 12-May-2026 | 13:03 | 19-May-2026 | 10:18
RQ108845 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-3 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-23 | 07:00 | 2026-05-23 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 13:04 | 20-May-2026 | 10:27
RQ108852 | PNOCC | kptcl | A/R of 400KV-JINDAL-BPS-4 | KPTCL | D | OPGW conductor stringing for JSW-BPS Line. OPGW pilot rope and roller assembly has been completed for a line length of 3.8 km out of 10 km from BPS station balance work to be carried out. | 2026-05-23 | 07:00 | 2026-05-23 | 14:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 12-May-2026 | 13:04 | 20-May-2026 | 10:27
RQ108855 | PNOCC | NLC | 400KV-NTPL-TUTICORIN_PS-1 | POWERGRID | D | RTV Silicone Coating Work | 2026-05-25 | 09:00 | 2026-05-25 | 18:00 | Approved in the 237th Outage Co-ordination Meeting on 14/05. Request to reschedule as the contractor could not arrive on schedule due to unforeseen circumstances. | Yes | Approved | No N-1 for NTPL. Mail communication received from NTPL to keep both units at technical minimum during the shutdown. Same need to be adhered by NTPL along with shutdown timelines. 400KV-NTPL-TUTICORIN_PS-2 100% shall be in service. | Line Circuits | 12-May-2026 | 13:08 | 22-May-2026 | 12:53
RQ108858 | PNOCC | TANTRANSCO | 765KV-THIRUVALAM-ARIYALUR-1 | TANTRANSCO | D | It is programmed to re-sagging of earth wire in 765 KV Ariyalur - Thiruvalam Circuit-I feeder between location No: 340 to 341(Kalavai Rod) by GCC-II contractor M/s. Transrail Lighting Ltd | 2026-05-17 | 09:00 | 2026-05-17 | 17:00 |  | Yes | Rejected | Planned Activities to be taken into Main OCC. | Line Circuits | 12-May-2026 | 13:30 | 14-May-2026 | 11:30
RQ108863 | PNOCC | PGCIL SR-2 | MAIN BAY (401) OF 400KV/220KV KOLAR_AC-ICT-1 AND KOLAR_AC - 400KV - BUS 1 @KOLAR_AC - 400KV | PGCIL SR-2 | D | For AMP Works | 2026-05-18 | 09:00 | 2026-05-18 | 17:00 |  | Yes | Rejected | Multiple shutdowns at the same station. | Bay | 12-May-2026 | 20:28 | 15-May-2026 | 11:41
RQ108868 | EMERGENCY | NLC | NEYVELI_TS_II - 230KV - BUS 2 | NLC | C | For attending 89B isolator of ST-3 Feeder. | 2026-05-14 | 07:00 | 2026-05-14 | 19:00 | Already ST-3 is in Transfer Bay as both isolators are having alignment issues. | Yes | Approved | No N_1 for Neyveli 230kV Generation | Bus | 13-May-2026 | 09:50 | 14-May-2026 | 10:09
RQ108869 | EMERGENCY | kptcl | 220KV-KAIGA-KADRA-1 | KPTCL | C | to attend emergency maintenance work of 89L isolator Y-PHASE Paddle REDHOT problem. | 2026-05-13 | 10:00 | 2026-05-13 | 15:00 | Emergency | Yes | Approved | 220kV Kaiga-Kodasally-Kadra connectivity shall be in service. In case of contingency, it is requested to bring Kadra unit into generation mode. LGB shall be maintained by KPTCL. Shutdown timings shall be strictly followed. | Line Circuits | 13-May-2026 | 09:52 | 13-May-2026 | 10:09
RQ108876 | EMERGENCY | PGCIL SR-2 | MAIN BAY (413) OF 400KV-TUMKUR-YELHANKA-1 AND TUMKUR - 400KV - BUS 1 @TUMKUR - 400KV | PGCIL SR-2 | C | eplacement of SF6 pressure Gauge leakage in ALSTOM make Y Phase CB due to leakage. | 2026-05-13 | 15:57 | 2026-05-13 | 17:57 | eplacement of SF6 pressure Gauge leakage in ALSTOM make Y Phase CB due to leakage. | Yes | Approved |  | Bay | 13-May-2026 | 15:59 | 13-May-2026 | 16:03
RQ108878 | PNOCC | TANTRANSCO | 400KV-SHOLINGANALLUR-KALVENDAPATTU-2 | TANTRANSCO | D | To replace the decapped disc insulator in Y ph of loc no 83 | 2026-05-17 | 06:00 | 2026-05-17 | 12:00 | 1. 400kV kalivanthapattu Sholinganallur feeder 2 will not be in service 2. 400kV Kalivathapattu Sholinganallur feeder 1 will feed entire 400kV Sholinganallur SS load There will not be any interruption of power supply | Yes | Approved | Load Management details as furnished by TN: 230KV Mylapore and Rapuram load will be transferred to 230KV Basin bridge& TNHQ -Puliyanthope. The same need to be ensured by TN prior to the shutdown by proper network rearrangement. Sensitivities for the shutdown: 400KV-SHOLINGANALLUR-KALVENDAPATTU-1 87% 230kV-SIRUSERI-KALVENDAPATTU 230kV-SIRUSERI-SHOLINGANALLUR 230kV-KALVENDAPATTU-OMEGA-SHOLINGANALLUR 230kV-SRIPERUMBADUR-THARAMANI shall be in service. In case of N-1 contingency of other parallel ckt of 400KV-SHOLINGANALLUR-KALVENDAPATTU: 230kV-KALVENDAPATTU-SIRUSERI may overload beyond its thermal limit, thus shutdown to be facilitated only when 230kV-KALVENDAPATTU-SIRUSERI line loading is within 130 MW and load at SIRUSERI station shall be less than 120 MW. In case of further overloading load management need to be done by TN subject to BHAVINI concurrence for opening one feeder of 230kV-BHAVINI-SIRUSERI in case of overloading of 230kV lines. | Line Circuits | 13-May-2026 | 17:12 | 14-May-2026 | 10:48
RQ108891 | EMERGENCY | aptransco | 132KV-PRATHAP_NAGAR-YANAM-1 | PONDICHERRY,APTRANSCO | C | For erection of 220kV Z-Type Tower underneath the crossing of 132kV Kakinada-Gollapalem circuit, Pratapnagar-Yanam circuit and 220kV SSS-Barge idle line duly temporarily diverting the existing 132kV SS, Yanam and 132kV SS, Gollapalem SS on to 220kV Kakinada SS with solid tapping. | 2026-05-14 | 08:00 | 2026-05-14 | 14:00 | On 13.05.2026, Video Conference was held by SPRC authorities with officials of CEA, SRPC, SRLDC, SLDC, Electrical Department/Yanam and APTRANSCO and concluded to avail solid tapping on Gollapalem & Yanam lines | Yes | Approved | FTC is required for normalization. As per records of the meeting on 13th May'26 the following need to be ensured: Conclusions of the Meeting are as follows: ➢ Keeping in view of the uninterrupted power supply to Yanam(Puducherry) and Gollapalem (AP), considering as a special unavoidable requirement, the forum approved the temporary tapping arrangement, as proposed by APSLDC/APTRANSCO with a suggestion to condense the duration of the S/D. ➢ The proposed shutdown of the 132kV Prathap Nagar-Yanam & 132kV Kakinada-Gollapalem feeders is approved on 14 th May’26 and 16 th May’26 from 08:00 hrs to 14:00 hrs for Z-type in-line tower erection works. ➢ APSLDC to closely and vigilantly monitor the system from an operational perspective during the temporary arrangement so as to ensure that no cascading tripping/disturbance occurs in the network. ➢ APTRANSCO/APSLDC were advised to minimize and condense the shutdown duration required for execution of the tower erection works. ➢ APSLDC/APTRANSCO shall ensure proper coordination and adequacy of all protection systems during the temporary arrangement at Kakinada end Record Notes of Special Meeting on 13.05.2026 ➢ PED was advised to review the relay settings at Yanam and reduce the operating delay, if feasible, to enable faster fault isolation and avoid extension of faults towards Kakinada. ➢ The Forum noted with serious concern that the shutdown requests submitted by APSLDC/APTRANSCO lacked adequate details, such as tapping arrangements and other essential operational information. The following operational coordination measures are suggested in line with the above conclusions: Shutdowns of the 132 kV Prathap Nagar–Yanam (Inter-State) feeder and 132 kV Kakinada–Gollapalem feeder (under APSLDC purview) are approved on 14th May’26 and 16th May’26 from 08:00 hrs to 14:00 hrs. Strict adherence to shutdown timelines shall be ensured. FTC clearance is required while charging the 132 kV Kakinada–Yanam (solid tapping)–Gollapalem S/C line while normalising on 14th and 16th May’26. The temporary tapping arrangement will remain in service for approximately 15 days until completion of the tower works. APSLDC shall ensure completion of the shutdown activities within the approved timelines and minimize the outage duration required for execution of the tower erection works. APSLDC and PED shall closely and vigilantly monitor the system during the temporary arrangement(tapping) to ensure that no cascading tripping/disturbance occurs in the network throughout the shutdown period. APSLDC/APTRANSCO shall ensure proper coordination and adequacy of all protection systems during the temporary arrangement at the Kakinada end. PED shall review the relay settings at Yanam and reduce the operating delay, if feasible, to enable faster fault isolation and avoid extension of faults towards Kakinada. APSLDC shall obtain FTC clearance for normalization of the shutdowns within the approved timelines. | Line Circuits | 13-May-2026 | 21:09 | 13-May-2026 | 22:49
RQ108894 | EMERGENCY | TANTRANSCO | A/R of 230KV-HOSUR_PG-UDANAPALLI-2 | TANTRANSCO | C | Live line permission required for replacing the flashed over discs in the Loc.51 of 230kV Shoolagiri - Uddanapally 2 Feeder by Hot lines wing in co-ordination with Hosur Lines wing | 2026-05-14 | 09:00 | 2026-05-14 | 14:00 | There will be no power supply disturbance, as the work is carried out in Live line | Yes | Approved |  | Auto Reclosure | 14-May-2026 | 08:29 | 14-May-2026 | 08:59
RQ108899 | EMERGENCY | TGTRANSCO | 400KV/11.5KV YADADRI TPP-ST-2 | TGGENCO,TGTRANSCO | C | It is requested to provide LC on 135MVA Station Transformer-2 on emergency basis for arresting oil leakage from top header. [From:14/05/2026 14:00 To 14/05/2026 17:00] | 2026-05-14 | 14:00 | 2026-05-14 | 17:00 | pl issue lc | Yes | Approved |  | Transformer | 14-May-2026 | 13:40 | 14-May-2026 | 15:03
RQ108900 | EMERGENCY | PGCIL SR-2 | HASSAN - 220KV - BUS 2 | PGCIL SR-2 | D | To attend alignment issue raised while closing the 20189A during 220 kV Bus-1 shutdown. | 2026-05-14 | 14:15 | 2026-05-14 | 17:30 | 220 kV Bus-1 shutdown is not availed. | Yes | Approved | Bus-1 shall be in service | Bus | 14-May-2026 | 14:16 | 14-May-2026 | 14:35
RQ108911 | PNOCC | PGCIL SR-1 | A/R of 400KV-KHAMMAM_PG-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-22 | 07:00 | 2026-05-22 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 14-May-2026 | 18:10 | 19-May-2026 | 10:28
RQ108912 | PNOCC | PGCIL SR-1 | A/R of 400KV-KHAMMAM_PG-NAGARJUNASAGAR_PG-1 | POWERGRID | D | For live line PID Scanning works of porcelain disc insulators | 2026-05-23 | 07:00 | 2026-05-23 | 18:00 | For live line PID Scanning works of porcelain disc insulators | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 14-May-2026 | 18:10 | 20-May-2026 | 10:35
RQ108915 | PNOCC | PGCIL SR-2 | MAIN BAY (413) OF 400KV-KALVENDAPATTU-NNTPP-1 AND KALVENDAPATTU - 400KV - BUS 2 @KALVENDAPATTU - 400KV | PGCIL SR-2 | D | AMP Works | 2026-05-18 | 09:00 | 2026-05-18 | 17:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 14-May-2026 | 20:43 | 15-May-2026 | 11:37
RQ108917 | EMERGENCY | PGCIL SR-1 | 400KV-NAGARJUNASAGAR_PG-RAMAGUNDAM-1 | POWERGRID | D | For attending HOT SPOT at 41289L | 2026-05-15 | 08:45 | 2026-05-15 | 14:30 | For attending HOT SPOT at 41289L | Yes | Approved |  | Line Circuits | 15-May-2026 | 08:46 | 15-May-2026 | 09:23
RQ108918 | EMERGENCY | TANTRANSCO | 400KV/230KV ALAMATHY-ICT-4 | TANTRANSCO | D | Hot spot rectification work in 400/230KV ICT 4 315MVA LV 89C R phase Isolator switch end clamp towards CB side and R phase Circuit Breaker Bottom pad clamp | 2026-05-15 | 10:00 | 2026-05-15 | 17:00 | During the period of shutdown 400/230KV ICT 4 315MVA will not be inservice.ICT 3 and ICT 4 will be inservice. | Yes | Approved | ICT5&6 shall be in service | Transformer | 15-May-2026 | 09:10 | 15-May-2026 | 09:25
RQ108919 | EMERGENCY | PGCIL SR-1 | MAIN BAY (415) OF 400KV/220KV ANANTHPURAM-ICT-5 AND ANANTHPURAM - 400KV - BUS 2 @ANANTHPURAM - 400KV | PGCIL SR-1 | D | For commissioning works of ICT-5 | 2026-05-15 | 11:15 | 2026-05-15 | 18:15 | For commissioning works of ICT-5 | Yes | Approved |  | Bay | 15-May-2026 | 11:17 | 15-May-2026 | 11:42
RQ108920 | EMERGENCY | PGCIL SR-1 | TIE BAY (414) OF 400KV/220KV ANANTHPURAM-ICT-5 AND ANANTHPURAM - 400KV B/R 1 @ANANTHPURAM - 400KV | PGCIL SR-1 | D | For commissioning works of ICT-5 | 2026-05-15 | 11:15 | 2026-05-15 | 18:15 | For commissioning works of ICT-5 | Yes | Approved |  | Bay | 15-May-2026 | 11:17 | 15-May-2026 | 11:42
RQ108933 | PNOCC | PGCIL SR-1 | 765KV/400KV MAHESHWARAM_PG-ICT-3 | PGCIL SR-1 | C | Already Approved in OCC 237 from 19.05.2026 to 20.05.2026 for Spare change over, to commissiong New Spare Aux. ICT Bus under SS-118 and SS-12T. But not availed due to ongoing Bus-2 Shut Down works. Please approve. | 2026-05-26 | 09:00 | 2026-05-27 | 23:00 | Already Approved in OCC 237 from 19.05.2026 to 20.05.2026 for Spare change over, to commissiong New Spare Aux. ICT Bus under SS-118 and SS-12T. But not availed due to ongoing Bus-2 Shut Down works. Please approve. | Yes | Approved | Subject to NLDC approval and real time grid conditions. Tentative NEW-SR ATC/TTC curtailment of 700 MW in SR import as per latest NLDC ready reckoner. N-1 limit for 765KV/400KV MAHESHWARAM_PG-ICTs is 1100 MW each. 765KV/400KV MAHESHWARAM_PG-ICT-1,2 28% each All 765kV/400kV NIZAMABAAD and KURNOOL ICTs shall be in service along with 400kV-RTPS-MEHBOOBNAGAR and 765KV-MAHESHWARAM_PG-KURNOOL_PG D/C. | Transformer | 15-May-2026 | 19:06 | 23-May-2026 | 18:33
RQ108934 | EMERGENCY | aptransco | 132KV-PRATHAP_NAGAR-YANAM-1 | PONDICHERRY,APTRANSCO | C | To attend the works related to formation of 2nd circuit to 132 SS KV Pratap Nagar from 220 KV SS Kakinada | 2026-05-16 | 08:00 | 2026-05-16 | 14:00 |  | Yes | Approved |  | Line Circuits | 15-May-2026 | 22:53 | 16-May-2026 | 08:16
RQ108935 | PNOCC | NTPC | TIE BAY (427) OF 400KV/220KV RAMAGUNDAM-ICT-4 AND 400KV-GHANAPUR-RAMAGUNDAM-4 @RAMAGUNDAM - 400KV | NTPC | C | Bay Pm works & equipment testings | 2026-05-22 | 08:00 | 2026-05-22 | 18:00 | Bay Pm works & equipment testings | Yes | Approved | Remaining bays shall be in service. | Bay | 16-May-2026 | 10:37 | 19-May-2026 | 10:24
RQ108939 | PNOCC | PGCIL SR-2 | MAIN BAY (428) OF 400KV-UDUMALPET_PG-PUGALUR HVDC-2 AND UDUMALPET_PG - 400KV - BUS 2 @UDUMALPET_PG - 400KV | PGCIL SR-2 | C | for AMP works. | 2026-05-22 | 09:00 | 2026-05-22 | 18:00 | for AMP works. | Yes | Approved | Remaining bays shall be in service. | Bay | 16-May-2026 | 12:29 | 19-May-2026 | 10:24
RQ108941 | PNOCC | NPCIL | KAIGA - 220KV - BUS 1 | NPCIL_KAIGA | C | String insulators replacement to be done | 2026-05-23 | 08:00 | 2026-05-24 | 20:00 | String insulators which are showing higher PID test value are to be replaced urgently in Line & SUT bays | Yes | Approved | Remaining all elements shall be in service. Approved along with 220KV-KAIGA-KADRA-1 as per the nature of work. | Bus | 16-May-2026 | 14:50 | 21-May-2026 | 12:24
RQ108946 | PNOCC | KSPDCL | PAVAGADA_PG - 220KV - BUS 3 | PGCIL SR-2 | C | Jumper connections work at Bay-230 | 2026-05-22 | 18:00 | 2026-05-23 | 02:00 |  | Yes | Approved | Remaining all elements shall be in service. | Bus | 16-May-2026 | 15:24 | 19-May-2026 | 10:24
RQ108953 | PNOCC | KSPDCL | PAVAGADA_PG - 220KV - BUS 3 | PGCIL SR-2 | C | Jumper Connection from BUS-3 to Newly constructed Bay-230/BUS 3 isolator terminals | 2026-05-25 | 18:00 | 2026-05-26 | 02:00 |  | Yes | Approved | Remaining all elements shall be in service. | Bus | 16-May-2026 | 16:35 | 22-May-2026 | 12:53
RQ108979 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | PID TESTING OF Porcelian disc insulator String | 2026-05-24 | 06:00 | 2026-05-24 | 18:00 | PID TESTING OF Porcelian disc insulator String | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 16-May-2026 | 19:24 | 21-May-2026 | 12:48
RQ108981 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | PID TESTING OF Porcelian disc insulator String | 2026-05-26 | 06:00 | 2026-05-26 | 18:00 | PID TESTING OF Porcelian disc insulator String | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 16-May-2026 | 19:24 | 23-May-2026 | 16:46
RQ108985 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | PID TESTING OF Porcelian disc insulator String | 2026-05-22 | 06:00 | 2026-05-22 | 18:00 | PID TESTING OF Porcelian disc insulator String | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 16-May-2026 | 19:27 | 19-May-2026 | 10:24
RQ108987 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | PID TESTING OF Porcelian disc insulator String | 2026-05-24 | 06:00 | 2026-05-24 | 18:00 | PID TESTING OF Porcelian disc insulator String | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 16-May-2026 | 19:27 | 21-May-2026 | 12:55
RQ108989 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | PID TESTING OF Porcelian disc insulator String | 2026-05-26 | 06:00 | 2026-05-26 | 18:00 | PID TESTING OF Porcelian disc insulator String | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 16-May-2026 | 19:27 | 23-May-2026 | 16:46
RQ108996 | PNOCC | PGCIL SR-2 | TIE BAY (417) OF 400KV-KALVENDAPATTU-PUGALUR-1 AND 400KV-SHOLINGANALLUR-KALVENDAPATTU-1 @KALVENDAPATTU - 400KV | PGCIL SR-2 | C | For Bay AMP works. | 2026-05-22 | 09:00 | 2026-05-22 | 18:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 16-May-2026 | 21:01 | 19-May-2026 | 10:28
RQ109004 | PNOCC | PGCIL SR-1 | MAIN BAY (416) OF 400KV/220KV VIJAYAWADA-ICT-1 AND VIJAYAWADA - 400KV - BUS 1 @VIJAYAWADA - 400KV | PGCIL SR-1 | C | 416 Bay Y & B-Ph CTs Replacement under Addcap along with precommissioining testing | 2026-05-22 | 00:00 | 2026-05-23 | 17:30 | 416 Bay Y & B-Ph CTs Replacement under Addcap along with precommissioining testing..Please approve S/D up to 23.05.2026 | Yes | Approved | FTC is required. Remaining bays shall be in service. | Bay | 17-May-2026 | 14:37 | 19-May-2026 | 10:24
RQ109008 | EMERGENCY | TGTRANSCO | 132KV-ASWAROAPET-T NARSAPURAM-1 | APTRANSCO,TGTRANSCO | C | For removing emergency jamail Trees b/w loc nos: 100-101 | 2026-05-18 | 09:00 | 2026-05-18 | 10:00 | this is Idle feeder and Please issue LC | Yes | Approved |  | Line Circuits | 17-May-2026 | 16:35 | 18-May-2026 | 09:57
RQ109010 | EMERGENCY | aptransco | 400KV-GUDDIGUDEM-HINDUJA-1 | APTRANSCO | C | For testing of auto reclosing operation by MRT wing after replacement of 417 Tie bay breaker at 400KV SS Guddigudem. | 2026-05-18 | 10:00 | 2026-05-18 | 13:00 | 417 Bay in open condition since 23.01.2025 | Yes | Approved | Other circuit and remaining all other lines shall be in service. | Line Circuits | 18-May-2026 | 10:12 | 18-May-2026 | 12:20
RQ109012 | PNOCC | PGCIL SR-2 | MAIN BAY (415) OF 400KV-SALEM-DHARMAPURI-1 AND SALEM - 400KV - BUS 1 @SALEM - 400KV | PGCIL SR-2 | C | For SF6 gas filtration work. | 2026-05-22 | 09:30 | 2026-05-23 | 17:30 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 18-May-2026 | 11:08 | 19-May-2026 | 10:28
RQ109013 | PNOCC | PGCIL SR-2 | A/R of 400KV-GUTTUR-HIRIYUR-1 | KPTCL | D | Auto to Non-Auto for online OPGW works | 2026-05-22 | 09:00 | 2026-05-22 | 18:00 |  | Yes | Rejected | Due to tower collapse of 400kV-KAIGA-GUTTUR D/C. | Auto Reclosure | 18-May-2026 | 12:40 | 19-May-2026 | 10:31
RQ109015 | PNOCC | PGCIL SR-2 | A/R of 400KV-GUTTUR-HIRIYUR-1 | KPTCL | D | Auto to Non-Auto for online OPGW works | 2026-05-24 | 09:00 | 2026-05-24 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. All the necessary precautions need to be taken while work as already 400kV-KAIGA-GUTTUR is under outage due to tower collapse. | Auto Reclosure | 18-May-2026 | 12:40 | 21-May-2026 | 12:48
RQ109016 | PNOCC | PGCIL SR-2 | A/R of 400KV-GUTTUR-HIRIYUR-2 | KPTCL | D | Auto to Non-Auto for online OPGW works | 2026-05-22 | 09:00 | 2026-05-22 | 18:00 |  | Yes | Rejected | Due to tower collapse of 400kV-KAIGA-GUTTUR D/C. | Auto Reclosure | 18-May-2026 | 12:40 | 19-May-2026 | 10:31
RQ109018 | PNOCC | PGCIL SR-2 | A/R of 400KV-GUTTUR-HIRIYUR-2 | KPTCL | D | Auto to Non-Auto for online OPGW works | 2026-05-24 | 09:00 | 2026-05-24 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. All the necessary precautions need to be taken while work as already 400kV-KAIGA-GUTTUR is under outage due to tower collapse. | Auto Reclosure | 18-May-2026 | 12:40 | 21-May-2026 | 12:48
RQ109021 | EMERGENCY | kptcl | 400KV-GUTTUR-HIRIYUR-2 | KPTCL | C | 400kV-Guttur-Beeranahalli-2 Bus-2 R phase PG isolator has got stuck in the middle and it was found very difficult to operate. Also the insulator stack got broken hence to open it manually | 2026-05-18 | 14:30 | 2026-05-18 | 15:30 |  | Yes | Approved | 400KV-GUTTUR-HIRIYUR-1 and 400KV-GUTTUR-NARENDRA-D/C shall be in service. | Line Circuits | 18-May-2026 | 14:23 | 18-May-2026 | 14:43
RQ109062 | EMERGENCY | PGCIL SR-2 | MAIN BAY (403) OF 400KV-SALEM-DHARMAPURI-1 AND DHARMAPURI - 400KV - BUS 2 @DHARMAPURI - 400KV | PGCIL SR-2 | D | Bay is showing zero current in all cores (core-1 to core-5) | 2026-05-18 | 17:00 | 2026-05-18 | 19:30 | Bay is showing zero current in all cores (core-1 to core-5) | Yes | Approved |  | Bay | 18-May-2026 | 16:48 | 18-May-2026 | 17:13
RQ109065 | EMERGENCY | PGCIL SR-2 | TIE BAY (419) OF 400KV-MADURAI_PG-TIRUNELVELI-1 AND 400KV-MADURAI_PG-PUGALUR-1 @MADURAI_PG - 400KV | PGCIL SR-2 | D | To rectify partially opened 41989B R‑phase Isolator | 2026-05-18 | 17:30 | 2026-05-18 | 21:30 | To rectify partially opened 41989B R‑phase Isolator | Yes | Approved |  | Bay | 18-May-2026 | 17:11 | 18-May-2026 | 17:14
RQ109067 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-GAJWEL-1 | POWERGRID | D | PID Scanning of porcelain insulators. | 2026-05-22 | 06:00 | 2026-05-22 | 18:00 | PID Scanning of porcelain insulators. | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 18-May-2026 | 17:53 | 19-May-2026 | 10:28
RQ109068 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-GAJWEL-1 | POWERGRID | D | PID Scanning of porcelain insulators. | 2026-05-23 | 06:00 | 2026-05-23 | 18:00 | PID Scanning of porcelain insulators. | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 18-May-2026 | 17:53 | 20-May-2026 | 10:35
RQ109069 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-GAJWEL-1 | POWERGRID | D | PID Scanning of porcelain insulators. | 2026-05-24 | 06:00 | 2026-05-24 | 18:00 | PID Scanning of porcelain insulators. | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 18-May-2026 | 17:53 | 21-May-2026 | 12:48
RQ109070 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-GAJWEL-1 | POWERGRID | D | PID Scanning of porcelain insulators. | 2026-05-25 | 06:00 | 2026-05-25 | 18:00 | PID Scanning of porcelain insulators. | Yes | Rejected | Multiple S/Ds at the same station. | Auto Reclosure | 18-May-2026 | 17:53 | 22-May-2026 | 12:53
RQ109071 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-GAJWEL-1 | POWERGRID | D | PID Scanning of porcelain insulators. | 2026-05-26 | 06:00 | 2026-05-26 | 18:00 | PID Scanning of porcelain insulators. | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 18-May-2026 | 17:53 | 23-May-2026 | 16:46
RQ109072 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-GAJWEL-1 | POWERGRID | D | PID Scanning of porcelain insulators. | 2026-05-27 | 06:00 | 2026-05-27 | 18:00 | PID Scanning of porcelain insulators. | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 18-May-2026 | 17:53 | 24-May-2026 | 10:26
RQ109077 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-NAGARJUNASAGAR_PG-1 | POWERGRID | D | PID Scanning of porcelain insulators. | 2026-05-22 | 06:00 | 2026-05-22 | 18:00 | PID Scanning of porcelain insulators. | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 18-May-2026 | 17:53 | 19-May-2026 | 10:28
RQ109079 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-NAGARJUNASAGAR_PG-1 | POWERGRID | D | PID Scanning of porcelain insulators. | 2026-05-24 | 06:00 | 2026-05-24 | 18:00 | PID Scanning of porcelain insulators. | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 18-May-2026 | 17:53 | 21-May-2026 | 12:48
RQ109080 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-NAGARJUNASAGAR_PG-1 | POWERGRID | D | PID Scanning of porcelain insulators. | 2026-05-25 | 06:00 | 2026-05-25 | 18:00 | PID Scanning of porcelain insulators. | Yes | Rejected | Multiple S/Ds at the same station. | Auto Reclosure | 18-May-2026 | 17:53 | 22-May-2026 | 12:53
RQ109081 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-NAGARJUNASAGAR_PG-1 | POWERGRID | D | PID Scanning of porcelain insulators. | 2026-05-26 | 06:00 | 2026-05-26 | 18:00 | PID Scanning of porcelain insulators. | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 18-May-2026 | 17:53 | 23-May-2026 | 16:46
RQ109082 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-NAGARJUNASAGAR_PG-1 | POWERGRID | D | PID Scanning of porcelain insulators. | 2026-05-27 | 06:00 | 2026-05-27 | 18:00 | PID Scanning of porcelain insulators. | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 18-May-2026 | 17:53 | 24-May-2026 | 10:26
RQ109089 | PNOCC | kptcl | A/R of 220KV-TUMKUR-KIADB-VNPURA-1 | KPTCL | D | For OPGW stringing work | 2026-05-24 | 06:00 | 2026-05-24 | 18:00 |  | Yes | Rejected | May be availed after revival of 400kV-PAVAGDA-TUMKUR D/C. | Auto Reclosure | 18-May-2026 | 21:56 | 21-May-2026 | 13:04
RQ109090 | PNOCC | kptcl | A/R of 220KV-TUMKUR-KIADB-VNPURA-1 | KPTCL | D | For OPGW stringing work | 2026-05-25 | 06:00 | 2026-05-25 | 18:00 |  | Yes | Rejected | May be availed after revival of 400kV-PAVAGADA-TUMKUR. | Auto Reclosure | 18-May-2026 | 21:56 | 22-May-2026 | 12:53
RQ109091 | PNOCC | kptcl | A/R of 220KV-TUMKUR-KIADB-VNPURA-1 | KPTCL | D | For OPGW stringing work | 2026-05-26 | 06:00 | 2026-05-26 | 18:00 |  | Yes | Rejected | May be availed after the revival of 400kV-PAVAGADA-TUMKUR D/C. | Auto Reclosure | 18-May-2026 | 21:56 | 23-May-2026 | 16:40
RQ109092 | PNOCC | kptcl | A/R of 220KV-TUMKUR-KIADB-VNPURA-1 | KPTCL | D | For OPGW stringing work | 2026-05-27 | 06:00 | 2026-05-27 | 18:00 |  | Yes | Rejected | May be availed after revival of 400kV-PAVAGADA-TUMKUR D/C. | Auto Reclosure | 18-May-2026 | 21:56 | 24-May-2026 | 10:20
RQ109098 | PNOCC | kptcl | A/R of 220KV-TUMKUR-MADHUGIRI-1 | KPTCL | D | For OPGW stringing work | 2026-05-24 | 06:00 | 2026-05-24 | 18:00 |  | Yes | Rejected | May be availed after revival of 400kV-PAVAGDA-TUMKUR D/C. | Auto Reclosure | 18-May-2026 | 21:56 | 21-May-2026 | 13:04
RQ109099 | PNOCC | kptcl | A/R of 220KV-TUMKUR-MADHUGIRI-1 | KPTCL | D | For OPGW stringing work | 2026-05-25 | 06:00 | 2026-05-25 | 18:00 |  | Yes | Rejected | May be availed after revival of 400kV-PAVAGADA-TUMKUR. | Auto Reclosure | 18-May-2026 | 21:56 | 22-May-2026 | 12:53
RQ109100 | PNOCC | kptcl | A/R of 220KV-TUMKUR-MADHUGIRI-1 | KPTCL | D | For OPGW stringing work | 2026-05-26 | 06:00 | 2026-05-26 | 18:00 |  | Yes | Rejected | May be availed after the revival of 400kV-PAVAGADA-TUMKUR D/C. | Auto Reclosure | 18-May-2026 | 21:56 | 23-May-2026 | 16:40
RQ109101 | PNOCC | kptcl | A/R of 220KV-TUMKUR-MADHUGIRI-1 | KPTCL | D | For OPGW stringing work | 2026-05-27 | 06:00 | 2026-05-27 | 18:00 |  | Yes | Rejected | May be availed after revival of 400kV-PAVAGADA-TUMKUR D/C. | Auto Reclosure | 18-May-2026 | 21:56 | 24-May-2026 | 10:20
RQ109107 | PNOCC | kptcl | A/R of 220KV-TUMKUR-MADHUGIRI-2 | KPTCL | D | For OPGW stringing work | 2026-05-24 | 06:00 | 2026-05-24 | 18:00 |  | Yes | Rejected | May be availed after revival of 400kV-PAVAGDA-TUMKUR D/C. | Auto Reclosure | 18-May-2026 | 21:56 | 21-May-2026 | 13:04
RQ109108 | PNOCC | kptcl | A/R of 220KV-TUMKUR-MADHUGIRI-2 | KPTCL | D | For OPGW stringing work | 2026-05-25 | 06:00 | 2026-05-25 | 18:00 |  | Yes | Rejected | May be availed after revival of 400kV-PAVAGADA-TUMKUR. | Auto Reclosure | 18-May-2026 | 21:56 | 22-May-2026 | 12:53
RQ109109 | PNOCC | kptcl | A/R of 220KV-TUMKUR-MADHUGIRI-2 | KPTCL | D | For OPGW stringing work | 2026-05-26 | 06:00 | 2026-05-26 | 18:00 |  | Yes | Rejected | May be availed after the revival of 400kV-PAVAGADA-TUMKUR D/C. | Auto Reclosure | 18-May-2026 | 21:56 | 23-May-2026 | 16:40
RQ109110 | PNOCC | kptcl | A/R of 220KV-TUMKUR-MADHUGIRI-2 | KPTCL | D | For OPGW stringing work | 2026-05-27 | 06:00 | 2026-05-27 | 18:00 |  | Yes | Rejected | May be availed after revival of 400kV-PAVAGADA-TUMKUR D/C. | Auto Reclosure | 18-May-2026 | 21:56 | 24-May-2026 | 10:20
RQ109147 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-23 | 06:00 | 2026-05-23 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 19-May-2026 | 16:49 | 20-May-2026 | 10:27
RQ109151 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-27 | 06:00 | 2026-05-27 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 19-May-2026 | 16:49 | 24-May-2026 | 10:20
RQ109152 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-28 | 06:00 | 2026-05-28 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 19-May-2026 | 16:49 | 25-May-2026 | 10:03
RQ109156 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-23 | 06:00 | 2026-05-23 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 19-May-2026 | 16:49 | 20-May-2026 | 10:27
RQ109160 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-27 | 06:00 | 2026-05-27 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 19-May-2026 | 16:49 | 24-May-2026 | 10:20
RQ109161 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-28 | 06:00 | 2026-05-28 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 19-May-2026 | 16:49 | 25-May-2026 | 10:03
RQ109170 | EMERGENCY | PGCIL SR-1 | 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | To remove foreign object at Loc 23 | 2026-05-19 | 19:00 | 2026-05-19 | 21:00 | To remove foreign object at Loc 23 | Yes | Approved | 400kV Hyderabad-Gajwel, 400kV Ramadugu-Gajwel D/C lines shall be in service. | Line Circuits | 19-May-2026 | 18:44 | 19-May-2026 | 18:54
RQ109172 | PNOCC | PGCIL SR-2 | MAIN BAY (424) OF 400KV-GOOTY-PAVAGADA_PG-1 AND PAVAGADA_PG - 400KV - BUS 2 @PAVAGADA_PG - 400KV | PGCIL SR-2 | D | FOR BAY AMP WORKS | 2026-05-23 | 10:00 | 2026-05-23 | 17:00 | pl approve | Yes | Rejected | Multiple shutdowns at the same station. | Bay | 19-May-2026 | 19:05 | 20-May-2026 | 10:35
RQ109173 | PNOCC | PGCIL SR-2 | TIE BAY (402) OF 400KV/220KV PAVAGADA_PG-ICT-1 AND FUTURE @PAVAGADA_PG - 400KV | PGCIL SR-2 | D | FOR BAY AMP WORKS | 2026-05-26 | 10:00 | 2026-05-26 | 17:00 | pl approve | Yes | Rejected | Multiple shutdowns at the same station. | Bay | 19-May-2026 | 19:05 | 23-May-2026 | 16:40
RQ109175 | EMERGENCY | NTPC | 400KV/220KV RAMAGUNDAM-ICT-5 | NTPC | C | for bay equipment tests | 2026-05-20 | 09:00 | 2026-05-20 | 17:24 | connected 220kv line-3 is under shutdown- occ approved | Yes | Approved |  | Transformer | 20-May-2026 | 08:28 | 20-May-2026 | 10:16
RQ109182 | PNOCC | PGCIL SR-1 | 400KV-CUDDAPAH-NAGARJUNASAGAR_PG-1 | POWERGRID | D | 400kV Ananthapuram-Kadapa D/c line construction works for OPGW diamond crossing works at locations AP77 and AP78 | 2026-05-24 | 08:00 | 2026-05-24 | 14:00 | Construction-Line over crossing works | Yes | Approved | 765kV-KURNOOL-CUDDAPAH D/C 13% each 765kV-CUDDAPAH-C'PETA D/C 12% each 400kV-NAGARJUNASAGAR-MEHBOOBNAGAR 12% 400kV-KURNOOL-NAGARJUNSAGAR 10% 400kV-KURNOOL-MAHESHWARAM D/C 10% each 400kV-GOOTY-PAVAGADA D/C All 765kV/400kV CUDDAPAH ICTs and All 400kV/220kV N'SAGAR ICTs shall be in service. | Line Circuits | 20-May-2026 | 10:40 | 21-May-2026 | 12:55
RQ109183 | PNOCC | PGCIL SR-1 | 400KV-CUDDAPAH-NAGARJUNASAGAR_PG-2 | POWERGRID | D | 400kV Ananthapuram-Kadapa D/c line construction works for OPGW diamond crossing works at locations AP77 and AP78 | 2026-05-24 | 08:00 | 2026-05-24 | 14:00 | Construction-Line over crossing works | Yes | Approved | 765kV-KURNOOL-CUDDAPAH D/C 13% each 765kV-CUDDAPAH-C'PETA D/C 12% each 400kV-NAGARJUNASAGAR-MEHBOOBNAGAR 12% 400kV-KURNOOL-NAGARJUNSAGAR 10% 400kV-KURNOOL-MAHESHWARAM D/C 10% each 400kV-GOOTY-PAVAGADA D/C All 765kV/400kV CUDDAPAH ICTs and All 400kV/220kV N'SAGAR ICTs shall be in service. | Line Circuits | 20-May-2026 | 10:40 | 21-May-2026 | 12:55
RQ109187 | EMERGENCY | aptransco | 400KV-GUDIWADA-SATTENPALLY-1 | APTRANSCO | C | for cutting the Mango tree on which harvesting is completed and is in induction zone to avoid future tripping. | 2026-05-20 | 13:00 | 2026-05-20 | 14:00 |  | Yes | Approved | Approved other line -2 shall be in service | Line Circuits | 20-May-2026 | 12:09 | 20-May-2026 | 12:38
RQ109200 | EMERGENCY | aptransco | 400KV/220KV TALARCHEVU-ICT-2 | APTRANSCO | D | For replacing damaged protection cable to avoid malopearation | 2026-05-20 | 14:30 | 2026-05-20 | 16:24 |  | Yes | Approved | ICT-1,3 shall be in service. | Transformer | 20-May-2026 | 14:26 | 20-May-2026 | 14:33
RQ109202 | EMERGENCY | UPCL | TIE BAY (405) OF 400KV-HEBBANAHALLI-UPCL-2 AND HEBBANAHALLI - 400KV - BUS 2 @HEBBANAHALLI - 400KV | KARNATAKA | C | SF6 pressure dropped to 0.78. | 2026-05-20 | 15:50 | 2026-05-20 | 17:50 | Kindly approve emergency shutdown for attending SF6 gas. | Yes | Approved | 404, 406 shall be in service | Bay | 20-May-2026 | 15:50 | 20-May-2026 | 16:58
RQ109205 | PNOCC | kptcl | 400KV-GUTTUR-BTPS-1 | KPTCL | C | For RT testing work and IPS tubes connection work line clear approval is needed | 2026-05-24 | 10:00 | 2026-05-24 | 18:00 |  | Yes | Rejected | Planned Activities to be taken into Main OCC. | Line Circuits | 20-May-2026 | 17:23 | 21-May-2026 | 12:48
RQ109223 | EMERGENCY | aptransco | 400KV-NARNOOR-JAMMALAMADUGU-1 | APTRANSCO | C | For fixing of Isolator alignment | 2026-05-20 | 23:54 | 2026-05-21 | 00:30 |  | Yes | Approved | Other lines at JAMMALAMADUGU shall be in service. | Line Circuits | 20-May-2026 | 23:58 | 21-May-2026 | 00:07
RQ109236 | EMERGENCY | PGCIL SR-2 | 400KV-TUTICORIN_PS-DHARMAPURI-2 | POWERGRID | C | Emergency SD required for attending one conductor of bundle conductors open in middle phase due to broken of jumper cone at loc no 8. | 2026-05-21 | 15:00 | 2026-05-21 | 17:00 | Line-1 will be in service. | Yes | Approved |  | Line Circuits | 21-May-2026 | 14:18 | 21-May-2026 | 15:54
RQ109239 | PNOCC | KNTL | KOPPAL - 220KV - BUS 3 | INDIGRID | D | AMP work | 2026-05-25 | 09:00 | 2026-05-25 | 18:00 | Shutdown | Yes | Approved | Remaining all elements shall be in service. | Bus | 21-May-2026 | 16:13 | 22-May-2026 | 12:53
RQ109241 | PNOCC | NTPC | BUS COUPLER BAY (203) OF KUDGI_NTPC - 220KV - BUS 1 AND KUDGI_NTPC - 220KV - BUS 2 @KUDGI_NTPC - 220KV | NTPC | C | Bph CT Oil leakage to attend the issue | 2026-05-26 | 06:00 | 2026-05-26 | 19:00 | Bph CT Oil leakage to attend the issue | Yes | Approved | Remaining bays shall be in service. | Bay | 21-May-2026 | 18:20 | 23-May-2026 | 16:46
RQ109242 | PNOCC | PGCIL SR-1 | MAIN BAY (406) OF GHANAPUR - 400KV - BUS 2 AND 400KV-GHANAPUR-RAMAGUNDAM-4 @GHANAPUR - 400KV | PGCIL SR-1 | D | 406 Bay AMP works | 2026-05-25 | 09:00 | 2026-05-25 | 18:00 | 406 Bay AMP works | Yes | Approved | Remaining bays shall be in service. | Bay | 21-May-2026 | 18:24 | 22-May-2026 | 12:53
RQ109251 | EMERGENCY | aptransco | 220KV-ASUPAKA-LOWER_SILERU-1 | APTRANSCO,TGTRANSCO | C | For replacement of damaged conductor between Bus-I & Bus-II isolator for R & Y phases. | 2026-05-22 | 06:00 | 2026-05-22 | 09:00 |  | Yes | Approved | Generation at Lower Sileru shall be monitored. | Line Circuits | 22-May-2026 | 04:42 | 22-May-2026 | 05:28
RQ109252 | EMERGENCY | TANTRANSCO | MAIN BAY (409) OF PALAVADI - 400KV B/R 1 AND PALAVADI - 400KV - BUS 1 @PALAVADI - 400KV | TANTRANSCO | D | To replace the melted expansion clamp in "409-89B - R phase isolator" | 2026-05-22 | 09:30 | 2026-05-22 | 15:00 | Bay No.409,408 is a spare bay to connect 400KV BUS 1 and 400KV BUS2 | Yes | Approved | approved | Bay | 22-May-2026 | 08:32 | 22-May-2026 | 09:24
RQ109253 | EMERGENCY | TANTRANSCO | TIE BAY (408) OF 400KV-PALAVADI-RASIPALYAM-2 AND PALAVADI - 400KV B/R 1 @PALAVADI - 400KV | TANTRANSCO | D | shutdown in 408 is also essential to isolate the 409 bay in order to replace the melted expansion clamp in "409-89B - R phase isolator" | 2026-05-22 | 09:30 | 2026-05-22 | 15:00 | Bay No.409, 408 is a spare bay to connect 400KV BUS 1 and 400KV BUS2 | Yes | Approved | lines should be in service | Bay | 22-May-2026 | 08:32 | 22-May-2026 | 09:24
RQ109258 | PNOCC | PGCIL SR-2 | MAIN BAY (401) OF 400KV/220KV KOLAR_AC-ICT-1 AND KOLAR_AC - 400KV - BUS 1 @KOLAR_AC - 400KV | PGCIL SR-2 | C | For AMP Works | 2026-05-26 | 09:00 | 2026-05-26 | 17:00 | For AMP Works | Yes | Approved | Remaining bays shall be in service. | Bay | 22-May-2026 | 12:44 | 23-May-2026 | 16:46
RQ109259 | PNOCC | PGCIL SR-2 | TIE BAY (402) OF 400KV/220KV KOLAR_AC-ICT-1 AND 400KV/220KV KOLAR_AC-ICT-2 @KOLAR_AC - 400KV | PGCIL SR-2 | C | For AMP Works | 2026-05-28 | 09:00 | 2026-05-28 | 17:00 | For AMP Works | Yes | Approved | Remaining bays shall be in service. | Bay | 22-May-2026 | 12:44 | 25-May-2026 | 10:03
RQ109267 | PNOCC | TANTRANSCO | NCPS - 400KV - BUS 1 | TANTRANSCO | D | to make open inspection in this Bay 406 | 2026-05-26 | 09:00 | 2026-05-26 | 17:00 | Safety LC at Bays 403,406,409,411 | Yes | Rejected | Planned Activities to be taken into Main OCC. | Bus | 22-May-2026 | 17:57 | 23-May-2026 | 17:10
RQ109269 | PNOCC | TGTRANSCO | 400KV-BHOOPALAPALLY-WARANGAL-2 | TGTRANSCO | C | As per TGTRANSCO request, please arrange to issue LC on KTPP-Ogulapur#2 line | 2026-05-26 | 06:00 | 2026-05-26 | 12:00 | Please approve L.C. | Yes | Rejected | Planned Activities to be taken into Main OCC. | Line Circuits | 22-May-2026 | 18:57 | 23-May-2026 | 16:49
RQ109270 | PNOCC | PGCIL SR-2 | A/R of 220KV-RENEW_SURYA_OJAS_KOPPAL_W-KOPPAL-1 | RSOPL | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 13/0 - 14/0 by Hotline Method. | 2026-05-26 | 07:00 | 2026-05-26 | 19:00 | Line Shutdowns were approved under Mid OCC_2371. However, IPP has denied to consent citing, substantial financial implication due to expected generation loss during shutdown period. In view of the commissioning target of 400 kV Gadag II - Koppal II D/C Transmission line by Mid of June 2026 and commencement of monsoon rains in North Karnataka area, it is planned to take up the powerline crossing works by hotline method. | Yes | Approved | Concurrence from the concerned RE developers is submitted by PGCIL SR-2 for taking A/R into Non-Auto mode dated 26.05.2026. It is to be noted that there is no N-1 redundancy available for the RE generating plants connected at 400kV KOPPAL PSS. Further, it is to be duly noted that the peak wind season in the Southern Region has already commenced, and multiple line tripping have been observed in nearby grid elements during the past few days. Already 400kV-KOPPAL-GADAG D/C is in tripped condition due to tower collapse. | Auto Reclosure | 22-May-2026 | 22:10 | 23-May-2026 | 16:40
RQ109277 | PNOCC | PGCIL SR-2 | A/R of 220KV-KOPPAL-RENEW_SURYA_KOPPAL-1 | RENEW POWER PVT LTD | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 13/0 - 14/0 by Hotline Method. | 2026-05-26 | 07:00 | 2026-05-26 | 19:00 | Line Shutdowns were approved under Mid OCC_2371. However, IPP has denied to consent citing, substantial financial implication due to expected generation loss during shutdown period. In view of the commissioning target of 400 kV Gadag II - Koppal II D/C Transmission line by Mid of June 2026 and commencement of monsoon rains in North Karnataka area, it is planned to take up the powerline crossing works by hotline method. | Yes | Approved | Concurrence from the concerned RE developers is submitted by PGCIL SR-2 for taking A/R into Non-Auto mode dated 26.05.2026. It is to be noted that there is no N-1 redundancy available for the RE generating plants connected at 400kV KOPPAL PSS. Further, it is to be duly noted that the peak wind season in the Southern Region has already commenced, and multiple line tripping have been observed in nearby grid elements during the past few days. Already 400kV-KOPPAL-GADAG D/C is in tripped condition due to tower collapse. | Auto Reclosure | 22-May-2026 | 22:10 | 23-May-2026 | 16:40
RQ109289 | EMERGENCY | aptransco | 400KV/220KV JAMMALAMADUGU-ICT-3 | APTRANSCO | C | To removal of bird nest on 400/220KV 500MVA ICT-II | 2026-05-23 | 17:00 | 2026-05-23 | 18:00 | No Interruption | Yes | Approved | Approved. NO RE curtailment to be done. | Transformer | 23-May-2026 | 16:44 | 23-May-2026 | 16:49
RQ109290 | EMERGENCY | aptransco | 400KV/220KV JAMMALAMADUGU-ICT-2 | APTRANSCO | C | to remove bird nest | 2026-05-23 | 18:00 | 2026-05-23 | 19:00 | no interruption | Yes | Approved | OTHER ICTS SHALL BE IN SERVICE. NO RE CURTAILMENT TO BE DONE. | Transformer | 23-May-2026 | 18:00 | 23-May-2026 | 18:07
RQ109292 | EMERGENCY | TGTRANSCO | 400KV-KETHIREDDYPALLY-SHANKARAPALLY-2 | TGTRANSCO | C | For replacement of Y-Ph CVT clamp | 2026-05-23 | 19:43 | 2026-05-23 | 21:00 | Please approve LC | Yes | Approved | Line-1 shall be in service. | Line Circuits | 23-May-2026 | 19:45 | 23-May-2026 | 20:23
RQ109293 | PNOCC | kptcl | MAIN BAY (407) OF 400KV-HASSAN-HEBBANAHALLI-2 AND HEBBANAHALLI - 400KV - BUS 1 @HEBBANAHALLI - 400KV | KARNATAKA | C | For breaker testing by RT wing | 2026-05-27 | 10:00 | 2026-05-27 | 16:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 23-May-2026 | 22:48 | 24-May-2026 | 10:20
RQ109294 | EMERGENCY | kseb | 132KV-KUZHITHURAI-PARASSALA-1 | KSEB,TANTRANSCO | D | EMERGENCY Permit to Work to carry out rectification work of hot-spot observed in the Y-Phase of the Line Isolator on 110kV 1PRKZ Feeder. | 2026-05-24 | 07:30 | 2026-05-24 | 15:00 | LOAD CAN BE MANAGED BY KSEBL | Yes | Approved | Load Management need to be done by TN and KSEB. Approved in emergency due to hot spots. | Line Circuits | 24-May-2026 | 07:21 | 24-May-2026 | 08:14
RQ109296 | PNOCC | kseb | 400KV/220KV MADAKKATHARA-ICT-1 | KSEB | D | FOR CONDUCTING RLA STUDY | 2026-05-28 | 08:00 | 2026-05-28 | 17:00 | The shutdown is rejected today by SRLDC due to the unavailability of Kozhikode ICT#3 | Yes | Approved | Load Management need to be done by KSEB. S3- 300 MW import ATC reduction. N-1 limit for MADAKKATHARA ICTs is 235 MW each. 400KV/220KV MADAKATHARA-ICT-2,3 25% each All PALAKKAD and KOZHIKODE ICTs shall be in service along with 220KV-ELANKUR-AREACODE-1 10% 220KV-ELAPULLY-MADAKATHARA-1 9% 220KV-PALAKKAD(KL)-MADAKATHARA-1 9% 220KV-MADAKATHARA-LOWER PERIYAR-1 8% 400KV-KOZHIKODE-MADAKKATHARA D/C 7% each 220KV-KOZHIKODE-AREACODE D/C 4% each. Approved shutdown in OCC, could not be availed due to system constraints. | Transformer | 24-May-2026 | 12:30 | 25-May-2026 | 10:03
RQ109304 | EMERGENCY | mepl | 400KV-NELLORE_PG-NPS-1 | POWERGRID | C | 402 CB Bphase arm connection Hot spot observed - 112deg. Now it is in raising trend & Tower No- 81 Rphase jumper connection temperature 83deg found | 2026-05-25 | 09:45 | 2026-05-25 | 16:33 | Need to attend immediately | Yes | Approved | Other circuit shall be in service | Line Circuits | 25-May-2026 | 09:38 | 25-May-2026 | 10:02
RQ109311 | EMERGENCY | PGCIL SR-1 | 400KV/220KV KURNOOL_PG_III-ICT-2 | PGCIL SR-1 | C | Emergency S/D to remove foreign material | 2026-05-25 | 11:45 | 2026-05-25 | 14:00 |  | Yes | Approved | Other ICTs shall be in service. No RE curtailment. | Transformer | 25-May-2026 | 11:35 | 25-May-2026 | 12:06
RQ109316 | PNOCC | PGCIL SR-2 | TIE BAY (411) OF 400KV-GUTTUR-HIRIYUR-1 AND 400KV-NELAMANGALA-HIRIYUR-1 @HIRIYUR - 400KV | PGCIL SR-2 | C | SF6 gas leakage arrest works | 2026-05-29 | 08:30 | 2026-05-30 | 18:00 | SF6 gas leakage arrest works | Yes | Approved | Remaining bays shall be in service. | Bay | 25-May-2026 | 12:32 | 26-May-2026 | 16:50
RQ109318 | EMERGENCY | NLC | 230KV-NEYVELI_TS_II-NLC MINES-3 | NLC | C | sag tightness in between tower no 07 and 08 of MF-III FEEDER due to diversion of lignite transportation road | 2026-05-26 | 06:00 | 2026-05-26 | 18:00 |  | Yes | Approved | Power supply to mines may be taken care with alternate feeders | Line Circuits | 25-May-2026 | 13:55 | 26-May-2026 | 07:12
RQ109322 | PNOCC | kptcl | MAIN BAY (409) OF 400KV/220KV NELAMANGALA-ICT-2 AND NELAMANGALA - 400KV - BUS 2 @NELAMANGALA - 400KV | KPTCL | C | For breaker testing by RT wing | 2026-05-29 | 10:00 | 2026-05-29 | 16:00 |  | Yes | Approved | Remaining bays shall be in service and subject to real time voltage conditions in near vicinity. | Bay | 25-May-2026 | 17:02 | 26-May-2026 | 16:50
RQ109361 | PNOCC | PGCIL SR-1 | TIE BAY (405) OF 400KV-GOOTY-PAVAGADA_PG-2 AND GOOTY - 400KV - BUS 1 @GOOTY - 400KV | PGCIL SR-1 | D | Bay AMP works. | 2026-05-29 | 09:00 | 2026-05-29 | 18:00 | Bay AMP works. | Yes | Approved | Remaining bays shall be in service. | Bay | 25-May-2026 | 21:23 | 26-May-2026 | 16:50
RQ109362 | EMERGENCY | aptransco | 400KV-NELLORE_AP-SEIL_P2-1 | ANDHRA PRADESH,APTRANSCO | C | for attending hot spot on 789L Line isolator B-phase (temp: 120°). Concurrence was taken from M/s SEIL. | 2026-05-26 | 07:10 | 2026-05-26 | 09:00 |  | Yes | Approved | 400KV-KRISHNAPATNAM-RACHAGUNNERI-1 shall be facilitated after revival of this line. no N-1 for evacuation of SEIL P2 U2 | Line Circuits | 26-May-2026 | 07:03 | 26-May-2026 | 07:29
RQ109363 | EMERGENCY | kptcl | 400KV-JINDAL-BPS-3 | KPTCL | C | for checking and replacement of the 400kV GIS Line #3 breaker trip coil and pole discrepancy operation timer. | 2026-05-26 | 09:32 | 2026-05-26 | 18:32 | Emergency | Yes | Approved | Other circuit shall be in service. Load/generation management to be done by JSW to control loading on ICTs. | Line Circuits | 26-May-2026 | 09:34 | 26-May-2026 | 09:47
RQ109406 | PNOCC | PGCIL SR-2 | 400KV-HOSUR_PG-SOMANAHALLI-1 | POWERGRID | D | AMP Works and attending shutdown nature defects in the line. | 2026-05-30 | 09:00 | 2026-05-30 | 17:00 | Approved under OCC 237 on 6th of May. Deferred due to low voltages in Bangalore area with remark to avail on weekend. Kindly approve. | Yes | Rejected | Multiple shutdowns having overlapping sensitivity on HOODY ICTs which are already crossing their N-1 limits. 400KV-MYLASANDRA-KOLAR_AC-1 20% 400KV-BIDADI_PG-SOMANAHALLI D/C 19% each 400KV-KOLAR_AC-HOODY D/C 15% each 400KV-DHARMAPURI-SOMANAHALLI D/C 13% | Line Circuits | 26-May-2026 | 21:47 | 27-May-2026 | 12:37
RQ109407 | PNOCC | kseb | 220KV-POTHENCODE-TRIVANDRUM-1 | KSEB | D | For the rectification of damaged portion of optic fiber link between Trivandrum PGCIL and Trivandrum KSEBL (Pothencode).. | 2026-05-30 | 08:00 | 2026-05-30 | 17:00 | A/R | Yes | Rejected | Only A/R off need to be applied. | Auto Reclosure | 26-May-2026 | 23:22 | 27-May-2026 | 12:00
RQ109408 | PNOCC | kseb | A/R of 220KV-POTHENCODE-TRIVANDRUM-2 | KSEB | D | For rectifying the damaged portion of optic fiber link between TrivandrumPGCIL and Trivandrum KSEBL (Pothencode) | 2026-05-30 | 08:00 | 2026-05-30 | 17:00 | A/R | Yes | Approved | Concurred, subject to real time grid conditions. Load Management need to be done by KSEB in case of any contingency. | Auto Reclosure | 26-May-2026 | 23:29 | 27-May-2026 | 12:00
RQ109409 | PNOCC | kseb | A/R of 220KV-POTHENCODE-TRIVANDRUM-3 | KSEB | D | For rectifying the damaged portion of optic fiber link between Trivandrum PGCIL and Trivandrum KSEBL (Pothencode} | 2026-05-30 | 08:00 | 2026-05-30 | 17:00 | A/R | Yes | Approved | Concurred, subject to real time grid conditions. Load Management need to be done by KSEB in case of any contingency. | Auto Reclosure | 26-May-2026 | 23:33 | 27-May-2026 | 12:00
RQ109410 | PNOCC | kseb | A/R of 220KV-POTHENCODE-TRIVANDRUM-4 | KSEB | D | For rectifying the damaged portion of optic fiber link between Trivandrum PGCIL and Trivandrum KSEBL (Pothencode} | 2026-05-30 | 08:00 | 2026-05-30 | 17:00 | A/R - Feeder renamed as Trivandrum New Katakada SC Line w.e.f 21.05.2026 | Yes | Rejected | Shutdown to be applied for A/R of 220kV-TRIVANDRUM - NEWKATAKADA | Auto Reclosure | 26-May-2026 | 23:42 | 27-May-2026 | 12:00
RQ109415 | EMERGENCY | kptcl | 400KV-NELAMANGALA-HASSAN-1 | PGCIL SR-1 | C | For testing of breaker by RT staff (only 407 bay) | 2026-05-27 | 11:45 | 2026-05-27 | 16:00 |  | Yes | Rejected |  | Bay | 27-May-2026 | 11:42 | 27-May-2026 | 11:57
RQ109488 | EMERGENCY | kptcl | DONI - 400KV B/R 1 | KPTCL | C | for emergency testing | 2026-05-27 | 19:45 | 2026-05-27 | 20:00 | emergency | Yes | Approved | Tests are pending, Not ready for charging. | Bus Reactor | 27-May-2026 | 19:32 | 27-May-2026 | 20:36
RQ109510 | EMERGENCY | PGCIL SR-2 | 400KV-KALVENDAPATTU-VALLUR-2 | POWERGRID | D | To replace heavily polluted pilot insulator of ckt-1 which is currently under shutdown. Emergency shutdown below circuit (Ckt--2) is required for working on top circuit (Ckt-1). This is a multi circuit tower. | 2026-05-28 | 13:10 | 2026-05-28 | 18:10 | pl approve | Yes | Approved | All the lines connected to Vallur station shall be in service. | Line Circuits | 28-May-2026 | 13:07 | 28-May-2026 | 14:36
RQ109511 | EMERGENCY | PGCIL SR-2 | A/R of 400KV-VALLUR-ALAMATHY-1 | POWERGRID | C | To facilitate insulator replacement works in 400kV Vallur-Kalivandapattu Ckt-1 as this is a multi-circuit tower. | 2026-05-28 | 13:12 | 2026-05-28 | 18:10 | pl approve | Yes | Rejected | Approved on emergency | Auto Reclosure | 28-May-2026 | 13:12 | 28-May-2026 | 14:36
RQ109512 | EMERGENCY | PGCIL SR-2 | A/R of 400KV-VALLUR-ALAMATHY-2 | POWERGRID | C | To facilitate insulator replacement works in 400kV Vallur-Kalivandapattu Ckt-1 as this is a multi-circuit tower. | 2026-05-28 | 13:12 | 2026-05-28 | 18:10 | pl approve | Yes | Rejected | Approved on emergency | Auto Reclosure | 28-May-2026 | 13:12 | 28-May-2026 | 14:36
RQ109542 | EMERGENCY | NTPC | 400KV-BHADRAVATHI-RAMAGUNDAM-2 | POWERGRID | C | minor air ionisation observed at wavetrap carona ring connection area | 2026-05-29 | 09:56 | 2026-05-29 | 13:00 | line shutdown required for 3 hrs | Yes | Approved | Line-1 shall be in service. | Line Circuits | 29-May-2026 | 10:06 | 29-May-2026 | 11:46
RQ109545 | EMERGENCY | PGCIL SR-2 | A/R of 400KV-KALVENDAPATTU-VALLUR-2 | POWERGRID | D | 400kV Vallur-Kalivandapattu (VLR-KVPT) Ckt-1 is under breakdown. Utilizing this opportunity we're planning to replace suspected CLR Tension & Pilot insulators in 400kV D/C tower loc121/0. For safety purpose and to facilitate the subject works, it is requested to arrange for non-auto mode of other charged circuit I.e., VLR-KVPT Ckt-2 | 2026-05-29 | 10:55 | 2026-05-29 | 19:00 | pl approve | Yes | Approved | Approved | Auto Reclosure | 29-May-2026 | 10:54 | 29-May-2026 | 11:09
RQ109565 | EMERGENCY | aptransco | CHITTOOR - 400KV B/R 1 | APTRANSCO | C | for detailed inspection and rectification of abnormal hissing noise in R phase main Isolator (1289-A). | 2026-05-29 | 11:12 | 2026-05-29 | 14:12 |  | Yes | Approved |  | Bus Reactor | 29-May-2026 | 11:14 | 29-May-2026 | 11:38
RQ108951 | PNOCC | KSPDCL | PAVAGADA_PG - 220KV - BUS 4 | PGCIL SR-2 | C | To conduct Stability test for Extended BUS 4 | 2026-05-27 | 18:00 | 2026-05-27 | 23:59 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Bus | 16-May-2026 | 16:15 | 24-May-2026 | 10:26
RQ108982 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | PID TESTING OF Porcelian disc insulator String | 2026-05-27 | 06:00 | 2026-05-27 | 18:00 | PID TESTING OF Porcelian disc insulator String | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 16-May-2026 | 19:24 | 24-May-2026 | 10:26
RQ108984 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | PID TESTING OF Porcelian disc insulator String | 2026-05-29 | 06:00 | 2026-05-29 | 18:00 | PID TESTING OF Porcelian disc insulator String | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 16-May-2026 | 19:24 | 26-May-2026 | 10:46
RQ108990 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | PID TESTING OF Porcelian disc insulator String | 2026-05-27 | 06:00 | 2026-05-27 | 18:00 | PID TESTING OF Porcelian disc insulator String | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 16-May-2026 | 19:27 | 24-May-2026 | 10:26
RQ108992 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | PID TESTING OF Porcelian disc insulator String | 2026-05-29 | 06:00 | 2026-05-29 | 18:00 | PID TESTING OF Porcelian disc insulator String | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 16-May-2026 | 19:27 | 26-May-2026 | 10:46
RQ109074 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-GAJWEL-1 | POWERGRID | D | PID Scanning of porcelain insulators. | 2026-05-29 | 06:00 | 2026-05-29 | 18:00 | PID Scanning of porcelain insulators. | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 18-May-2026 | 17:53 | 26-May-2026 | 10:46
RQ109075 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-GAJWEL-1 | POWERGRID | D | PID Scanning of porcelain insulators. | 2026-05-30 | 06:00 | 2026-05-30 | 18:00 | PID Scanning of porcelain insulators. | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 18-May-2026 | 17:53 | 27-May-2026 | 11:21
RQ109084 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-NAGARJUNASAGAR_PG-1 | POWERGRID | D | PID Scanning of porcelain insulators. | 2026-05-29 | 06:00 | 2026-05-29 | 18:00 | PID Scanning of porcelain insulators. | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 18-May-2026 | 17:53 | 26-May-2026 | 10:46
RQ109085 | PNOCC | PGCIL SR-1 | A/R of 400KV-GHANAPUR-NAGARJUNASAGAR_PG-1 | POWERGRID | D | PID Scanning of porcelain insulators. | 2026-05-30 | 06:00 | 2026-05-30 | 18:00 | PID Scanning of porcelain insulators. | Yes | Rejected | Multiple shutdowns at the same station. | Auto Reclosure | 18-May-2026 | 17:53 | 27-May-2026 | 11:21
RQ109094 | PNOCC | kptcl | A/R of 220KV-TUMKUR-KIADB-VNPURA-1 | KPTCL | D | For OPGW stringing work | 2026-05-29 | 06:00 | 2026-05-29 | 18:00 |  | Yes | Rejected | May be availed after the revival of 400kV-PAVAGDA-TUMKUR D/C. | Auto Reclosure | 18-May-2026 | 21:56 | 26-May-2026 | 10:35
RQ109103 | PNOCC | kptcl | A/R of 220KV-TUMKUR-MADHUGIRI-1 | KPTCL | D | For OPGW stringing work | 2026-05-29 | 06:00 | 2026-05-29 | 18:00 |  | Yes | Rejected | May be availed after the revival of 400kV-PAVAGDA-TUMKUR D/C. | Auto Reclosure | 18-May-2026 | 21:56 | 26-May-2026 | 10:35
RQ109112 | PNOCC | kptcl | A/R of 220KV-TUMKUR-MADHUGIRI-2 | KPTCL | D | For OPGW stringing work | 2026-05-29 | 06:00 | 2026-05-29 | 18:00 |  | Yes | Rejected | May be availed after the revival of 400kV-PAVAGDA-TUMKUR D/C. | Auto Reclosure | 18-May-2026 | 21:56 | 26-May-2026 | 10:35
RQ109153 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-29 | 06:00 | 2026-05-29 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 19-May-2026 | 16:49 | 26-May-2026 | 10:35
RQ109155 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-1 | KPTCL | D | For OPGW stringing work | 2026-05-31 | 06:00 | 2026-05-31 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 19-May-2026 | 16:49 | 28-May-2026 | 10:29
RQ109162 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-29 | 06:00 | 2026-05-29 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 19-May-2026 | 16:49 | 26-May-2026 | 10:35
RQ109164 | PNOCC | kptcl | A/R of 220KV-KOLAR_AC-T GOLLAHALLI-2 | KPTCL | D | For OPGW stringing work | 2026-05-31 | 06:00 | 2026-05-31 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 19-May-2026 | 16:49 | 28-May-2026 | 10:29
RQ109212 | PNOCC | PGCIL SR-2 | 220KV-HASSAN-YECHANAHALLI-1 | KPTCL | D | For terminal Equipment AMP Works | 2026-05-30 | 09:00 | 2026-05-30 | 18:00 | For terminal Equipment AMP Works | Yes | Rejected | Planned Activities to be taken into Main OCC. | Line Circuits | 20-May-2026 | 19:33 | 27-May-2026 | 11:26
RQ109260 | PNOCC | PGCIL SR-1 | 765KV-KURNOOL_PG-NPS-1 | POWERGRID | D | Already approved in OCC 237 on 25.05.2026 for Jumper Guy Anchoring works. But not availed due to work exigencies. May please approve | 2026-05-29 | 07:00 | 2026-05-29 | 19:00 | Already approved in OCC 237 on 25.05.2026 for Jumper Guy Anchoring works. But not availed due to work exigencies. May please approve | Yes | Approved | 765KV-NPS-KURNOOL_PG-2 56% 400KV-THIRUVALAM-NPS D/C 12% each 400KV-NPS-GOOTY D/C 10% each 400KV-KURNOOL_PG-NARNOOR D/C 4% each All GOOTY ICTs shall be in service. Subject to NLDC approval and real time grid conditions. | Line Circuits | 22-May-2026 | 16:01 | 26-May-2026 | 17:43
RQ109261 | PNOCC | PGCIL SR-1 | 765KV-KURNOOL_PG-NPS-2 | POWERGRID | D | Already approved in OCC 237 on 26.05.2026 for Jumper Guy Anchoring works. But not availed due to work exigencies. May please approve | 2026-05-30 | 07:00 | 2026-05-30 | 19:00 | Already approved in OCC 237 on 26.05.2026 for Jumper Guy Anchoring works. But not availed due to work exigencies. May please approve | Yes | Approved | Subject to NLDC approval. 765KV-NPS-KURNOOL_PG-2 56% 400KV-THIRUVALAM-NPS D/C 12% each 400KV-NPS-GOOTY D/C 10% each 400KV-KURNOOL_PG-NARNOOR D/C 4% each All GOOTY ICTs shall be in service. | Line Circuits | 22-May-2026 | 16:01 | 27-May-2026 | 11:21
RQ109268 | PNOCC | TANTRANSCO | NCPS - 400KV - BUS 1 | TANTRANSCO | D | to make open inspection in this Bay 406 | 2026-05-27 | 09:00 | 2026-05-27 | 17:00 | Safety LC at Bays 403,406,409,411 | Yes | Rejected | Planned Activities to be taken into Main OCC. | Bus | 22-May-2026 | 17:57 | 24-May-2026 | 10:44
RQ109271 | PNOCC | PGCIL SR-2 | A/R of 220KV-RENEW_SURYA_OJAS_KOPPAL_W-KOPPAL-1 | RSOPL | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 13/0 - 14/0 by Hotline Method. | 2026-05-27 | 07:00 | 2026-05-27 | 19:00 | Line Shutdowns were approved under Mid OCC_2371. However, IPP has denied to consent citing, substantial financial implication due to expected generation loss during shutdown period. In view of the commissioning target of 400 kV Gadag II - Koppal II D/C Transmission line by Mid of June 2026 and commencement of monsoon rains in North Karnataka area, it is planned to take up the powerline crossing works by hotline method. | Yes | Approved | Concurrence from the concerned RE developers is submitted by PGCIL SR-2 for taking A/R into Non-Auto mode through mail communication dated 26.05.20206. Further, there is no N-1 redundancy available for the RE generating plants connected at 400kV KOPPAL PSS. Also, it is to be duly noted that the peak wind season in the Southern Region has already commenced, and multiple line tripping have been observed in nearby grid elements during the past few days. 400kV-KOPPAL-GADAG D/C is already under shutdown due to tower collapse. | Auto Reclosure | 22-May-2026 | 22:10 | 24-May-2026 | 10:29
RQ109273 | PNOCC | PGCIL SR-2 | A/R of 220KV-RENEW_SURYA_OJAS_KOPPAL_W-KOPPAL-1 | RSOPL | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 13/0 - 14/0 by Hotline Method. | 2026-05-29 | 07:00 | 2026-05-29 | 19:00 | Line Shutdowns were approved under Mid OCC_2371. However, IPP has denied to consent citing, substantial financial implication due to expected generation loss during shutdown period. In view of the commissioning target of 400 kV Gadag II - Koppal II D/C Transmission line by Mid of June 2026 and commencement of monsoon rains in North Karnataka area, it is planned to take up the powerline crossing works by hotline method. | Yes | Approved | Concurrence from the concerned RE developers is submitted by PGCIL SR-2 for taking A/R into Non-Auto mode through mail communication dated 26.05.20206. Further, there is no N-1 redundancy available for the RE generating plants connected at 400kV KOPPAL PSS. Also, it is to be duly noted that the peak wind season in the Southern Region has already commenced, and multiple line tripping have been observed in nearby grid elements during the past few days. 400kV-KOPPAL-GADAG D/C is already under shutdown due to tower collapse. | Auto Reclosure | 22-May-2026 | 22:10 | 26-May-2026 | 10:35
RQ109275 | PNOCC | PGCIL SR-2 | A/R of 220KV-RENEW_SURYA_OJAS_KOPPAL_W-KOPPAL-1 | RSOPL | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 13/0 - 14/0 by Hotline Method. | 2026-05-31 | 07:00 | 2026-05-31 | 19:00 | Line Shutdowns were approved under Mid OCC_2371. However, IPP has denied to consent citing, substantial financial implication due to expected generation loss during shutdown period. In view of the commissioning target of 400 kV Gadag II - Koppal II D/C Transmission line by Mid of June 2026 and commencement of monsoon rains in North Karnataka area, it is planned to take up the powerline crossing works by hotline method. | Yes | Approved | Concurrence from the concerned RE developers is submitted by PGCIL SR-2 for taking A/R into Non-Auto mode through mail communication dated 26.05.20206. Further, there is no N-1 redundancy available for the RE generating plants connected at 400kV KOPPAL PSS. Also, it is to be duly noted that the peak wind season in the Southern Region has already commenced, and multiple line tripping have been observed in nearby grid elements during the past few days. 400kV-KOPPAL-GADAG D/C is already under shutdown due to tower collapse. | Auto Reclosure | 22-May-2026 | 22:10 | 28-May-2026 | 10:29
RQ109278 | PNOCC | PGCIL SR-2 | A/R of 220KV-KOPPAL-RENEW_SURYA_KOPPAL-1 | RENEW POWER PVT LTD | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 13/0 - 14/0 by Hotline Method. | 2026-05-27 | 07:00 | 2026-05-27 | 19:00 | Line Shutdowns were approved under Mid OCC_2371. However, IPP has denied to consent citing, substantial financial implication due to expected generation loss during shutdown period. In view of the commissioning target of 400 kV Gadag II - Koppal II D/C Transmission line by Mid of June 2026 and commencement of monsoon rains in North Karnataka area, it is planned to take up the powerline crossing works by hotline method. | Yes | Approved | Concurrence from the concerned RE developers is submitted by PGCIL SR-2 for taking A/R into Non-Auto mode through mail communication dated 26.05.20206. Further, there is no N-1 redundancy available for the RE generating plants connected at 400kV KOPPAL PSS. Also, it is to be duly noted that the peak wind season in the Southern Region has already commenced, and multiple line tripping have been observed in nearby grid elements during the past few days. 400kV-KOPPAL-GADAG D/C is already under shutdown due to tower collapse. | Auto Reclosure | 22-May-2026 | 22:10 | 24-May-2026 | 10:29
RQ109280 | PNOCC | PGCIL SR-2 | A/R of 220KV-KOPPAL-RENEW_SURYA_KOPPAL-1 | RENEW POWER PVT LTD | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 13/0 - 14/0 by Hotline Method. | 2026-05-29 | 07:00 | 2026-05-29 | 19:00 | Line Shutdowns were approved under Mid OCC_2371. However, IPP has denied to consent citing, substantial financial implication due to expected generation loss during shutdown period. In view of the commissioning target of 400 kV Gadag II - Koppal II D/C Transmission line by Mid of June 2026 and commencement of monsoon rains in North Karnataka area, it is planned to take up the powerline crossing works by hotline method. | Yes | Approved | Concurrence from the concerned RE developers is submitted by PGCIL SR-2 for taking A/R into Non-Auto mode through mail communication dated 26.05.20206. Further, there is no N-1 redundancy available for the RE generating plants connected at 400kV KOPPAL PSS. Also, it is to be duly noted that the peak wind season in the Southern Region has already commenced, and multiple line tripping have been observed in nearby grid elements during the past few days. 400kV-KOPPAL-GADAG D/C is already under shutdown due to tower collapse. | Auto Reclosure | 22-May-2026 | 22:10 | 26-May-2026 | 10:35
RQ109282 | PNOCC | PGCIL SR-2 | A/R of 220KV-KOPPAL-RENEW_SURYA_KOPPAL-1 | RENEW POWER PVT LTD | D | Construction Works of 400 kV Gadag-II - Koppal-II D/C Line: Powerline crossing at Loc. 13/0 - 14/0 by Hotline Method. | 2026-05-31 | 07:00 | 2026-05-31 | 19:00 | Line Shutdowns were approved under Mid OCC_2371. However, IPP has denied to consent citing, substantial financial implication due to expected generation loss during shutdown period. In view of the commissioning target of 400 kV Gadag II - Koppal II D/C Transmission line by Mid of June 2026 and commencement of monsoon rains in North Karnataka area, it is planned to take up the powerline crossing works by hotline method. | Yes | Approved | Concurrence from the concerned RE developers is submitted by PGCIL SR-2 for taking A/R into Non-Auto mode through mail communication dated 26.05.20206. Further, there is no N-1 redundancy available for the RE generating plants connected at 400kV KOPPAL PSS. Also, it is to be duly noted that the peak wind season in the Southern Region has already commenced, and multiple line tripping have been observed in nearby grid elements during the past few days. 400kV-KOPPAL-GADAG D/C is already under shutdown due to tower collapse. | Auto Reclosure | 22-May-2026 | 22:10 | 28-May-2026 | 10:29
RQ109284 | PNOCC | PGCIL SR-2 | TIE BAY (411) OF 400KV-GUTTUR-HIRIYUR-1 AND 400KV-NELAMANGALA-HIRIYUR-1 @HIRIYUR - 400KV | PGCIL SR-2 | D | For SF6 leakage arrest works | 2026-05-27 | 08:30 | 2026-05-27 | 18:00 |  | Yes | Approved | Remaining bays shall be in service. | Bay | 23-May-2026 | 12:53 | 24-May-2026 | 10:44
RQ109287 | PNOCC | PGCIL SR-1 | NAGARJUNASAGAR_PG - 400KV - BUS 1 | PGCIL SR-1 | C | Already approved on 24.5.2026 and 25.5.2026 in OCC 237 for Bus Bar Relay testing works but not availed due other lines shut down.May please approve | 2026-05-29 | 09:00 | 2026-05-30 | 18:00 | Already approved on 24.5.2026 and 25.5.2026 in OCC 237 for Bus Bar Relay testing works but not availed due other lines shut down.May please approve | Yes | Approved | Remaining all elements shall be in service. | Bus | 23-May-2026 | 16:41 | 26-May-2026 | 17:35
RQ109295 | EMERGENCY | TGTRANSCO | 400KV-BHOOPALAPALLY-WARANGAL-2 | TGTRANSCO | C | Arrange to issue to LC on KTPP-Ogulapur#2 for replacement of flashed over discs at location NO.45 (Suspension tower) on top phase. | 2026-05-25 | 06:00 | 2026-05-25 | 12:00 | Please approve L.C. | Yes | Approved | Line-1 and Bhoopalpally-Chandulapur D/C shall be in service. | Line Circuits | 24-May-2026 | 10:50 | 25-May-2026 | 06:39
RQ109300 | EMERGENCY | aptransco | MAIN BAY (414) OF 400KV-KALPAKKA-VEMAGIRI_AP-1 AND KALPAKKA - 400KV - BUS 3 @KALPAKKA - 400KV | APTRANSCO | C | Heavy sparks observed continuously on Y- Phase flexible clamp of Breaker in 400KV Kalapaka- Vemagiri feeder at 400kV ss kalapaka | 2026-05-24 | 19:05 | 2026-05-24 | 19:10 |  | Yes | Approved |  | Bay | 24-May-2026 | 19:01 | 24-May-2026 | 19:04
RQ109313 | EMERGENCY | aptransco | MAIN BAY (410) OF 400KV-KRISHNAPATNAM-NELLORE_AP-2 AND NELLORE_AP - 400KV - BUS 1 @NELLORE_AP - 400KV | APTRANSCO | C | for attending hotspot on 400KV 4-1089A isolator stud Clamp(Y-Phase). | 2026-05-25 | 12:04 | 2026-05-25 | 15:04 | No Interruption | Yes | Approved | Other bays shall be in service | Bay | 25-May-2026 | 12:05 | 25-May-2026 | 12:14
RQ109314 | EMERGENCY | RSTCL | 765KV-RAICHUR_PG-SHOLAPUR-2 | RSTCL | D | To replace the broken insulator at Tower No. 101, Location No. 11/25, B-Phase outer | 2026-05-25 | 12:05 | 2026-05-25 | 17:05 | To replace the broken insulator at Tower No. 101, Location No. 11/25, B-Phase outer | Yes | Approved |  | Line Circuits | 25-May-2026 | 12:09 | 25-May-2026 | 12:22
RQ109315 | PNOCC | TGTRANSCO | 400KV-YEDULA-DINDI-1 | TGTRANSCO | C | To ascertain the performance of SFP's and to re-check the end to end line differential relay. | 2026-05-29 | 10:00 | 2026-05-29 | 18:00 | Please issue LC. | Yes | Rejected | Element is already under outage. | Line Circuits | 25-May-2026 | 12:18 | 26-May-2026 | 10:46
RQ109319 | EMERGENCY | PGCIL SR-1 | 400KV-KHAMMAM_PG-NAGARJUNASAGAR_PG-1 | POWERGRID | D | To remove foreign object on transmission line | 2026-05-25 | 15:28 | 2026-05-25 | 17:00 | To remove foreign object on transmission line | Yes | Approved |  | Line Circuits | 25-May-2026 | 15:32 | 25-May-2026 | 15:39
RQ109320 | EMERGENCY | aptransco | 400KV/220KV NELLORE_AP-ICT-1 | APTRANSCO | C | rectify hot spot on Y-phase LV CT stud clamp | 2026-05-25 | 16:01 | 2026-05-25 | 18:01 |  | Yes | Approved |  | Transformer | 25-May-2026 | 16:03 | 25-May-2026 | 16:09
RQ109321 | EMERGENCY | PGCIL SR-2 | TIE BAY (417) OF 400KV-MADURAI_PG-TIRUNELVELI-2 AND 400KV-KUDANKULAM-TIRUNELVELI-1 @TIRUNELVELI - 400KV | PGCIL SR-2 | C | for attending SF6 low alarm. | 2026-05-25 | 16:02 | 2026-05-25 | 19:02 | nil | Yes | Approved |  | Bay | 25-May-2026 | 16:04 | 25-May-2026 | 16:09
RQ109324 | PNOCC | PGCIL SR-2 | A/R of 400KV-NNTPP-PUDUCHERRY-1 | POWERGRID | D | PID scanning of complete line due to frequent failure of porcelain insulators | 2026-05-29 | 09:00 | 2026-05-29 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 25-May-2026 | 17:14 | 26-May-2026 | 10:46
RQ109325 | PNOCC | PGCIL SR-2 | A/R of 400KV-NNTPP-PUDUCHERRY-1 | POWERGRID | D | PID scanning of complete line due to frequent failure of porcelain insulators | 2026-05-30 | 09:00 | 2026-05-30 | 18:00 |  | Yes | Approved | Concurred, subject to real time grid conditions | Auto Reclosure | 25-May-2026 | 17:14 | 27-May-2026 | 11:21
RQ109334 | PNOCC | PGCIL SR-1 | A/R of 400KV-GAJWEL-RAMAGUNDAM-1 | POWERGRID | D | PID TESTING OF 120 KN AND 160 KN Porcelain insulator String | 2026-05-30 | 08:00 | 2026-05-30 | 18:00 | PID TESTING OF 120 KN AND 160 KN Porcelain insulator String | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 25-May-2026 | 18:28 | 27-May-2026 | 11:21
RQ109336 | PNOCC | PGCIL SR-1 | A/R of 400KV-VIJAYAWADA-VEMAGIRI_PG-1 | POWERGRID | D | For carrying PID scanning of 400kV Vijayawada-Vemagiri SC Line | 2026-05-30 | 08:00 | 2026-05-30 | 18:00 | For carrying PID scanning of 400kV Vijayawada-Vemagiri SC Line | Yes | Approved | Concurred, subject to real time grid conditions. | Auto Reclosure | 25-May-2026 | 18:34 | 27-May-2026 | 11:21
RQ109377 | PNOCC | PGCIL SR-1 | MAIN BAY (406) OF 400KV-GOOTY-PAVAGADA_PG-2 AND GOOTY - 400KV - BUS 2 @GOOTY - 400KV | PGCIL SR-1 | D | Bay AMP works | 2026-05-30 | 08:00 | 2026-05-30 | 18:00 | Bay AMP works | Yes | Approved | Remaining bays shall be in service. | Bay | 26-May-2026 | 17:04 | 27-May-2026 | 11:26
RQ109378 | PNOCC | kptcl | TIE BAY (410) OF 400KV/11.5KV BTPS-ST-3 AND 400KV-GUTTUR-BTPS-1 @BTPS - 400KV | KPCL | C | to take the line on Main breaker after testing | 2026-05-30 | 10:00 | 2026-05-30 | 14:00 |  | Yes | Approved | Remaining bays shall be in service and subject to voltage conditions. | Bay | 26-May-2026 | 17:09 | 27-May-2026 | 11:26
RQ109403 | PNOCC | PGCIL SR-2 | KOZHIKODE - 400KV - BUS 1 | PGCIL SR-2 | D | AMP works. | 2026-05-30 | 08:00 | 2026-05-30 | 18:00 | AMP works. | Yes | Approved | OCC approved shutdown. Remaining all elements shall be in service. | Bus | 26-May-2026 | 17:30 | 27-May-2026 | 11:26
RQ109405 | EMERGENCY | PGCIL SR-2 | 400KV-KALVENDAPATTU-VALLUR-1 | POWERGRID | D | Removal of hanging tarpaulin/flex sheet | 2026-05-26 | 18:45 | 2026-05-26 | 20:15 | Removal of hanging tarpaulin/flex sheet | Yes | Approved | Other line to be in service. shutdown timelines to be followed. | Line Circuits | 26-May-2026 | 18:38 | 26-May-2026 | 18:40
RQ109412 | EMERGENCY | aptransco | 400KV-GAZUWAKA-KALPAKKA-1 | APTRANSCO | C | For attending redhot on Y-phase C isolator towards breaker | 2026-05-27 | 06:50 | 2026-05-27 | 08:50 |  | Yes | Approved |  | Line Circuits | 27-May-2026 | 06:49 | 27-May-2026 | 08:17
RQ109413 | EMERGENCY | TANTRANSCO | 400KV-RASIPALYAM-ANAIKADAVU-2 | TANTRANSCO | D | Communication Disturbance between Rasipalayam 400 KVSS and Anikadavu 400 KVSS – Found Fibre cut on OPGW at Gantry Tower of Rasipalayam SS - rectification and replacement work of OPGW | 2026-05-27 | 10:00 | 2026-05-27 | 18:00 | Other feeder will be in service | Yes | Approved |  | Line Circuits | 27-May-2026 | 09:58 | 27-May-2026 | 10:02
RQ109414 | EMERGENCY | PGCIL SR-1 | MAIN BAY (407) OF 400KV-GHANAPUR-RAMAGUNDAM-3 AND GHANAPUR - 400KV - BUS 1 @GHANAPUR - 400KV | PGCIL SR-1 | D | Air leakage is persisting near the pressure switch of compressor at 407-52 ABB Breaker. | 2026-05-27 | 09:58 | 2026-05-27 | 17:00 | Air leakage is persisting near the pressure switch of compressor at 407-52 ABB Breaker. | Yes | Approved |  | Bay | 27-May-2026 | 10:01 | 27-May-2026 | 11:19
RQ109429 | EMERGENCY | TGTRANSCO | GAJWEL - 400KV - BUS 1 | TGTRANSCO | C | For bus-1 testing by mrt wing.all bays connected to bus-1 are in tripped condition except 414 and 417 bays breaker due to bus bar operation [From:27/05/2026 13:30 To 27/05/2026 15:30] | 2026-05-27 | 15:00 | 2026-05-27 | 18:00 | pl issue lc | Yes | Approved | BUS-2 shall be in service | Bus | 27-May-2026 | 14:43 | 27-May-2026 | 14:54
RQ109435 | EMERGENCY | PGCIL SR-1 | ANANTHPURAM - 400KV - BUS 1 | PGCIL SR-1 | C | Renew bay commissioning works at ATP | 2026-05-27 | 15:15 | 2026-05-28 | 18:00 | Renew bay commissioning works at ATP | Yes | Approved | Remaining elements shall be in service. | Bus | 27-May-2026 | 15:11 | 27-May-2026 | 15:13
RQ109478 | EMERGENCY | PGCIL SR-2 | MAIN BAY (403) OF 400KV/230KV KALVENDAPATTU-ICT-1 AND KALVENDAPATTU - 400KV - BUS 1 @KALVENDAPATTU - 400KV | PGCIL SR-2 | D | It was observed the 403 -Y phase bay (ICT -I Bay) current is showing zero. So requested for provide the 403 bay shutdown to attend the issue. | 2026-05-27 | 16:58 | 2026-05-27 | 18:58 | PL approve | Yes | Approved | dia shall be in service | Bay | 27-May-2026 | 16:57 | 27-May-2026 | 17:00
RQ109480 | PNOCC | KSPDCL | PAVAGADA_PG - 220KV - BUS 4 | PGCIL SR-2 | C | IPS Al Tube erection work under bay no 230 | 2026-05-31 | 18:00 | 2026-06-01 | 02:00 |  | Yes | Approved | Remaining all elements shall be in service. | Bus | 27-May-2026 | 17:23 | 28-May-2026 | 10:29
RQ109507 | EMERGENCY | TGTRANSCO | 400KV/220KV DAMARCHERLA-ICT-2 | TGTRANSCO | C | For reconnecting the isolator terminal connector to IPS TUBE at bay no.406 89A which was dislocated due to the heavy wind and for the realignment. | 2026-05-28 | 11:45 | 2026-05-28 | 16:00 | Please approve L.C. | Yes | Approved |  | Transformer | 28-May-2026 | 11:42 | 28-May-2026 | 11:57
RQ109544 | EMERGENCY | NLC | MAIN BAY (401) OF 400KV/16.5KV NEYVELI_TS2_EXP-GT-1 @NEYVELI_TS2_EXP - 400KV | NLC | C | Preventive maintenance work in Power Transformers. | 2026-05-29 | 10:34 | 2026-05-30 | 17:00 | Unit -1 is in shutdown condition due to water wall puncture. So we use this opportunity to do PM work in Power Transformer's(GT-1,UAT-1,SAT-1) | Yes | Approved | Subject to outage of both units, shutdown is approved. | Bay | 29-May-2026 | 10:50 | 29-May-2026 | 11:30
RQ109574 | EMERGENCY | aptransco | 400KV/220KV NARNOOR-ICT-1 | APTRANSCO | D | For MRT testing and general maintenance | 2026-05-29 | 14:15 | 2026-05-29 | 17:10 | OCC approved on 27.05.26, but due to heavy rain couldn't availed LC | Yes | Approved | All other ICT's shall be in service. | Transformer | 29-May-2026 | 12:12 | 29-May-2026 | 13:04
RQ109592 | EMERGENCY | TANTRANSCO | NCPS - 400KV - BUS 1 | TANTRANSCO | C | SAFETY LC TO ATTEND BAY NO 404 & 406 WHICH IS UNDER BREAKDOWN FROM 30.10.2025 | 2026-05-30 | 07:00 | 2026-05-30 | 18:00 | BUS LC REQUIRED INCLUSIVE OF BAY NO.403,409 AND 411 | Yes | Approved | Concurred, for inspection of the break down. No network in the downstream. | Bus | 29-May-2026 | 14:01 | 29-May-2026 | 18:44
RQ109705 | EMERGENCY | aptransco | 400KV/220KV GUDDIGUDEM-ICT-1 | APTRANSCO | C | For Rectification isolator closing problem on 417-89B towards ICT 400KV SS Guddigudem. | 2026-05-30 | 11:15 | 2026-05-30 | 13:45 | ICT-2 in service and it can cater the loads as load on each ICT105MW | Yes | Approved | ICT-2 shall be in service. No n-1 for 220kV Pattiseema S/S. Load management to be done by APSLDC | Transformer | 30-May-2026 | 10:59 | 30-May-2026 | 13:32
RQ109755 | EMERGENCY | KSPDCL | PAVAGADA_PG - 220KV - BUS 4 | PGCIL SR-2 | C | IPS tube erection and isolator (89B) alignment of newly constructed bay 230 | 2026-05-30 | 18:00 | 2026-05-31 | 02:00 |  | Yes | Approved | Concurred, subject to real time grid conditions. | Bus | 30-May-2026 | 15:37 | 30-May-2026 | 16:05
RQ109821 | EMERGENCY | PGCIL SR-2 | TIE BAY (405) OF 400KV/220KV PAVAGADA_PG-ICT-2 AND FUTURE @PAVAGADA_PG - 400KV | PGCIL SR-2 | D | For attending dislocated 405-89A, B-Phase isolator horizontal take-off conductor | 2026-05-31 | 18:35 | 2026-05-31 | 20:30 | For attending dislocated 405-89A, B-Phase isolator horizontal take-off conductor | Yes | Approved |  | Bay | 31-May-2026 | 18:39 | 31-May-2026 | 18:59