## Sheet1
S.no | Shutdown date | Element Name | Owner/Agency | Outage approved Start Date & Time | Outage approved End Date & Time | Shutdown availed Date & Time | Shutdown restoration Date & Time | Duration of outage actully availed | Duration of outage actully planned | Delay Hours | Reason | NLDC Remark
1 | 46028 | 765KV-MAHESHWARAM_PG-WARANGAL(NEW)-2 | WKTL | 06/01/2026 08:00 | 06/01/2026 18:00 | 06-Jan-2026 08:37 | 06-Jan-2026 21:57 | 13 Hours 20 Minutes | 10 Hours 0 Minutes | 3 Hours 20 Minutes | For Annual Shutdown, Insulator replacement & Rectification Works | 765kV Warora - Warangal_NEW D/C, 765kV Warangal_New - C_Peta D/C, 765kV Nizamabad - Maheswaram_PG D/C shall be in service.
2 | 46028 | 765KV/400KV NPS-ICT-3 | pgsr1_sd | 06/01/2026 09:00 | 06/01/2026 17:00 | 06-Jan-2026 08:22 | 07-Jan-2026 00:37 | 16 Hours 15 Minutes | 8 Hours 0 Minutes | 8 Hours 15 Minutes | AMP Works | ICT 1 & 2 to be inservice with complete Dia. N-1 limit of each ICT is 834 MW. 400kV NPS - Gooty D/C, 400kV NPS - Thiruvallam_PG D/C shall be in service.
3 | 46029 | 765KV/400KV CHILAKALURIPETA-ICT-2 | pgsr1_sd | 07/01/2026 09:00 | 07/01/2026 18:00 | 07-Jan-2026 09:47 | 07-Jan-2026 22:03 | 12 Hours 16 Minutes | 9 Hours 0 Minutes | 3 Hours 16 Minutes | AMP Works | ICT-1 (60% sensitivity) to be in service with complete Dia. N-1 limit of each ICT is 891 MW. 765KV/400KV VEMAGIRI_PG-ICT-1 & 2 7% each 400KV-SATTENPALLY-VTPS_IV-1 11% 765KV-CHILAKALURIPETA-CUDDAPAH-1 & 2 8% each 400KV-SATTENPALLY-VEMAGIRI_AP-1 & 2 5% each
4 | 46045 | 765KV/400KV WARORA-PG-ICT 2 | POWERGRID WR1 | 23/01/2026 09:00 | 23/01/2026 13:00 | 23-Jan-2026 10:10 | 23-Jan-2026 17:32 | 7 Hours 22 Minutes | 4 Hours 0 Minutes | 3 Hours 22 Minutes | For ICT AMP works(ICT#2) @Warora SS | 765KV/400KV WARORA-PG-ICT-1 to be in service.
5 | 46061 | 765KV-RAICHUR_PG-SHOLAPUR-2 | RSTCL | 08/02/2026 09:00 | 08/02/2026 16:00 | 08-Feb-2026 10:14 | 09-Feb-2026 22:18 | 1 Days 12 Hours 4 Minutes | 7 Hours 0 Minutes | 1 Days 5 Hours 4 Minutes | To rectify Shutdown defects such as missing/damaged fittings (G-Ring, Split Pin, C.C. Ring, Jumpers, Spacers, Plates, Shackles, Clamps, Dampers, Connectors, Bonds, etc.), rusting/corrosion of hardware, loose or misaligned accessories, insulator failures (including IR-detected hot spots), arcing horns, conductor issues (strand cut/jumper conductor) | "Ckt-1 to be in service, ATC curtailment of SR Export. Subject to strict revival of 765kV-SRIKAKULAM-VEMAGIRI D/C S/D and no other NEW-SR IR shutdowns having ATC/TTC curtailment in SR Import / export. In case of non-facilitation of outage ATC may be revised by NLDC CR."
6 | 46062 | 765KV-RAICHUR_PG-SHOLAPUR-2 | RSTCL | 09/02/2026 09:00 | 09/02/2026 16:00 | 09-Feb-2026 08:52 | 09-Feb-2026 23:33 | 14 Hours 41 Minutes | 7 Hours 0 Minutes | 7 Hours 41 Minutes | To rectify Shutdown defects such as missing/damaged fittings (G-Ring, Split Pin, C.C. Ring, Jumpers, Spacers, Plates, Shackles, Clamps, Dampers, Connectors, Bonds, etc.), rusting/corrosion of hardware, loose or misaligned accessories, insulator failures (including IR-detected hot spots), arcing horns, conductor issues (strand cut/jumper conductor) | Ckt-1 to be in service with A/R enabled. ATC curtailed by 750 MW in SR Import.
7 | 46077 | 765KV-WARANGAL(NEW)-WARORA-1 | WKTL | 24/02/2026 00:00 | 25/02/2026 00:00 | 24-Feb-2026 09:23 | 25-Feb-2026 18:54 | 1 Days 9 Hours 31 Minutes | 1 Days 0 Hours 0 Minutes | 9 Hours 31 Minutes | For NGR BYPASS Activity at Warora Substation | Ckt-2 to be in service with A/R enabled. ATC curtailed by 700 MW in SR Import.
8 | 46078 | 765KV-WARANGAL(NEW)-WARORA-1 | WKTL | 24/02/2026 00:00 | 25/02/2026 00:00 | 24-Feb-2026 09:23 | 25-Feb-2026 18:54 | 1 Days 9 Hours 31 Minutes | 1 Days 0 Hours 0 Minutes | 9 Hours 31 Minutes | For NGR BYPASS Activity at Warora Substation | Ckt-2 to be in service with A/R enabled. ATC curtailed by 700 MW in SR Import.
9 | 46079 | 765KV-WARANGAL(NEW)-WARORA-2 | WKTL | 25/02/2026 00:10 | 26/02/2026 00:10 | 25-Feb-2026 19:28 | 27-Feb-2026 00:56 | 1 Days 5 Hours 28 Minutes | 1 Days 0 Hours 0 Minutes | 5 Hours 28 Minutes | For NGR BYPASS Activity at Warora Substation | Subjected to revival of Ckt 1. Ckt-1 to be in service with A/R enabled. ATC curtailed by 700 MW in SR Import.
10 | 46082 | 765KV/400KV MAHESHWARAM_PG-ICT-2 | pgsr1_sd | 01/03/2026 10:00 | 01/03/2026 14:00 | 01-Mar-2026 17:32 | 02-Mar-2026 01:32 | 8 Hours 0 Minutes | 4 Hours 0 Minutes | 4 Hours 0 Minutes | HV test of new 765kV GIB of ICT-3 Extension works under SS-118 | "NEW-SR import ATC/TTC curtailment of 700 MW. 765KV/400KV MAHESHWARAM_PG-ICT-1 44% All 765kV/400kV NIZAMABAAD ICTs 400KV-KURNOOL_PG-NARNOOR D/C 765KV-CUDDAPAH-KURNOOL_PG D/C shall be in service. Shutdown of 400kV-NAGARJUNASAGAR-MEHBOOBNAGAR to be facilitated only after the revival of 765KV/400KV MAHESHWARAM_PG-ICT-2."