# Draft Report on grid event Complete Outage of 220kV Renigunta SS of APTRANSCO in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 13-06-2026 18:57

# Event Summary (घटना का सारांश):

# As per the reports submitted, the triggering incident was R-Phase CT failure in 220kV Nagari Renigunta line at Renigunta SS which eventually became a 220kV Bus fault. 220kV BBP did not operate and all lines connected to 220kV Renigunta SS tripped from remote ends. This led to complete outage of 220kV Renigunta SS.

- Time and Date of the Event (घटना का समय और दिनांक:  21-05-2026 22:49

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): ANDHRA PRADESH

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Andhra Pradesh State Demand (MW) | 12198 | 12128 |
| Andhra Pradesh State Generation (MW) | 9150 | 9156 |
| Grid Frequency (Hz) | 49.91 | 49.98 |
| SR Demand (MW) | 56906 | 56879 |
| SR Generation (MW) | 57438 | 57405 |

*Pre and post data of 1 minute before and after the event

| Elements under outage | - KODURU - 220KV |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

At 220kVRenigunta SS:

220kV Renigunta Kodur line was idle charged from Renigunta end

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 0.0 MW | 250.0 MW |

- Duration of interruption (रुकावट की अवधि):  0 hours, 27 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण):

| Equipment Type | Equipment make |
| --- | --- |
| CT | WS industries |
| CB | ALSTOM |

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 220KV-CHITTOOR-RENIGUNTA-1

      - 220KV-CUDDAPAH-RENIGUNTA-1

      - 220KV-RENIGUNTA-NAGIRI-1

      - 220KV-RENIGUNTA-RACHAGUNNERI-1

      - 220KV-RENIGUNTA-RACHAGUNNERI-2

      - 220KV-RENIGUNTA-KODURU-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

As per the reports submitted, the triggering incident was R-Phase CT failure in 220kV 220kV Nagari Renigunta line at Renigunta SS leading to a 220kV Bus fault. Further as the failure R-ph CT fire has come into vicinity and the CB connected to Nagiri also failed (as per FIR) as shown below. This has led to a R-G fault at 22:49:10.960 Hrs which cleared in time and later developed into R-Y-B fault at 22:49:11.600 Hrs.

During the fault, protection at Renigunta for the Nagiri line (Main-1 relay NR/PCS902 and Main2 ALSTOM/P444 and BCU NR/PCS9705 got failed) and also 220KV Bus Bar Protection Relay NR/PCS915 failed (as per the detailed report).

220KV-RENIGUNTA-NAGIRI-1:

The fault was only sensed at Nagiri end in Z2 and carrier was received from Renigunta end (hence at Renigunta, the fault was sensed in Z1 but DR for the event was not available as the Relay failed) and 3ph tripped. The fault continued to be fed from Renigunta end.

220KV-CUDDAPAH-RENIGUNTA-1:

At Renigunta end, one of the main sensed in Z1 and carrier was sent to the remote end and R-pole opened during the CT failure fault. Later during Y fault, the fault was sensed in Z4. However DT was received at remote end after around 100ms from the fault. Exact reason for DT sent could not be ascertained and line was holding from Renigunta end. At Cuddapah end, the fault was sensed in Z2 carrier aided protection and R-pole opened and during the Y-ph fault, DT was received and 3ph tripped.

220KV-CHITTOOR-RENIGUNTA-1:

At Renigunta end, the fault was sensed in Z4 and 3ph tripped after around 200ms from the sensing of the fault. At Chittoor end, the fault was sensed in Z2 and was holding.

220KV-RENIGUNTA-RACHAGUNNERI-1:

At Rachagunneri end, the R-G fault was sensed in carrier aided zone-2 and R-pole opened. During A/R dead time, later during Y-G fault, the fault was sensed in zone-2 and the line tripped after around 350ms. At Renigunta end, it is reported from the FIR that the line is holding.

220KV-RENIGUNTA-RACHAGUNNERI-2:

The R-G fault was initially sensed at Rachagunneri end in zone-2 start and the line was holding at both end without any pole tripping. At rachagunneri end, Later for the Y-G fault, the fault was initially sensed in zone-2 start and then it eventually became RY-G fault which was sensed in zone-1 and the line tripped. At Renigunta end, the fault was sensed in zone-4 and later carrier was received and the line tripped. It is suspected that Zone-1 protection operated at Rrenigunta end during RY-G fault as carrier send was seen in the DR. The line tripped at both ends.

Tripping of all these lines led to complete outage of 220kV Renigunta SS .

- DR Analysis:

RENIGUNTA - 220KV

|  | RENIGUNTA - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:21-05-2026 22:49:10.929 Any Start, IN>1 Start DIST Rev, Z4, DIST Start A IN>1 Start Any Start, IN>1 Start DIST Rev, Z4, DIST Start B External Trip A External Trip B, External Trip C Any Trip, 86A Optd DIST Start A R Ph Open B Ph Open Y Ph Open Any Pole Dead, All Pole Dead Ir (max): 3.62 kA Iy (max): 3.29 kA Ib (max): 0.63 kA Vr (max): 141.02 kV Vy (max): 146.99 kV Vb (max): 151.58 kV DR Trigger Time:21-05-2026 22:49:10.926 Any Start, IN>1 Start DIST Rev, DIST Start A Z4 Any Start, IN>1 Start Any Start, IN>1 Start DIST Start B DIST Rev Z4 External Trip A, External Trip B, External Trip C A/R Lockout, DIST Start A, 86A Optd Any Trip AR Lockout Shot> 86B Optd B Ph Open Any Pole Dead, R Ph Open, Y Ph Open All Pole Dead DIST. Chan Recv, CR-2 Ir (max): 9.53 kA Iy (max): 5.77 kA Ib (max): 0.70 kA Vr (max): 139.04 kV Vy (max): 143.99 kV Vb (max): 146.60 kV |

220KV-RENIGUNTA-NAGIRI-1

|  | RENIGUNTA - 220KV | NAGIRI - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | Yes |
| DR Analysis | DR is not available | DR Trigger Time:21-05-2026 23:46:19.815 Any Start, IN>1 Start DIST Start A, Dist Start N DIST. Chan Recv, L8 CARR REC CH1 Z2 Any Trip, DIST Trip A, 3P Trip, R12 86A TR-Z2_.., R18 86B TR-Z2_.. L13 86A OP-LBBIN, L14 86B OP-LBBIN I>3 Start L1 M CB OPN-R Dist Start N L3 M CB OPN-B L2 M CB OPN-Y External Trip A, External Trip B, External Trip C Ir (max): 1.88 kA Iy (max): 0.16 kA Ib (max): 0.28 kA Vr (max): 129.82 kV Vy (max): 152.08 kV Vb (max): 141.74 kV |

220KV-RENIGUNTA-RACHAGUNNERI-2

|  | RENIGUNTA - 220KV | RACHAGUNNERI - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:21-05-2026 22:49:10.926 Any Start, IN>1 Start DIST Rev, DIST Start A Z4 Any Start, IN>1 Start Any Start, IN>1 Start DIST Start B DIST Rev Z4 External Trip A, External Trip B, External Trip C A/R Lockout, DIST Start A, 86A Optd Any Trip AR Lockout Shot> 86B Optd B Ph Open Any Pole Dead, R Ph Open, Y Ph Open All Pole Dead DIST. Chan Recv, CR-2 Ir (max): 9.53 kA Iy (max): 5.77 kA Ib (max): 0.70 kA Vr (max): 139.04 kV Vy (max): 143.99 kV Vb (max): 146.60 kV | DR Trigger Time:21-05-2026 22:49:10.913 IEDStartup PhAStartup, ZeroSeqStartup PhBStartup, ZeroSeqStartup PilotDistRcvMsg, X9_BI9: CARR RECEIVE CH-1 PhAStartup TripSplitPhTripA, TripSplitPhTripB, TripSplitPhTripC, Trip3PhTrip, PilotDistSendMsg, PilotDistTrip X7_BO1: 86A RELAY CKT, X7_BO4: R-PH TRIP RLY CKT, X7_BO5: Y-PH TRIP RLY CKT, X7_BO6: B-PH TRIP RLY CKT, X7_BO7: 86B RELAY CKT X9_BI3: 3PH GRP A/B TRIP PhAOpenPosn, X7_BI1: CB R PH OPEN PhCOpenPosn, X7_BI3: CB B PH OPEN PhBOpenPosn, X7_BI2: CB Y PH OPEN X9_BI1: PREP 3.PH TRIP Ir (max): 9.28 kA Iy (max): 5.63 kA Ib (max): 0.68 kA Vr (max): 127.84 kV Vy (max): 128.30 kV Vb (max): 128.09 kV DR Trigger Time:21-05-2026 22:49:11.878 TOC1-START ZONE3_START ZONE2_START, ZONE[2]_STL1 TOC1-START ZONE3_START ZONE2_START, ZONE[2]_STL2 Carr Rec ch-1 ZONE[2]_STL1 ZONE1_TRIP, ZONE1_START, 1ph INITIATIO TRIP R, Carr Send, TRIP-Rphase, TRP1-TRIP 86GA/GB OPTD ZCOM TRIP CB R PH OPEN CB BPH OPEN CB YPH OPEN Ir (max): 9.23 kA Iy (max): 5.64 kA Ib (max): 0.68 kA Vr (max): 127.52 kV Vy (max): 128.16 kV Vb (max): 128.08 kV |

220KV-RENIGUNTA-RACHAGUNNERI-1

|  | RENIGUNTA - 220KV | RACHAGUNNERI - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | Line was holding | DR Trigger Time:21-05-2026 22:49:10.914 IEDStartup PhAStartup, ZeroSeqStartup PilotDistRcvMsg, X9_BI9: CARR RECEIVE CH-1 TripSplitPhTripA, PilotDistTrip PilotDistSendMsg X7_BO4: R-PH TRIP RLY CKT PhAOpenPosn, X7_BI1: CB R PH OPEN PhBStartup ZeroSeqStartup X9_BI1: PREP 3.PH TRIP PhBStartup, ZeroSeqStartup TripSplitPhTripA, TripSplitPhTripB, TripSplitPhTripC, Trip3PhTrip, IEDTrip3Ph/BlkAR, DistZ2Trip X7_BO1: 86A RELAY CKT, X7_BO4: R-PH TRIP RLY CKT, X7_BO5: Y-PH TRIP RLY CKT, X7_BO6: B-PH TRIP RLY CKT, X7_BO7: 86B RELAY CKT X9_BI3: 3PH GRP A/B TRIP PhBOpenPosn, PhCOpenPosn, X7_BI2: CB Y PH OPEN, X7_BI3: CB B PH OPEN PhBStartup, ZeroSeqStartup Ir (max): 4.69 kA Iy (max): 6.65 kA Ib (max): 1.36 kA Vr (max): 127.78 kV Vy (max): 128.50 kV Vb (max): 128.21 kV DR Trigger Time:21-05-2026 22:49:10.933 ZONE3_START ZONE2_START CB R PH OPEN ZONE3_START ZONE2_START ZONE2_TRIP TRIP Y CB YPH OPEN CB BPH OPEN Ir (max): 4.69 kA Iy (max): 6.66 kA Ib (max): 1.36 kA Vr (max): 127.60 kV Vy (max): 128.28 kV Vb (max): 128.18 kV DR Trigger Time:21-05-2026 22:49:10.998 ZONE3_START ZONE2_START CB R PH OPEN ZONE3_START ZONE2_START ZONE2_TRIP TRIP Y CB YPH OPEN CB BPH OPEN Ir (max): 4.69 kA Iy (max): 6.66 kA Ib (max): 1.36 kA Vr (max): 127.60 kV Vy (max): 128.28 kV Vb (max): 128.18 kV |

220KV-CUDDAPAH-RENIGUNTA-1

|  | CUDDAPAH - 220KV | RENIGUNTA - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:21-05-2026 22:49:10.935 Any Start Z2 Any Trip, DIST Trip A, R14 Zcom Trip, L4 CARR REC CH2, L8 CARR REC CH1, R4 1PH TR-R Any Start Z2 A/R Lockout L13 86A OP-LBBIN L14 86B OP-LBBIN Ir (max): 1.71 kA Iy (max): 1.64 kA Ib (max): 0.64 kA Vr (max): 133.82 kV Vy (max): 134.42 kV Vb (max): 132.78 kV DR Trigger Time:21-05-2026 22:49:10.967 TEF1-STFW, TEF1-2NDHARMD PHS-STFWL1, PHS-STFWPE, PHS START ZM03-START, ZM04-START ZM02-START TEF1-START BI EXT TRIPL1 TEF1-2NDHARMD AR INPROGR CB_RPH_OPEN TEF1-2NDHARMD TEF1-STRV BRC START AR PREP3P TEF1-2NDHARMD PHS-STFWL2, PHS-STFWPE, PHS START ZM03-START, ZM04-START ZM02-START BI EXT TRIP3P CB_BPH_OPEN CB_YPH_OPEN TEF1-STFW, TEF1-2NDHARMD L1 FUSE FAIL Ir (max): 1.68 kA Iy (max): 1.61 kA Ib (max): 0.63 kA Vr (max): 137.63 kV Vy (max): 132.09 kV Vb (max): 143.56 kV | DR Trigger Time:21-05-2026 22:49:10.927 Any Start, IN>1 Start DIST Rev, DIST Start A Z4 Any Start, IN>1 Start DIST Rev, Z4, DIST Start B Any Pole Dead All Pole Dead All Pole Dead Ir (max): 1.74 kA Iy (max): 1.67 kA Ib (max): 0.65 kA Vr (max): 139.65 kV Vy (max): 144.69 kV Vb (max): 147.16 kV |

220KV-CHITTOOR-RENIGUNTA-1

|  | RENIGUNTA - 220KV | CHITTOOR - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:21-05-2026 22:49:10.929 Any Start, IN>1 Start DIST Rev, Z4, DIST Start A IN>1 Start Any Start, IN>1 Start DIST Rev, Z4, DIST Start B External Trip A External Trip B, External Trip C Any Trip, 86A Optd DIST Start A R Ph Open B Ph Open Y Ph Open Any Pole Dead, All Pole Dead Ir (max): 3.62 kA Iy (max): 3.29 kA Ib (max): 0.63 kA Vr (max): 141.02 kV Vy (max): 146.99 kV Vb (max): 151.58 kV | DR Trigger Time:21-05-2026 22:49:10.935 IN>1 Start Z2 I>1 Start IN>1 Start Z2 I>1 Start Ir (max): 3.62 kA Iy (max): 3.28 kA Ib (max): 0.60 kA Vr (max): 137.00 kV Vy (max): 137.99 kV Vb (max): 137.09 kV DR Trigger Time:21-05-2026 22:49:10.935 IN>1 Start Z2 I>1 Start IN>1 Start Z2 I>1 Start Ir (max): 3.62 kA Iy (max): 3.28 kA Ib (max): 0.60 kA Vr (max): 137.00 kV Vy (max): 137.99 kV Vb (max): 137.09 kV |

- A) PMU Analysis:

From PMU dip in R-G fault is observed followed by Y-G fault which eventually became RY-G fault which was cleared with a delay of around 350ms.

B) SCADA Analysis:

From SCADA plot, tripping of 220kV Renigunta Rachagunneri Line-2 is observed.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| APTRANSCO | 1. Non operation of 220kV BBP at Renigunta end. 2. Zone-1 over reach in 220kV Renigunta Rachagunneri Line-2 at Rachagunneri end. 3. Reason for sending DT to Cuddapah end from Renigunta end during Y-G fault. 4. Zone-4 delay time of 220kV Chittoor Renigunta Line-1 at Renigunta end needs to be reviewed. |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| APTRANSCO | Faulty 220KV Nagari feeder got isolated and fire had quenched and the SubStation taken into service and Due to failure of Bus Bar relay ( Out of Service) the split bus arrangement had made as follows 220KV Bus-1 220KV RCGR-1&2, 100MVA PTR-3 and 160MVA PTR-2 and on 220KV Bus-2 : 220KV CKP, 220KV KDR, 220KV MMG and 160MVA PTR-1 |

- RLDC Analysis/Observations (Based on Simulation Studies):

- Restoration Details:

Restoration activities were taken up as detailed below:

1.220 kV RGT–CK Palli feeder was charged from CK Palli end at 23:16 hrs.

2.220 kV Rachagunneri feeder–1 was charged from Rachagunneri end at 23:27 hrs.

3.Supply was extended to both 220 kV Bus-1 and Bus-2, and supply to all 132 kV feeders was restored.

4.220 kV Rachagunneri–2 feeder was charged at 23:47 hrs.

5.220 kV Mahadevamangalam feeder was charged at 00:25 hrs.

6.220 kV Koduru feeder was charged at 00:45 hrs.

7.Bus coupler H/T and busbar protection were kept out of service, and split bus arrangement was made as follows:

220 kV Bus-1:

Bus 1 Connected Elements: 220Rachagunneri-1, 220KV C.K.Palli,160MVA PTR-2 and 100MVA PTR-3160 MVA PTR-1

220KV Bus-2:

Bus 2 Connected elements: 220KV CKPalli, 220KV Koduru and 220KV M.Mangalam and 160MVA PTR-1

Normalcy was restored.

Duration of interruption was from 22:49 hrs to 23:16 hrs.

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | APTRANSCO |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | APTRANSCO |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) | APTRANSCO |
| 4 | Any other non-compliance | IEGC section 17.3 | APTRANSCO |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: