# Draft Report on grid event Complete Outage of 765kV NCPS Pooling station of TANTRANSCO and 765kV NCTPS Generating station of TNPGCL in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 11-06-2026 12:51

# Event Summary (घटना का सारांश):

# 765kV NCPS Pooling station and 765kV NCTPS Generating station are radially connected through 765kV Ariyalur NCPS Line-1&2. During antecedent conditions, 765kV Ariyalur NCPS Line-1 was under outage from 18-05-2026 23:30 Hrs due to Y-G fault and hence 765kV NCPS Pooling station and 765kV NCTPS Generating station were radially connected to 765kV Ariyalur NCPS Line-2. The triggering incident is the Y-G fault in the 765kV Ariyalur NCPS Line-2 and the line tripped. Tripping of the only source led to complete outage of 765kV NCPS Pooling station and 765kV NCTPS Generating station

- Time and Date of the Event (घटना का समय और दिनांक:  03-06-2026 18:34

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): TAMILNADU

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| TamilNadu State Demand (MW) | 18138 | 18082 |
| TamilNadu State Generation (MW) | 7504 | 6879 |
| Grid Frequency (Hz) | 50.15 | 50.1 |
| SR Demand (MW) | 52430 | 52461 |
| SR Generation (MW) | 47757 | 47327 |

*Pre and post data of 1 minute before and after the event

| Elements under outage | - 765KV-ARIYALUR-NCPS-1 |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

At NCTPS ST3 end :

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 483.0 MW | 0.0 MW |

- Duration of interruption (रुकावट की अवधि):  1 hours, 40 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 765KV/27KV NCTPS STG3-GT-1

      - NCTPS STG3 - UNIT 1

      - 765KV-ARIYALUR-NCPS-2

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

765kV NCPS Pooling station and 765kV NCTPS Generating station are radially connected through 765kV Ariyalur NCPS Line-1&2. During antecedent conditions, 765kV Ariyalur NCPS Line-1 was under outage from 18-05-2026 23:30 Hrs due to Y-G fault and hence 765kV NCPS Pooling station and 765kV NCTPS Generating station were radially connected to 765kV Ariyalur NCPS Line-2.

As per the reports submitted, the triggering incident was Y-G fault in 765kV Ariyalur NCPS Line-2 during 18:30 Hrs and 18:33 Hrs.

Fault at 18:30:43.368 Hrs :

At Ariyalur end, the fault was sensed in Z2 carrier aided protection, Y-pole opened in both main and tie breakers, Auto recloser only operated in main breaker and did not operate in tie breaker. The tie breaker R and B poles tripped due to suspected PD operation and 3ph tripped. Main breaker AR was successful and the line was holding. At NCPS end AR operated and was successful (based on DR from Ariyalur end).

Fault at 18:33:55.952 Hrs :

At Ariyalur end, the fault was sensed in Z2 carrier aided protection, AR did not operate and 3ph. At NCPS end, the fault was sensed in Z1, AR operated and tripped due to persistent fault.

Tripping of the only source (765kV Ariyalur NCPS Line-2) led to complete outage of 765kV NCPS Pooling station and 765kV NCTPS Generating station. During the event NCTPS ST3 U1 was in service and was generating around 483 MW and tripped on Low forward power protection (as per FIR) and leading to generation loss of 483MW.

- DR Analysis:

765KV-ARIYALUR-NCPS-2

|  | ARIYALUR - 765KV | NCPS - 765KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:03-06-2026 18:30:43.368 10 CARR REC-1 Any Trip, Aided 1 Trip B CB1 AR 1p InProg, AR Start, ARIP, CB2 AR 1p InProg L18 AR INI Y Zone 1 B Trip, R17 CARR SEND-1 L2 MN CB Y OPN, L15 TIE CB Y OPN Auto Close CB1, R14 MCB AR CLS Auto Close CB2, R15 TCB AR CLS CB2 AR Lockout, R8 TIE GR-A TRP, R31 TIE GR-B TRP L21 TIE AR BLK Any Trip L14 TIE CB R OPN L16 TIE CB B OPN Ir (max): 0.46 kA Iy (max): 1.68 kA Ib (max): 0.47 kA Vr (max): 462.19 kV Vy (max): 487.85 kV Vb (max): 462.89 kV DR Trigger Time:03-06-2026 18:33:55.952 10 CARR REC-1 Any Trip, Aided 1 Trip B L4 86A OPTD, L4 86A OPTD, L18 AR INI Y, L20 MN AR BLK Zone 1 B Trip, CB1 AR 1p InProg, AR Start, ARIP, R17 CARR SEND-1 L2 MN CB Y OPN L1 MN CB R OPN, L3 MN CB B OPN 10 CARR REC-1 Ir (max): 0.55 kA Iy (max): 3.77 kA Ib (max): 1.13 kA Vr (max): 540.29 kV Vy (max): 527.66 kV Vb (max): 536.04 kV | DR Trigger Time:03-06-2026 18:33:55.912 Any Start Any Trip, DIST Trip B, DIST Fwd, Z1 Any Pole Dead DIST. Chan Recv Any Start DIST Fwd Any Trip, Z1, SOTF/TOR Trip External Trip C Any Pole Dead All Pole Dead Ir (max): 0.76 kA Iy (max): 2.82 kA Ib (max): 1.29 kA Vr (max): 511.50 kV Vy (max): 444.51 kV Vb (max): 527.13 kV |

NCPS - 765KV

|  | NCPS - 765KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis |  |

NCTPS STG3 - 765KV

|  | NCTPS STG3 - 765KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:03-06-2026 18:34:23.915 F<2 Trip, Any Trip 4 HVCB/GCB OPEN Power2 Trip Ir (max): 5.29 kA Iy (max): 5.31 kA Ib (max): 5.36 kA Vr (max): 16.38 kV Vy (max): 16.55 kV Vb (max): 16.40 kV |

765KV/27KV NCTPS STG3-GT-1

|  | NCTPS STG3 - 765KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:03-06-2026 18:34:23.915 F<2 Trip, Any Trip 4 HVCB/GCB OPEN Power2 Trip Ir (max): 5.29 kA Iy (max): 5.31 kA Ib (max): 5.36 kA Vr (max): 16.38 kV Vy (max): 16.55 kV Vb (max): 16.40 kV |

- A) PMU Analysis:

From the PMU plot, Y-G fault can be observed at 18:30 and 18:33 Hrs without any delayed fault clearance.

B) SCADA Analysis:

From the SCADA data, tripping of the line can be observed and complete outage of NCPS and NCTPS ST3 can be observed

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| TANTRANSCO | 1. Non operation of tie breaker AR during the first Y-G fault at 18:30 Hrs needs review 2. Non operation of main breaker AR during the second Y-G fault at 18:33 Hrs needs review |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):  Nil

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

03/06/2026 20:14

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | TANTRANSCO, TNPGCL |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | TNPGCL |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: