# Draft Report on grid event Complete Outage of 220kV Renew_Surya_Koppal of Renew in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 13-06-2026 19:16

# Event Summary (घटना का सारांश):

# As per the report submitted, while charging 220KV/33KV Renew_Surya_Koppal-ICT-1, 220kV KOPPAL-Renew_Surya_Koppal-1 tripped at Renew_Surya_Koppal end and DT was sent to Koppal end. The line tripped at Koppal end upon receiving DT. Tripping of the only connected line led to complete outage of Renew_Surya_Koppal.

- Time and Date of the Event (घटना का समय और दिनांक:  06-06-2026 13:42

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): KARNATAKA

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Karnataka State Demand (MW) | 12563 | 12540 |
| Karnataka State Generation (MW) | 7340 | 7398 |
| Grid Frequency (Hz) | 49.91 | 49.91 |
| SR Demand (MW) | 57508 | 57604 |
| SR Generation (MW) | 57919 | 58144 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Cloudy |

At Renew_Surya_Koppal 220 kV :

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) |  | Load Loss (MW) |
| --- | --- | --- |
| Solar | 18.0 MW | 0.0 MW |
| Wind | 0.0 MW |  |
| Others | 0.0 MW |  |
| Total | 18.0 MW |  |

- Duration of interruption (रुकावट की अवधि):  0 hours, 43 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 220KV-KOPPAL-Renew_Surya_Koppal-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

Renew_Surya_Koppal-220 kV is radially connected to Koppal 220 kV through 220KV-KOPPAL-Renew_Surya_Koppal-1.

In the antecedent condition, 220KV/33KV Renew_Surya_Koppal-ICT-1 was under outage. As per the report submitted, while charging 220KV/33KV Renew_Surya_Koppal-ICT-1, 220kV KOPPAL-Renew_Surya_Koppal-1 tripped at Renew_Surya_Koppal end and DT was sent to Koppal end. The line tripped at Koppal end upon receiving DT. Tripping of the only connected line led to complete outage of Renew_Surya_Koppal.

- DR Analysis:

220KV-KOPPAL-Renew_Surya_Koppal-1

|  | Renew_Surya_Koppal - 220KV | KOPPAL - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:06-06-2026 13:42:52.393 Any Trip, Trip Output A, Trip Output B, 86.1 Trip Relay, 86.2 Trip Relay, 87L1 Optd To PMU, DT Send CH-2, Spare DT Send CH-1 A/R Block CB B-ph Open Ir (max): 0.10 kA Iy (max): 0.36 kA Ib (max): 0.19 kA Vr (max): 145.04 kV Vy (max): 130.41 kV Vb (max): 131.35 kV | DR Trigger Time:06-06-2026 13:42:52.412 L18 CR REC CH2, DIST UNB CR L8 DT REC CH1, R7 GRP-A TRIP, R8 GRP-B TRIP L22 GRP A OPTD 3PH GR B OPTD L3 M CB B OPN L1 M CB R OPN, L2 M CB Y OPN T1 Ir (max): 0.09 kA Iy (max): 0.35 kA Ib (max): 0.18 kA Vr (max): 147.33 kV Vy (max): 129.75 kV Vb (max): 131.51 kV DR Trigger Time:06-06-2026 13:42:52.433 L1 DT REC CH1 R9 GRP-A TRIP, R10 GRP-B TRIP L15 86B OPTD, L15 86B OPTD Ir (max): 0.08 kA Iy (max): 0.33 kA Ib (max): 0.17 kA Vr (max): 147.29 kV Vy (max): 129.69 kV Vb (max): 131.49 kV |

Renew_Surya_Koppal - 220KV

|  | Renew_Surya_Koppal - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:06-06-2026 13:42:52.393 Any Trip, Trip Output A, Trip Output B, 86.1 Trip Relay, 86.2 Trip Relay, 87L1 Optd To PMU, DT Send CH-2, Spare DT Send CH-1 A/R Block CB B-ph Open Ir (max): 0.10 kA Iy (max): 0.36 kA Ib (max): 0.19 kA Vr (max): 145.04 kV Vy (max): 130.41 kV Vb (max): 131.35 kV |

- A) PMU Analysis:  Nil

B) SCADA Analysis:

From the SCADA plot, tripping of the line and Renew_Surya_Koppal station can be observed with a generation loss of around 18MW

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| RENEW POWER PVT LTD | Tripping of 220KV-KOPPAL-Renew_Surya_Koppal-1 at Renew_Surya_Koppal end while charging ICT-1 needs review |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| RENEW POWER PVT LTD | Post‑fault patrolling and inspection of the transmission line and associated PSS/protection system have been completed, and no abnormalities were observed. it was happened due to a DT operation while Energizing the ICT-1. |

- RLDC Analysis/Observations (Based on Simulation Studies):

AN

- Restoration Details:

Post‑fault patrolling and inspection of the transmission line and associated PSS/protection system have been completed, and no abnormalities were observed. It happened due to a DT operation while Energizing the ICT-1. 220KV-KOPPAL-Renew_Surya_Koppal-1 line charged at 14:25 Hrs.

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | RENEW POWER PVT LTD |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | INDIGRID |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: