# Draft Report on grid event Complete Outage of 220kV Hiriyur_Ostro of RENEW in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 11-06-2026 16:15

# Event Summary (घटना का सारांश):

# 220kV Hiriyur_Ostro is connected radially to Hiriyur through 220KV-HIRIYUR_OSTRO-HIRIYUR-1. The triggering incident is the R-G fault in the line and the line tripped. Tripping of the only line connected to Hiriyur_Ostro led to the complete outage of Hiriyur_Ostro of RENEW

- Time and Date of the Event (घटना का समय और दिनांक:  08-06-2026 07:49

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): KARNATAKA

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Karnataka State Demand (MW) | 11595 | 11500 |
| Karnataka State Generation (MW) | 6509 | 6301 |
| Grid Frequency (Hz) | 50.05 | 50.06 |
| SR Demand (MW) | 50406 | 50308 |
| SR Generation (MW) | 48261 | 47979 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Cloudy , Rainy |

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) |  | Load Loss (MW) |
| --- | --- | --- |
| Solar | 0.0 MW | 0.0 MW |
| Wind | 85.0 MW |  |
| Others | 0.0 MW |  |
| Total | 85.0 MW |  |

- Duration of interruption (रुकावट की अवधि):  12 hours, 40 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 220KV-HIRIYUR_OSTRO-HIRIYUR-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

220kV Hiriyur_Ostro is connected radially to Hiriyur through 220KV-HIRIYUR_OSTRO-HIRIYUR-1. The triggering incident is the R-G fault in the line during the inclement weather due to suspension insulator failure was observed at Tower No. 67. At Hiriyur end, the fault was sensed in differential protection, 3ph tripped and further DT was sent to remote end. At Ostro end, the fault was sensed in differential protection and due to receipt of DT 3ph tripped. Tripping of the only line connected to Hiriyur_Ostro led to the complete outage of Hiriyur_Ostro of RENEW.

- DR Analysis:

220KV-HIRIYUR_OSTRO-HIRIYUR-1

|  | HIRIYUR_OSTRO - 220KV | HIRIYUR - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:08-06-2026 07:49:36.982 ZMFCPDIS_STFW, ZMFCPDIS_STFW ZMF02-START, ZMF03-START, EF4PTOC[1]-ST L3CPDIF_STL1, L3CPDIF_BLK2H, L3CPDIF_BLK5H, L3CPDIF_BLKHL1 L3CPDIF_STARTRES L3CPDIF_TRIP, L3CPDIF_TRL1, L3CPDIF_STARTUNR TRIP1_TRIP, TRIP1 L1, TRIP1 L2, TRIP1 L3, LDLPSCH_TRIP, LDLPSCH_TRL1, BLOCK_AR FAULT_LOOP_R 86A/B OPTD REM_INTR RCV LDLPSCH_TRREM DT RCV CH1 PERM1P TR_BCU_M/ MN CB OPEN R, MN CB OPEN Y, MN CB OPEN B Ir (max): 0.72 kA Iy (max): 0.36 kA Ib (max): 0.35 kA Vr (max): 130.78 kV Vy (max): 141.01 kV Vb (max): 134.90 kV DR Trigger Time:08-06-2026 07:49:36.983 ZMF02-START, ZMF03-START, PHS-STFWL1, PHS-STFWPE TEF-START CARR RCV CH2 CARR RCV CH1 86A/B OPTD DT RCV CH2 TRIP1_TRIP, TRIP1 L1, TRIP1 L2, TRIP1 L3 FAULT LOOP R PERM1P TR_BCU_ ZCOM_TRIP, AR START Ir (max): 0.72 kA Iy (max): 0.36 kA Ib (max): 0.35 kA Vr (max): 130.80 kV Vy (max): 141.02 kV Vb (max): 134.97 kV | DR Trigger Time:08-06-2026 07:49:37.053 DIR_E/F_START, EF4PTOC_STFW M12CRSD L3CPDIF_STL1, L3CPDIF_BLK2H M2_TRIP L3CPDIF_STARTRES L3CPDIF_TRL1 M1_TRIP, DT_SEND, LDLPSCH_TRL1, R-PH_TRIP, Y-PH_TRIP, B-PH_TRIP FAULT LOOP RPH DT_SEND_CH1 LDCM_DT_RCV PR3P_TRP_MAIN T CB_RO U/V_START T CB_BO T CB_YO M CB_RO M CB_YO M CB_BO M CB_BO Ir (max): 7.45 kA Iy (max): 0.35 kA Ib (max): 0.32 kA Vr (max): 130.82 kV Vy (max): 137.05 kV Vb (max): 131.61 kV |

HIRIYUR_OSTRO - 220KV

|  | HIRIYUR_OSTRO - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | Supply Failure |

- A) PMU Analysis:

From PMU, dip in R-G fault is observed indicating R-G fault during the event with no delayed fault clearance.

B) SCADA Analysis:

From the SCADA data, tripping of the line can be observed

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| PGCIL SR-2 | 1. Non operation of AR at Hiriyur end needs review 2. Sending of DT to remote end needs review |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| OSTRO_KANNADA | 1. Line patrolling was conducted, and suspension insulator failure was observed at Tower No. 67. A new insulator was replaced. Post-fault patrolling and inspection of the transmission line and associated PSS/protection system have been completed, and no abnormalities were observed. 2. Line patrolling carried out for entire rest of line and no further observation found. |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

20:29Hrs on 08/06/2026.

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | OSTRO_KANNADA |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | OSTRO_KANNADA |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: