# Draft Report on grid event Complete Outage of 765kV NCPS Pooling station of TANTRANSCO and 765kV NCTPS Generating station of TNPGCL in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 11-06-2026 15:16

# Event Summary (घटना का सारांश):

# 765kV NCPS Pooling station and 765kV NCTPS Generating station are radially connected through 765kV Ariyalur NCPS Line-1&2. During antecedent conditions, 765kV Ariyalur NCPS Line-1 was under outage and hence 765kV NCPS Pooling station and 765kV NCTPS Generating station were radially connected to 765kV Ariyalur NCPS Line-2. As per the reports submitted, the triggering incident was persistent Y-G fault in 765kV Ariyalur NCPS Line-2 and the 3-ph tripped. Tripping of the only source led to complete outage of 765kV NCPS Pooling station and 765kV NCTPS Generating station.

- Time and Date of the Event (घटना का समय और दिनांक:  09-06-2026 20:10

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): TAMILNADU

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| TamilNadu State Demand (MW) | 18701 | 18709 |
| TamilNadu State Generation (MW) | 7727 | 7706 |
| Grid Frequency (Hz) | 50.05 | 50.04 |
| SR Demand (MW) | 53191 | 53196 |
| SR Generation (MW) | 51289 | 51188 |

*Pre and post data of 1 minute before and after the event

| Elements under outage | - 765KV-ARIYALUR-NCPS-1 |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 514.0 MW | 0.0 MW |

- Duration of interruption (रुकावट की अवधि):  23 hours, 31 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 765KV-ARIYALUR-NCPS-2

      - NCTPS STG3 - UNIT 1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

765kV NCPS Pooling station and 765kV NCTPS Generating station are radially connected through 765kV Ariyalur NCPS Line-1&2. During antecedent conditions, 765kV Ariyalur NCPS Line-1 was under outage from 18-05-2026 23:30 Hrs due to R-G fault and hence 765kV NCPS Pooling station and 765kV NCTPS Generating station were radially connected to 765kV Ariyalur NCPS Line-2.

As per the reports submitted, the triggering incident was Y-G fault in 765kV Ariyalur NCPS Line-2. At Ariyalur end, the fault was sensed in Z2 carrier aided trip, AR operated and 3ph tripped due to persistent fault. At NCPS end, the fault was sensed in Z1, AR operated and tripped due to persistent fault. Tripping of the only source (765kV Ariyalur NCPS Line-2) led to complete outage of 765kV NCPS Pooling station and 765kV NCTPS Generating station. During the event NCTPS ST3 U1 was in service and was generating around 514 MW and tripped on low forward power protection (as per FIR) and leading to generation loss of 514 MW.

- DR Analysis:

765KV-ARIYALUR-NCPS-2

|  | ARIYALUR - 765KV | NCPS - 765KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:09-06-2026 20:10:49.457 10 CARR REC-1 Any Trip, Aided 1 Trip B CB1 AR 1p InProg, AR Start, ARIP, L18 AR INI Y, CB2 AR 1p InProg L15 TIE CB Y OPN L2 MN CB Y OPN Auto Close CB1, R14 MCB AR CLS Any Trip, TOR Trip Zone 2, R7 MAIN GR-A TRP, R8 TIE GR-A TRP, R30 MN GR-B TRP, R31 TIE GR-B TRP CB1 AR Lockout, CB2 AR Lockout 10 CARR REC-1 Aided 1 Trip B AR Start L20 MN AR BLK L4 86A OPTD, L4 86A OPTD, L21 TIE AR BLK L18 AR INI Y L1 MN CB R OPN, L3 MN CB B OPN, L14 TIE CB R OPN L16 TIE CB B OPN L2 MN CB Y OPN Ir (max): 0.99 kA Iy (max): 5.06 kA Ib (max): 1.09 kA Vr (max): 804.22 kV Vy (max): 549.65 kV Vb (max): 521.50 kV | DR trigger time : 20:10:50.613 Y-G fault Z1 AR operated ToR |

NCTPS STG3 - 765KV

|  | NCTPS STG3 - 765KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:09-06-2026 20:11:18.806 F<2 Trip, Any Trip V/Hz>4 Trip 4 HVCB/GCB OPEN Power2 Trip Ir (max): 5.38 kA Iy (max): 5.39 kA Ib (max): 5.53 kA Vr (max): 17.48 kV Vy (max): 17.32 kV Vb (max): 17.28 kV |

NCPS - 765KV

|  | NCPS - 765KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | Supply Failure |

- A) PMU Analysis:

From the PMU plot, persistent Y-G fault is observed during the event.

B) SCADA Analysis:

From the SCADA data, tripping of the line can be observed.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):  Nil

- Action Taken/Remedial Measures (सुधारात्मक उपाय):  Nil

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | TNPGCL, TANTRANSCO |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 |  |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: