# Draft Report on grid event Complete Outage of 220kV HSR SS, 220kV Nimhans SS, 220kV Koramangala SS, 220kV Nagnathpura SS of KPTCL in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 26-06-2026 16:54

# Event Summary (घटना का सारांश):

# As per the reports submitted, the triggering incident was Y-G fault in 220kV Mylasandra HSR Line-2 and the line tripped. At the same time, 220kV Mylasandra HSR Line-1 and 220kV Mylasandra Nagnathpura lines tripped at HSR end and Nagnathpura end on Zone-1 over reach and SOTF maloperation. This led to over loading of 220kV HSR EPIP line and the line was eventually hand tripped due to arcing. Tripping of all these lines led to complete outage of all radial stations namely 220kV HSR SS, 220kV Nimhans SS, 220kV Koramangala SS, 220kV Nagnathpura SS.

- Time and Date of the Event (घटना का समय और दिनांक:  10-06-2026 10:53

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): KARNATAKA

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Karnataka State Demand (MW) | 12314 | 11558 |
| Karnataka State Generation (MW) | 9315 | 9310 |
| Grid Frequency (Hz) | 50.12 | 50.19 |
| SR Demand (MW) | 56839 | 56199 |
| SR Generation (MW) | 57369 | 57218 |

*Pre and post data of 1 minute before and after the event

| Elements under outage | - 220KV-EDC-NIMHANS-1 |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

At Koramanagala SS:

Prior to the incident 220kV NIMHANS -EDC line was kept open as per SLDC instructions hence NIMHANS was radial on HSR source.

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 0.0 MW | 501.0 MW |

- Duration of interruption (रुकावट की अवधि):  0 hours, 17 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 220KV-NAGNATHPURA-HSR-1

      - 220KV-HSR-MYLASANDRA-2

      - 220KV-MYLASANDRA-HSR-1

      - 220KV-EPIP-HSR-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

During antecedent conditions, 220kV 220kV NIMHANS -EDC line was kept open as per SLDC instructions. As per the reports submitted, the triggering incident was Y-G fault in 220kV Mylasandra HSR Line-2  due to arcing in Y phase CVT in the line at Mylasandra end. At Mylasansadra end, the fault was sensed in zone-1 and the line tripped. At HSR end, the fault was sensed in zone-2 and carrier was not received. The line tripped with a delay of around 350ms. At the same time, 220kV Mylasandra HSR Line-1 and 220kV Mylasandra Nagnathpura lines tripped at HSR end and Nagnathpura end on Zone-1 over reach and SOTF maloperation in main-2 relay. Further, Due to 86 trip continuous high in 220kV Naganathpura -HSR line at Naganathpura end, when load current in 220kV Nagnathpura HSR line crossed 0.2 A secondary, LBB operated at 220kV Naganathpura SS and all the elements tripped leading to complete outage of 220kV Nagnathpura SS.

After tripping of above lines. the current flow in 220kV HSR EPIP became around 1040 A which subsequently reduced up to 620A after Naganathpura bus tripping and load relief obtained at HSR due to SPS operation(as reported).

Even after the load relief, 220kV HSR EPIP line remained over loaded and the line was eventually hand tripped due to arcing. Tripping of all these lines led to complete outage of all radial stations namely 220kV HSR SS, 220kV Nimhans SS, 220kV Koramangala SS, 220kV Nagnathpura SS.

- DR Analysis:

NAGNATHPURA - 220KV

|  | NAGNATHPURA - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | Loss of power supply |

KORAMANGALA - 220KV

|  | KORAMANGALA - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | Loss of power supply |

NIMHANS - 220KV

|  | NIMHANS - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | Loss of power supply |

HSR - 220KV

|  | HSR - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | Loss of power supply DR of 220kV HSR EPIP line. DR Trigger Time:10-06-2026 10:53:46.397 Any Start I> Start Any B Ir (max): 0.78 kA Iy (max): 0.94 kA Ib (max): 0.72 kA Vr (max): 122.02 kV Vy (max): 123.95 kV Vb (max): 122.99 kV DR Trigger Time:10-06-2026 10:52:42.808 Relay PICKUP BUS_FAULT Relay TRIP >Trig.Wave.Cap., 21 PU Z3, Trip-Y-Ph, Zone1 Trip, Zone1 Star, Zone2 Star, Carier Snd Y-Ph Initi Trip-R-Ph, Trip-B-Ph 3Ph GR A/B 3Ph LBB In B-Ph Initi R-Ph Initi Ir (max): 0.86 kA Iy (max): 37.00 kA Ib (max): 36.38 kA Vr (max): 123.02 kV Vy (max): 121.48 kV Vb (max): 127.57 kV |

220KV-HSR-MYLASANDRA-2

|  | HSR - 220KV | MYLASANDRA - 220KV |
| --- | --- | --- |
| Time Sync Issue | Yes | Yes |
| DR Analysis | DR Trigger Time:10-06-2026 10:37:06.978 NTRL DIR OC1 FWD GND DIST Z3 PKP, GND DIST Z3 PKP GND DIST Z2 PKP OSC TRIGGER ON (VO40), GND DIST Z1 OP, AR LOCKOUT ON (VO25), DIST YPH TRIP ON (VO16), GND DIST Z1 PKP, NEUTRAL TOC1 PKP R22 M2 Y-PH TRIP CLOSED (CO22), R19 GEN TRIP CLOSED (CO19), R2 M1 Y-PH TRIP RLY CLOSED (CO2), R4 TO 86A RLY CLOSED (CO4), R5 TO 86B RLY CLOSED (CO5), R10 AR LOCKOUT ANN CLOSED (CO10) L8 86B OPTD ON (CI8) L20 86A OPTD ON (CI20) L1 CB R-OPEN ON (CI1), L3 CB B-PH OPEN ON (CI3) L2 CB Y-PH OPEN ON (CI2) Ir (max): 0.68 kA Iy (max): 2.62 kA Ib (max): 0.48 kA Vr (max): 123.29 kV Vy (max): 123.81 kV Vb (max): 123.97 kV | DR of 220kV HSR Mylasandra Line-2 DR Trigger Time:10-06-2026 10:37:06.978 NTRL DIR OC1 FWD GND DIST Z3 PKP, GND DIST Z3 PKP GND DIST Z2 PKP OSC TRIGGER ON (VO40), GND DIST Z1 OP, AR LOCKOUT ON (VO25), DIST YPH TRIP ON (VO16), GND DIST Z1 PKP, NEUTRAL TOC1 PKP R22 M2 Y-PH TRIP CLOSED (CO22), R19 GEN TRIP CLOSED (CO19), R2 M1 Y-PH TRIP RLY CLOSED (CO2), R4 TO 86A RLY CLOSED (CO4), R5 TO 86B RLY CLOSED (CO5), R10 AR LOCKOUT ANN CLOSED (CO10) L8 86B OPTD ON (CI8) L20 86A OPTD ON (CI20) L1 CB R-OPEN ON (CI1), L3 CB B-PH OPEN ON (CI3) L2 CB Y-PH OPEN ON (CI2) Ir (max): 0.68 kA Iy (max): 2.62 kA Ib (max): 0.48 kA Vr (max): 123.29 kV Vy (max): 123.81 kV Vb (max): 123.97 kV |

220KV-MYLASANDRA-HSR-1

|  | MYLASANDRA - 220KV | HSR - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | Yes |
| DR Analysis | Line was holding | DR Trigger Time:10-06-2026 10:37:06.978 NTRL DIR OC1 FWD GND DIST Z3 PKP, GND DIST Z3 PKP GND DIST Z2 PKP OSC TRIGGER ON (VO40), GND DIST Z1 OP, AR LOCKOUT ON (VO25), DIST YPH TRIP ON (VO16), GND DIST Z1 PKP, NEUTRAL TOC1 PKP R22 M2 Y-PH TRIP CLOSED (CO22), R19 GEN TRIP CLOSED (CO19), R2 M1 Y-PH TRIP RLY CLOSED (CO2), R4 TO 86A RLY CLOSED (CO4), R5 TO 86B RLY CLOSED (CO5), R10 AR LOCKOUT ANN CLOSED (CO10) L8 86B OPTD ON (CI8) L20 86A OPTD ON (CI20) L1 CB R-OPEN ON (CI1), L3 CB B-PH OPEN ON (CI3) L2 CB Y-PH OPEN ON (CI2) Ir (max): 0.68 kA Iy (max): 2.62 kA Ib (max): 0.48 kA Vr (max): 123.29 kV Vy (max): 123.81 kV Vb (max): 123.97 kV |

220KV-NAGNATHPURA-MYLASANDRA-2

|  | NAGNATHPURA - 220KV | MYLASANDRA - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR trigger time:11:51:13.5 SOTF/TOR trip 3P trip | Line was holding |

220KV-NAGNATHPURA-HSR-1

|  | NAGNATHPURA - 220KV | HSR - 220KV |
| --- | --- | --- |
| Time Sync Issue | Yes | No |
| DR Analysis | DR Trigger Time:10-06-2026 11:52:42.887 Any Start Z3 Ir (max): 1.62 kA Iy (max): 6.39 kA Ib (max): 0.83 kA Vr (max): 122.72 kV Vy (max): 103.65 kV Vb (max): 122.69 kV DR Trigger Time:10-06-2026 12:41:07.999 13.SOTF INN 1.CB R PH CLOSE 2.CB Y PH CLOSE, 3.CB B PH CLOSE Ir (max): 0.01 kA Iy (max): 0.01 kA Ib (max): 0.02 kA Vr (max): 141.96 kV Vy (max): 108.02 kV Vb (max): 128.64 kV DR Trigger Time:10-06-2026 10:54:14.169 Start 3-Ph Bay3 Protec Startup CBF Retrip, BZ1 CBF Op DR Trigger Time:10-06-2026 11:51:13.556 Any Start Z2, Relay 4, Relay 5, SOTF/TOR Trip, Any Trip Z3 1.CB R PH CLOSE, 2.CB Y PH CLOSE, 3.CB B PH CLOSE, 8.86 A/B OPTD Ir (max): 2.19 kA Iy (max): 6.30 kA Ib (max): 1.07 kA Vr (max): 124.35 kV Vy (max): 124.18 kV Vb (max): 123.35 kV | Line was holding |

- A) PMU Analysis:

From the PMU, Y-G fault is observed during the event with a delay of around 350ms.

B) SCADA Analysis:

From the SCADA plots. loss of power supply to 220kV HSR SS and tripping of 220kV HSR EPIP line can be observed.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| KPTCL | 1. Non operation of A/R in 220kV HSR Mylasandra Line-2. 2. Non-reciept of carrier signal in 220kV HSR Mylasandra Line-2 at HSR end. 3. Maloperation of LBB relay at Nagnathpura SS. 4. Zone-1 over reach in 220kV HSR Mylasandra Line-1 at HSR end. |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| KPTCL | Settings of Mylasandra line-1 at HSR end is under review PLCC issue at HSR end will be rectified by TCD wing At Naganathpura detail testing of Mylasandra line Main-2 relay, BBP relay etc is scheduled on 20.06.2026 Operation wing have been informed to rectify GPS time synch issue at HSR and Naganathpura Substations. |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

Restoration: Supply restored to Nimhans,Koramangala at 11.10 Hrs by closing EDC-NIMHANS line

Supply restored to Naganathpura and HSR through Hoody source at 11.22 Hrs.

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | KPTCL |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | KPTCL |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) | KPTCL |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: