# Draft Report on grid event Complete Outage of 400kV ILFS of ITPCL in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 04-06-2026 19:48

# Event Summary (घटना का सारांश):

# 400kV ILFS is only connected to NAGAPATTNAM_PS through 400KV-ILFS-NAGAPATTNAM_PS-1&2 lines. In the antecedent conditions, 400KV-ILFS-NAGAPATTNAM_PS-2 was under outage due to planned shutdown and hence 400kV ILFS was radially connected to NAGAPATTNAM_PS prior to the event through 400KV-ILFS-NAGAPATTNAM_PS-1. The triggering incident was R-G fault in 400KV-ILFS-NAGAPATTNAM_PS-1. Tripping of the only connected line led to complete outage of 400KV-ILFS and a generation loss of around 557MW.

- Time and Date of the Event (घटना का समय और दिनांक:  22-05-2026 12:45

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): TAMILNADU

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| TamilNadu State Demand (MW) | 16546 | 16462 |
| TamilNadu State Generation (MW) | 15351 | 15350 |
| Grid Frequency (Hz) | 50.04 | 50.04 |
| SR Demand (MW) | 59567 | 59503 |
| SR Generation (MW) | 62240 | 61832 |

*Pre and post data of 1 minute before and after the event

| Elements under outage | - 400KV-ILFS-NAGAPATTNAM_PS-2 |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Windy |

ILFS End :-

Unit-2 in service condition at 557MW generation & unit-1 under Shutdown condition

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 557.0 MW | 0.0 MW |

- Duration of interruption (रुकावट की अवधि):  0 hours, 35 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 400KV-ILFS-NAGAPATTNAM_PS-1

      - 420KV/22KV ILFS-GT-2

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

400kV ILFS is only connected to NAGAPATTNAM_PS through 400KV-ILFS-NAGAPATTNAM_PS-1&2 lines. In the antecedent conditions, 400KV-ILFS-NAGAPATTNAM_PS-2 was under outage due to planned shutdown and hence 400kV ILFS was radially connected to NAGAPATTNAM_PS prior to the event through 400KV-ILFS-NAGAPATTNAM_PS-1.

The triggering incident was R-G fault in 400KV-ILFS-NAGAPATTNAM_PS-1. At NAGAPATTNAM_PS end, the fault was sensed in Z1 and R-pole opened, carrier was sent to remote end (as per DR), AR operated after around 1s and was successful and the line was holding. At ILFS, the fault was sensed in Z2, however the carrier was not received from remote end and continued to feed the fault and 3ph tripped on Z2 time trip. Tripping of the only connected line during the event (400KV-ILFS-NAGAPATTNAM_PS-1) at ILFS end led to complete outage of 400KV-ILFS of ITPCL. During the event, ILFS U2 was generating around 557MW and tripped due to Low forward power due to the loss of evacuation lines and led to a generation loss of around 557MW. The frequency plot observed as per the DR available at ILFS U2 is as below.

- DR Analysis:

ILFS - 400KV

|  | ILFS - 400KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:22-05-2026 12:45:10.271 Relay PICKUP Diff picked up Pf< TRIP, Relay TRIP Ir (max): 31.57 kA Iy (max): 18.28 kA Ib (max): 40.04 kA Vr (max): 14.58 kV Vy (max): 14.63 kV Vb (max): 14.61 kV DR Trigger Time:22-05-2026 12:45:10.186 Relay PICKUP Diff picked up Pf< TRIP, Relay TRIP f4 TRIP Ir (max): 31.50 kA Iy (max): 18.16 kA Ib (max): 40.21 kA Vr (max): 14.61 kV Vy (max): 14.67 kV Vb (max): 14.65 kV |

400KV-ILFS-NAGAPATTNAM_PS-1

|  | ILFS - 400KV | NAGAPATTNAM_PS - 400KV |
| --- | --- | --- |
| Time Sync Issue | No | Yes |
| DR Analysis | DR Trigger Time:22-05-2026 12:45:10.222 EF Pickup, Relay PICKUP, Relay PICKUP E Dis.Pickup L1, Dis.Pickup E, Dis. forward, Relay PICKUP L1 Relay TRIP L1, Relay TRIP L2, Relay TRIP L3, Relay TRIP Ir (max): 3.41 kA Iy (max): 1.73 kA Ib (max): 0.79 kA Vr (max): 227.78 kV Vy (max): 229.94 kV Vb (max): 229.84 kV DR Trigger Time:22-05-2026 12:45:10.222 EF Pickup, Relay PICKUP, Relay PICKUP E Dis.Pickup L1, Dis.Pickup E, Dis. forward, Relay PICKUP L1 Relay TRIP L1, Relay TRIP L2, Relay TRIP L3, Relay TRIP Ir (max): 3.41 kA Iy (max): 1.73 kA Ib (max): 0.79 kA Vr (max): 227.78 kV Vy (max): 229.94 kV Vb (max): 229.84 kV | DR Trigger Time:22-05-2026 12:45:09.427 M2 Z2 STR, M2Z3_ST M2_TRIP, M2 Z1 OPTD, M12CRSD M1_TRIP M CB_RO T CB_RO Ir (max): 10.41 kA Iy (max): 1.70 kA Ib (max): 0.78 kA Vr (max): 238.26 kV Vy (max): 261.91 kV Vb (max): 240.31 kV DR Trigger Time:22-05-2026 12:45:09.423 M1_TRIP, M1Z1_OP, M1Z2_ST, M1Z3_ST, M12CRSD M2_TRIP M_CB_RO T_CB_RO M_CB_AR T_CB_AR Ir (max): 10.57 kA Iy (max): 1.73 kA Ib (max): 0.79 kA Vr (max): 238.07 kV Vy (max): 262.98 kV Vb (max): 244.39 kV DR Trigger Time:22-05-2026 12:45:09.427 M2 Z2 STR, M2Z3_ST M2_TRIP, M2 Z1 OPTD, M12CRSD M1_TRIP M CB_RO T CB_RO Ir (max): 10.41 kA Iy (max): 1.70 kA Ib (max): 0.78 kA Vr (max): 238.26 kV Vy (max): 261.91 kV Vb (max): 240.31 kV |

- A) PMU Analysis:

From the PMU plot, dip in R-phase voltage is observed indicating R-G fault during the event.

B) SCADA Analysis:

From the SCADA plot, generation loss of 557MW is observed during the event.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| ILFS | 1. Non receipt of carrier and tripping of the line in Z2 time trip needs review 2. Non furnishing of detailed report needs review |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| ILFS | 1. Tree removal below the transmission line corridor taken up. |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

22-05-2026 12:49

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | ILFS |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | ILFS, PGCIL SR-2 |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) | ILFS |
| 4 | Any other non-compliance | IEGC section 17.3 | PGCIL SR-2 |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: