# Draft Report on grid event Complete outage of 765kV NCPS of TANTRANSCO and 765kV NCTPS Stage-3Generating station of TNPGCL in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 29-06-2026 09:52

# Event Summary (घटना का सारांश):

# 765kV NCTPS Stage-II generating station is evacuating power through 765 kV NCPS–NCTPS STG3-1 and 765 kV NCPS–NCTPS STG3-2, while 765 kV Ariyalur–NCPS-1 and 765 kV Ariyalur–NCPS-2 were also in service. The triggering incident is a issuance of a spurious Direct Trip (DT) signal from the Main-2 at NCPS to the remote ends, resulting in the tripping of 765 kV NCPS–NCTPS STG3-1 and 2 at the NCTPS end and 765 kV Ariyalur–NCPS-1 and 2 at the Ariyalur end. This led to complete outage of 765kV NCPS of TANTRANSCO and 765kV NCTPS Stage-3Generating station of TNPGCL

- Time and Date of the Event (घटना का समय और दिनांक:  20-06-2026 16:07

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): TAMILNADU

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| TamilNadu State Demand (MW) | 18374 | 18741 |
| TamilNadu State Generation (MW) | 9905 | 9805 |
| Grid Frequency (Hz) | 50.09 | 49.99 |
| SR Demand (MW) | 61164 | 61253 |
| SR Generation (MW) | 53516 | 53228 |

*Pre and post data of 1 minute before and after the event

| Elements under outage | - NCTPS STG3 - 765KV - Bus 1 - NCTPS STG3 - 765KV - Bus 2 - 765KV/27KV NCTPS STG3-GT-1 - NCTPS STG3 - UNIT 1 |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 522.0 MW | 0.0 MW |

- Duration of interruption (रुकावट की अवधि):  2 hours, 13 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 765KV-NCPS-NCTPS STG3-1

      - 765KV-NCPS-NCTPS STG3-2

      - 765KV/27KV NCTPS STG3-GT-1

      - NCTPS STG3 - UNIT 1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

765kV NCTPS Stage-II generating station is evacuating power through 765 kV NCPS–NCTPS STG3-1 and 765 kV NCPS–NCTPS STG3-2, while 765 kV Ariyalur–NCPS-1 and 765 kV Ariyalur–NCPS-2 were also in service. The triggering incident is a issuance of a spurious Direct Trip (DT) signal from the Main-2 at NCPS to the remote ends, resulting in the tripping of 765 kV NCPS–NCTPS STG3-1 and 2 at the NCTPS end and 765 kV Ariyalur–NCPS-1 and 2 at the Ariyalur end. This led to complete outage of 765kV NCPS of TANTRANSCO and 765kV NCTPS Stage-3Generating station of TNPGCL

- DR Analysis:

765KV-ARIYALUR-NCPS-1

|  | ARIYALUR - 765KV | NCPS - 765KV |
| --- | --- | --- |
| Time Sync Issue | Yes | No |
| DR Analysis | DR Trigger Time:20-06-2026 16:07:42.028 ANY TRIP ON (VO41), 21.DT RC-2 ON (CI21) TRIP PHASE A, TRIP PHASE B, TRIP PHASE C, TRIP 3-POLE 14.MN GRP-A TRP CLOSED (CO14), 15.TIE GRP-A TRP CLOSED (CO15) 19.MN AR BLK ON (CI19), 20.T AR BLK ON (CI20) 1.MN CB RPH OPN ON (CI1), 2.MN CB YPH OPN ON (CI2), 3.MN CB BPH OPN ON (CI3), 12.GRP-B OPTD ON (CI12), 13. T CB RPH OPN ON (CI13), 14.T CB YPH OPN ON (CI14), 15.T CB BPH OPN ON (CI15) OPEN POLE OP A OPEN POLE OP B OPEN POLE OP C OPEN POLE OP A OPEN POLE OP A OPEN POLE OP A OPEN POLE OP A OPEN POLE OP A OPEN POLE OP A OPEN POLE OP C PHASE UV1 OP Ir (max): 0.34 kA Iy (max): 0.45 kA Ib (max): 0.37 kA Vr (max): 611.73 kV Vy (max): 575.97 kV Vb (max): 644.39 kV |  |

765KV-ARIYALUR-NCPS-2

|  | ARIYALUR - 765KV | NCPS - 765KV |
| --- | --- | --- |
| Time Sync Issue | Yes | No |
| DR Analysis | DR Trigger Time:20-06-2026 16:07:42.027 ANY TRIP ON (VO41), 21.DT RC-2 ON (CI21) TRIP PHASE A, TRIP PHASE B, TRIP PHASE C, TRIP 3-POLE 14.MN GRP-A TRP CLOSED (CO14), 15.TIE GRP-A TRP CLOSED (CO15) 19.MN AR BLK ON (CI19), 20.T AR BLK ON (CI20) 12.GRP-B OPTD ON (CI12) 1.MN CB RPH OPN ON (CI1), 2.MN CB YPH OPN ON (CI2), 3.MN CB BPH OPN ON (CI3), 13. T CB RPH OPN ON (CI13), 15.T CB BPH OPN ON (CI15) 14.T CB YPH OPN ON (CI14) OPEN POLE OP B OPEN POLE OP C OPEN POLE OP A ANY TRIP ON (VO41), 21.DT RC-2 ON (CI21) TRIP PHASE A, TRIP PHASE B OPEN POLE OP C OPEN POLE OP A OPEN POLE OP A OPEN POLE OP A OPEN POLE OP C OPEN POLE OP A OPEN POLE OP C PHASE UV1 OP Ir (max): 0.34 kA Iy (max): 0.31 kA Ib (max): 0.37 kA Vr (max): 610.16 kV Vy (max): 574.63 kV Vb (max): 643.37 kV |  |

NCTPS STG3 - 765KV

|  | NCTPS STG3 - 765KV |
| --- | --- |
| Time Sync Issue | Yes |
| DR Analysis | DR Trigger Time:20-06-2026 16:08:10.016 F<2 Trip, Any Trip Power2 Trip V/Hz>4 Trip 4 HVCB/GCB OPEN Power2 Trip Ir (max): 6.33 kA Iy (max): 6.33 kA Ib (max): 6.34 kA Vr (max): 16.91 kV Vy (max): 16.84 kV Vb (max): 16.76 kV |

NCPS - 765KV

|  | NCPS - 765KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis |  |

765KV-NCPS-NCTPS STG3-1

|  | NCPS - 765KV | NCTPS STG3 - 765KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis |  |  |

765KV-NCPS-NCTPS STG3-2

|  | NCPS - 765KV | NCTPS STG3 - 765KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis |  |  |

- A) PMU Analysis:

From the PMU data, the triggering incident was observed at 16:07:41 hrs. During this incident, a change in the voltage of Ariyalur Bus-2 was observed

B) SCADA Analysis:

From the SCADA data, a change in power flow on the 765 kV Ariyalur–NCPS-2 line was observed at the triggering incident 16:07 hrs.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| TANTRANSCO | Direct Trip (DT) signal from the Main-2 DTPC (NSD570) at NCPS needs review. |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| TANTRANSCO | 1. Main.2 DTPC kept out of service & referred to OEM( M/s. ABB) 2. Frequent SNTP failure observed in all DTPcs. This is also referred to OEM for rectification. |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

765kV NCPS_Ariyalur_1:20-06-2026 at 18:20hrs

765kV NCPS_Ariyalur_2:20-06-2026 at 18:24hrs

765kV NCPS_NCTPS Stage.3_1:20-06-2026 at 21:15hrs

765kV NCPS_NCTPS Stage.3_2:20-06-2026 at 21:17hrs

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) |  |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | TNPGCL |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: