# Draft Report on grid event Complete Outage of 220kV Garividi SS, 220kV Bobbili SS, 220kV Tekkali SS of APTRANSCO in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 05-06-2026 18:21

# Event Summary (घटना का सारांश):

# During antecedent conditions, 220kV Maradam Bobbili line-2 was under shutdown and 220kV Garividi Bobbili Line-1 was in hand tripped condition at Garividi end. 220kV Bobbili SS, 220kV Garividi SS and 220kV Tekkali SS are being radially fed from 220kV Maradam Bibbili Line-1 and 220kV Maradam Garividi Line-1&2. As per the reports submitted, 220kV Maradam Bobbili Line-1 tripped on B-G fault at 11:48hrs, 220kV Maradam Garividi Line-2 tripped on B-G fault at 11:56hrs and 220kV Maradam Garividi Line-1 tripped at 11:57hrs on B-G fault. Tripping of all these lines led to complete outage of 220kV Garividi SS, 220kV Bobbili SS, 220kV Tekkali SS

- Time and Date of the Event (घटना का समय और दिनांक:  23-05-2026 11:57

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): ANDHRA PRADESH

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Andhra Pradesh State Demand (MW) | 11252 | 11280 |
| Andhra Pradesh State Generation (MW) | 8619 | 8611 |
| Grid Frequency (Hz) | 49.95 | 49.95 |
| SR Demand (MW) | 58332 | 58348 |
| SR Generation (MW) | 59042 | 58916 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Thunders , Windy |

At Garividi SS:

At 220kV Bobbili SS:

At 220kV Tekkali SS:

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 0.0 MW | 615.0 MW |

- Duration of interruption (रुकावट की अवधि):  0 hours, 13 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 220KV-GARIVIDI-MARADAM-1

      - 220KV-GARIVIDI-MARADAM-2

      - 220KV-BOBBILI-MARADAM-1

      - 220KV-GARIVIDI-BOBBILI-2

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

During antecedent conditions, 220kV Maradam Bobbili line-2 was under shutdown for Breakdown rectification works from 22.05.2026@18:31hrs and 220kV Garividi Bobbili Line-1 was in hand tripped condition at Garividi end to limit Load on 220kV Bobbili- Maradam-1 Line. 220kV Bobbili SS, 220kV Garividi SS and 220kV Tekkali SS are being radially fed from 220kV Maradam Bibbili Line-1 and 220kV Maradam Garividi Line-1&2. As per the reports submitted, at 11:48hrs, B-G fault was observed in 220kV Maradam Bobbili Line-1. At both ends, the fault was sensed in zone-1 and B-pole opened. At Maradam end, A/R operated and the line tripped on persistent fault. At Bobbili end, though A/R close signal is observed, A/R lockout operated with no persiting fault and the line tripped. At 11:56hrs, B-G fault was observed in 220kV Maradam Garividi Line-2 due to suspected over loading and sag in the line. At both ends, the fault was sened in zone-1. A/R operated and the line tripped on persistent fault. At 11:57hrs, B-G fault was observed in 220kV Maradam Garividi Line-1. At Maradam end, the fault was sensed in zone-1. A/R operated and the line was holding. At Garividi end, the fault was sensed in carried aided zone-2. A/R did not operate and line tripped on suspected PD. Tripping of all these lines led to complete outage of 220kV Garividi SS, 220kV Bobbili SS, 220kV Tekkali SS

- DR Analysis:

GARIVIDI - 220KV

|  | GARIVIDI - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | Loss of power supply |

BOBBILI - 220KV

|  | BOBBILI - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | Loss of power supply |

TEKKALI - 220KV

|  | TEKKALI - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | Loss of power supply |

220KV-GARIVIDI-MARADAM-1

|  | GARIVIDI - 220KV | MARADAM - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | Yes |
| DR Analysis | DR Trigger Time:23-05-2026 11:47:05.257 PHASE SELECT VOID BREAKER 1 CLOSED PHASE SELECT CG, PHASE SELECT SLG PHASE SELECT AB, PHASE SELECT MULTI-P SRC1 VT FF OP PHASE SELECT VOID PHASE SELECT AB, PHASE SELECT MULTI-P PHASE SELECT VOID BREAKER 1 OPEN PHASE SELECT AB, PHASE SELECT MULTI-P TRIPBUS 2 OP, AR LO PHASE SELECT VOID PHASE SELECT MULTI-P AR BKR1 BLK PHASE SELECT VOID Ir (max): 0.93 kA Iy (max): 0.94 kA Ib (max): 0.02 kA Vr (max): 132.16 kV Vy (max): 133.87 kV Vb (max): 235.92 kV DR Trigger Time:23-05-2026 11:56:18.202 Z3 Z2 DIST Trip C, DIST. Chan Recv A/R 1P In Prog CB Aux C (52-B) Z3 A/R Trip 3P A/R Close CB Aux C (52-A) CB Aux C (52-B) CB Aux A (52-B), CB Aux B (52-B) A/R Lockout Ir (max): 1.01 kA Iy (max): 1.62 kA Ib (max): 1.54 kA Vr (max): 125.98 kV Vy (max): 128.79 kV Vb (max): 127.05 kV | DR Trigger Time:23-05-2026 11:57:50.095 Z2 START, Z3 START, Z4 START GENERAL TR, TRIP BPH, Z1 TRIP, Z1 START, CS, 1 PH LBB AR START MCB B OP AR OPTD Ir (max): 0.98 kA Iy (max): 1.57 kA Ib (max): 5.33 kA Vr (max): 130.22 kV Vy (max): 130.00 kV Vb (max): 224.60 kV |

220KV-GARIVIDI-MARADAM-2

|  | GARIVIDI - 220KV | MARADAM - 220KV |
| --- | --- | --- |
| Time Sync Issue | Yes | No |
| DR Analysis | DR Trigger Time:23-05-2026 11:55:29.582 Any Start Any Trip, DIST Trip C, DIST Fwd, Z1, Z2, Z3 Any Pole Dead Any Trip, SOTF/TOR Trip DIST Fwd Z1, Z2, Z3 Any Pole Dead All Pole Dead DIST. Chan Recv, DIST. Chan Recv, DIST UNB CR Ir (max): 0.64 kA Iy (max): 1.21 kA Ib (max): 5.73 kA Vr (max): 133.24 kV Vy (max): 129.75 kV Vb (max): 129.65 kV DR Trigger Time:23-05-2026 11:56:57.519 AR-START, BusAR INPROGR AR-PREP3P 86A_OPTD, 86B_OPTD AR BLOCK 86B_OPTD M_CB_B_OPEN M_CB_R_OPEN, M_CB_Y_OPEN CAR_REC_CH1 Ir (max): 0.62 kA Iy (max): 1.18 kA Ib (max): 5.60 kA Vr (max): 129.73 kV Vy (max): 127.00 kV Vb (max): 126.73 kV | DR Trigger Time:23-05-2026 11:56:18.360 T1 1ph Fault Z3 Z2 AR OPTD MAIN CB B PH CLS T1, 1ph Fault Any Trip, Any Trip A, Any Trip B, Any Trip C, Z1, DIST Sig. Send, SOTF/TOR Trip 86-2 OPTD, 86-2 OPTD Z2 Ir (max): 0.63 kA Iy (max): 1.21 kA Ib (max): 4.69 kA Vr (max): 131.86 kV Vy (max): 132.39 kV Vb (max): 131.88 kV |

220KV-GARIVIDI-BOBBILI-1

|  | GARIVIDI - 220KV | BOBBILI - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | Loss of power supply | Loss of power supply |

220KV-GARIVIDI-BOBBILI-2

|  | GARIVIDI - 220KV | BOBBILI - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | Loss of power supply | Loss of power supply |

220KV-BOBBILI-MARADAM-1

|  | BOBBILI - 220KV | MARADAM - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:23-05-2026 11:48:50.707 Any Start Z2 Any Trip, DIST Trip C, Z1, Any Int. Trip C DIST. Chan Recv, 6_CR RXD CH1/2, 3_CB B-PH OPEN A/R Close, A/R Reclaim SOTF Enable 3_CB B-PH OPEN Any Trip, Any Int. Trip A, Any Int. Trip B, Any Int. Trip C, AR Lockout Shot> DIST. Chan Recv, 6_CR RXD CH1/2 1_CB R-PH OPEN, 2_CB Y-PH OPEN Ir (max): 0.84 kA Iy (max): 1.78 kA Ib (max): 4.77 kA Vr (max): 133.96 kV Vy (max): 132.26 kV Vb (max): 131.45 kV DR Trigger Time:23-05-2026 11:48:50.734 EF Pickup, Relay PICKUP, Relay PICKUP L3, Relay PICKUP E Dis.Pickup L3, Dis.Pickup E, Dis. forward Relay TRIP L1, Relay TRIP L2, Relay TRIP L3, Relay TRIP | DR Trigger Time:23-05-2026 11:48:50.222 Z2 START, Z3 START, Z4 START GENERAL TR, TRIP B PH, Z1 TRIP, Z1 START, CS, 1PH LBB IN MCB B OPEN CR Z2 START, Z3 START, Z4 START GENERAL TR, TRIP B PH, Z1 TRIP, Z1 START, CS, 1PH LBB IN AR BLOCK MCB B OPEN MCB R OPEN MCB Y OPEN Ir (max): 0.82 kA Iy (max): 1.73 kA Ib (max): 9.82 kA Vr (max): 129.53 kV Vy (max): 133.38 kV Vb (max): 161.73 kV |

220KV-BOBBILI-MARADAM-2

|  | BOBBILI - 220KV | MARADAM - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | Under shutdown | Under shutdown |

- A) PMU Analysis:

From PMU dip in B-phase voltage is observed at 11:48hrs, 11:56hrs and 11:57hrs with no delayed fault clearance during the event.

B) SCADA Analysis:

From SCADA plot, tripping of 400kV Garividi Maradam Line-1&2 is observed.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| APTRANSCO | 1. Hand tripping of 220kV Garividi Bobbili Line-1 to limit Load on 220kV Bobbili- Maradam-1 Line needs review. 2. Non operation of A/R in 220kV Maradam Bobbili Line-1 at Bobbili end. 3. Non operation of A/R in 220kV Maradam Garividi Line-1 at Garividi end. |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):  Nil

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

Restored 220kV Supply to Garividi SS through 220kV Garividi-Maradam-1 feeder at 12:10hrs.

Restored 220kV Supply to Bobbili GC through 220kV Garividi-Bobbili GC-2 feeder at 12:10hrs.

Incoming Supply Restored to 220KV Tekkali SS from 220KV Garividi SS at 12:17hrs

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | APTRANSCO |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | APTRANSCO |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 | APTRANSCO |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: