# Draft Report on grid event Complete Outage of 400kV Vattem SS of TGTRANSCO in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 11-06-2026 11:22

# Event Summary (घटना का सारांश):

# During the antecedent conditions, 400 kV Yedula–Vattem Line-2 was under outage and 400 kV Vattem SS was being radially fed through 400 kV Yedula–Vattem Line-1. The triggering incident is the R-G fault in the line, during which OV St-2 was sensed at Vattem end and 3ph tripped and DT sent to remote end leading to 3ph tripped at Yedula end. Tripping of the only line connected to 400 kV Vattem SS, led to the complete outage of 400 kV Vattem SS of TGTRANSCO.

- Time and Date of the Event (घटना का समय और दिनांक:  24-05-2026 03:19

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): TELANGANA

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Telangana State Demand (MW) | 8749 | 8701 |
| Telangana State Generation (MW) | 3852 | 3836 |
| Grid Frequency (Hz) | 50.02 | 50.05 |
| SR Demand (MW) | 46305 | 46214 |
| SR Generation (MW) | 49987 | 49832 |

*Pre and post data of 1 minute before and after the event

| Elements under outage | - 400KV-VATTEM-UDDANDAPUR-1 - 400KV-VATTEM-UDDANDAPUR-2 - 400KV-YEDULA-VATTEM-2 |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 0.0 MW | 0.4 MW |

- Duration of interruption (रुकावट की अवधि):  3 hours, 7 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 400KV-YEDULA-VATTEM-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

400kV Vattem is connected through 400kV Yedula–Vattem-1&2 as 400kV Vattem-Uddandapur lines are still in commissioning stage. During the antecedent conditions, 400 kV Yedula–Vattem Line-2 was under outage and hence 400 kV Vattem SS was being radially fed through 400 kV Yedula–Vattem Line-1.

The triggering incident is the R-G fault in the line. At Yedula end, the fault was sensed in Z2, but the fault was not sensed at Vattem (as there is no fault contribution). During the fault the Y and B phase voltages were observed to increase at both Yedula and Vattem ends.

At Vattem end, the voltages reached around 1.4 times to around 326kV for more than 100ms during the fault leading to operation of OV St-2 operation and 3ph trip and DT was sent to remote end. At Yedula, 3ph tripped due to DT receipt (as per FIR)

Tripping of the only line connected to 400 kV Vattem SS, led to the complete outage of 400 kV Vattem SS of TGTRANSCO.

- DR Analysis:

400KV-YEDULA-VATTEM-1

|  | YEDULA - 400KV | VATTEM - 400KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:24-05-2026 03:19:22.984 ZONE-2 START, ZONE-3 START, ZONE-4 START OV-1 START 86B OPTD TIE 86B OPTD Ir (max): 10.52 kA Iy (max): 0.28 kA Ib (max): 0.31 kA Vr (max): 246.18 kV Vy (max): 332.58 kV Vb (max): 314.14 kV | DR Trigger Time:24-05-2026 03:19:22.945 V>1 Start V>2 Start Any Trip, IM Output 4, V>2 Trip L23 T 86A OPTD L1 M 86A OPTD L18 T CB OPEN Y L17 T CB OPEN R, L19 T CB OPEN B L12 M CB OPEN R, L13 M CB OPEN Y, L14 M CB OPEN B Ir (max): 0.17 kA Iy (max): 0.13 kA Ib (max): 0.14 kA Vr (max): 249.26 kV Vy (max): 377.99 kV Vb (max): 341.81 kV |

VATTEM - 400KV

|  | VATTEM - 400KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | Supply Failure. |

- A) PMU Analysis:

From PMU, dip in R-G fault is observed indicating R-G fault during the event with delayed fault clearance.

B) SCADA Analysis:

From SCADA tripping of 400kV Vattem Bus-1, Bus-2, Bus-3 can at 03:19:41 hrs on the 24-05-2026

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| TGTRANSCO | 1. Substantial increase in Y and B phases during the fault in R phase and leading to OV st-2 operation needs review. |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):  Nil

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

24/05/2026 06:26

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | TGTRANSCO |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | TGTRANSCO |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) | TGTRANSCO |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: