# Draft Report on grid event Complete Outage of 230kV NTPC Ettayapuram of NTPC in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 01-06-2026 12:52

# Event Summary (घटना का सारांश):

# 230kV NTPC_Ettayapuram is radially connected to TTGS through 230KV-TTGS-Ettayapuram-1 line. As per the reports submitted, the triggering incident was B-G fault in 230KV-TTGS-Ettayapuram-1 line and the line tripped. Tripping of the only connected line led to complete outage of 230kV NTPC Ettayapuram of NTPC.

- Time and Date of the Event (घटना का समय और दिनांक:  24-05-2026 13:21

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): TAMILNADU

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| TamilNadu State Demand (MW) | 15463 | 15482 |
| TamilNadu State Generation (MW) | 14629 | 14644 |
| Grid Frequency (Hz) | 49.98 | 49.95 |
| SR Demand (MW) | 51834 | 51745 |
| SR Generation (MW) | 57179 | 57286 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Rainy , Windy |

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) |  | Load Loss (MW) |
| --- | --- | --- |
| Solar | 144.0 MW | 0.0 MW |
| Wind | 0.0 MW |  |
| Others | 0.0 MW |  |
| Total | 144.0 MW |  |

- Duration of interruption (रुकावट की अवधि):  7 hours, 42 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 230KV-TTGS-Ettayapuram-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

230kV NTPC_Ettayapuram is radially connected to TTGS through 230KV-TTGS-Ettayapuram-1 line. As per the reports submitted, the triggering incident was B-G fault in 230KV-TTGS-Ettayapuram-1 line due to the failure of jumper supporting insulator at tower no.30 due to inclement weather. At Ettayapuram end, the fault was sensed in Line differential protection and the line tripped and DT was sent to the remote end. At TTGS end, the fault was sensed in Line Differential protection operated and B-pole opened. However after around 80ms, DT was received from Ettayapuram end and 3ph tripped. Tripping of the only connected line led to complete outage of 230kV NTPC Ettayapuram of NTPC.

- DR Analysis:

230KV-TTGS-Ettayapuram-1

|  | TTGS - 230KV | Ettayapuram - 230KV |
| --- | --- | --- |
| Time Sync Issue | No | Yes |
| DR Analysis | DR Trigger Time:24-05-2026 13:21:55.718 MAIN1_Z2_START, MAIN1_Z3_START, M1/2_CARR_SEND MAIN2_TRIP MAIN1_TRIP, Diff Trip, Diff Trip C MAIN_CB_B_OPEN DT_REC_CH1/2 3PH_GR_A/B_OPTD MAIN_CB_AR_LO MAIN_CB_R_OPEN, MAIN_CB_Y_OPEN Ir (max): 0.68 kA Iy (max): 0.54 kA Ib (max): 11.05 kA Vr (max): 133.00 kV Vy (max): 135.20 kV Vb (max): 132.64 kV | DR Trigger Time:24-05-2026 06:27:28.247 Diff Trip, Trip Output C, R3 87L1 B TRIP, Diff Trip, Diff Trip C Diff InterTrip B8 CARR REC CH1 Aided 1 Receive B11 CARR REC CH2 B5 MCB B-PH OPEN B10 DT SEND CH1 B4 MCB Y-PH OPEN B3 MCB R-PH OPEN Ir (max): 0.68 kA Iy (max): 0.54 kA Ib (max): 0.78 kA Vr (max): 143.38 kV Vy (max): 139.48 kV Vb (max): 133.04 kV |

Ettayapuram - 230KV

|  | Ettayapuram - 230KV |
| --- | --- |
| Time Sync Issue | Yes |
| DR Analysis | DR Trigger Time:24-05-2026 06:27:28.247 Diff Trip, Trip Output C, R3 87L1 B TRIP, Diff Trip, Diff Trip C Diff InterTrip B8 CARR REC CH1 Aided 1 Receive B11 CARR REC CH2 B5 MCB B-PH OPEN B10 DT SEND CH1 B4 MCB Y-PH OPEN B3 MCB R-PH OPEN Ir (max): 0.68 kA Iy (max): 0.54 kA Ib (max): 0.78 kA Vr (max): 143.38 kV Vy (max): 139.48 kV Vb (max): 133.04 kV |

- A) PMU Analysis:

From PMU, dip in B-phase is observed indicating B-G fault during the event.

B) SCADA Analysis:

From SCADA plot, tripping of 230KV-TTGS-Ettayapuram-1 line can be observed with a generation loss of around 144MW.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| NTPC | 1. Non operation of AR at Ettayapuram end needs review 2. Sending of DT to remote end for single phase fault needs review |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| NTPC | At tower no.30, the jumper supporting insulator got detached from the supporting structure due to heavy whirlwind present at the time of fault. The jumper support insualtor is fixed properly. Line is charged. |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

230KV-TTGS-Ettayapuram-1 tripped at 24/05/2026 13:21 and restored at 24/05/2026 21:03

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | NTPC |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | PGCIL SR-2, NTPC |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 | NTPC |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: