# Draft Report on grid event Complete Outage of 220kV Exora SS, 220kV Vikas Tech and 220kV Bus-1 Outage at 220kV Malur SS of KPTCL in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 10-06-2026 17:26

# Event Summary (घटना का सारांश):

# 220kV Malur SS was operating with split bus condition with 220kV Hoody Malur line feeding 220kV Malur Bus-1. 220kV/66kV Exora and 220kV/66kV Vikas Tech Park were being radially fed from 220kV Malur Bus-1. As per the reports submitted, the triggering incident was Y-G fault in 220kV Hoody Malur line and the line tripped. Tripping of this line led to loss of power supply to 220kV Malur Bus-1 which in turn led to complete outage of 220kV Exora SS and 220kV Vikas Tech Park.

- Time and Date of the Event (घटना का समय और दिनांक:  29-05-2026 17:35

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): KARNATAKA

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Karnataka State Demand (MW) | 12433 | 12244 |
| Karnataka State Generation (MW) | 7473 | 7483 |
| Grid Frequency (Hz) | 50.33 | 50.31 |
| SR Demand (MW) | 55988 | 55584 |
| SR Generation (MW) | 49263 | 49121 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Cloudy , Windy |

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 0.0 MW | 143.0 MW |

- Duration of interruption (रुकावट की अवधि):  0 hours, 40 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 220KV-HOODY-MALUR-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

220kV Malur SS was operating with split bus condition with 220kV Hoody Malur line feeding 220kV Malur Bus-1. 220kV/66kV Exora and 220kV/66kV Vikas Tech Park were being radially fed from 220kV Malur Bus-1 as shown below.

As per the reports submitted, the triggering incident was Y-G fault in 220kV Hoody Malur line. At both ends, the fault was sensed in Z1 and since AR is disabled 3ph tripped. Tripping of this line led to loss of power supply to 220kV Malur Bus-1 which in turn led to complete outage of 220kV Exora SS and 220kV Vikas Tech Park.

- DR Analysis:

VIKAS_TECH_PARK - 220KV

|  | VIKAS_TECH_PARK - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | Supply Failure. No DR triggered |

EXORA - 220KV

|  | EXORA - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | Supply Failure. No DR triggered |

MALUR - 220KV

|  | MALUR - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | Supply Failure. No DR triggered |

220KV-HOODY-MALUR-1

|  | HOODY - 220KV | MALUR - 220KV |
| --- | --- | --- |
| Time Sync Issue | Yes | Yes |
| DR Analysis | DR Trigger Time:29-05-2026 17:35:22.231 Z1, DIST Trip B, Z2, DIST Sig. Send 13_86_OPTD DIST. Chan Recv Ir (max): 0.98 kA Iy (max): 8.95 kA Ib (max): 0.40 kA Vr (max): 125.54 kV Vy (max): 126.71 kV Vb (max): 126.76 kV DR Trigger Time:29-05-2026 17:35:22.232 PH_SEL_ST_FW, PH_SEL_ST_ND Z1_OPTD, M2_YPH_OPTD, ZONE_2_START, DIST_ST_ND, M2_CAR_SEND 86_OPTD CAR_REC1/2 ZCOM_OPTD Ir (max): 0.97 kA Iy (max): 8.78 kA Ib (max): 0.39 kA Vr (max): 125.86 kV Vy (max): 126.93 kV Vb (max): 126.80 kV | DR Trigger Time:29-05-2026 17:33:17.846 Any Trip, DIST Trip B, Any Trip C, Z1, Z2, Z3, 10.CARR SEND-2 8.86 A/B OPTD, 8.86 A/B OPTD 6.CR REC 1/2 Ir (max): 0.98 kA Iy (max): 0.85 kA Ib (max): 0.39 kA Vr (max): 131.26 kV Vy (max): 125.36 kV Vb (max): 132.08 kV |

- A) PMU Analysis:

From PMU, dip in Y-G fault is observed indicating Y-G fault during the event with no delayed fault clearance.

B) SCADA Analysis:

From the SCADA data, tripping of the 220KV-HOODY-MALUR-1 line can be observed

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| KPTCL | 1. Tapping of EXORA and VIKAS_TECH_PARK at 220kV level needs review |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):  Nil

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

29/05/2026 18:15

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | KPTCL |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | KPTCL |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 | KPTCL |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: