# Draft Report on grid event Complete Outage of 220kV KANKAPURA, HAROHALLI, KIADB-HAROHALLI of KPTCL in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 15-06-2026 10:44

# Event Summary (घटना का सारांश):

# In the antecedent conditions, 220kV KANKAPURA-TK HALLI was under idle charged condition and hence 220kV KANKAPURA, HAROHALLI, KIADB-HAROHALLI were radially connected through 220KV-HAROHALLI-SOMANAHALLI-1. The triggering incident is the R-G fault in 220KV-HAROHALLI-SOMANAHALLI-1 line and the line tripped. Tripping of the only line connected led to the Complete Outage of 220kV KANKAPURA, HAROHALLI, KIADB-HAROHALLI of KPTCL

- Time and Date of the Event (घटना का समय और दिनांक:  31-05-2026 19:47

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): KARNATAKA

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Karnataka State Demand (MW) | 10126 | 10154 |
| Karnataka State Generation (MW) | 6759 | 6853 |
| Grid Frequency (Hz) | 49.91 | 49.95 |
| SR Demand (MW) | 49828 | 49877 |
| SR Generation (MW) | 43312 | 43421 |

*Pre and post data of 1 minute before and after the event

| Elements under outage | - 220KV-KANKAPURA-TK_HALLI-1 |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Thunders |

Bus Configuration at Somanahally 220KV Substation and elements under tripped condition in Prefault condition are as follows:

220kV Bus A:

Section 1 : 500MVA ICT-1,Tataguni and Harohalli lines

Section 2: Lines Mylasandra-1,Mylasandra-2,Keonics city, Khodays, 500MVA ICT 2 & 3, Bus Sectionaliser was in closed condition.

220kV Bus B:

Lines Bidadi-1,Bidadi-2, Malur (idle charged ) line and local load of Somanahally, Bus Sectionaliser was in closed condition.

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 0.0 MW | 92.0 MW |

- Duration of interruption (रुकावट की अवधि):  0 hours, 20 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 220KV-HAROHALLI-SOMANAHALLI-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

In the antecedent conditions, 220kV KANKAPURA-TK HALLI was under idle charged condition and hence 220kV KANKAPURA, HAROHALLI, KIADB-HAROHALLI were radially connected through 220KV-HAROHALLI-SOMANAHALLI-1.

At Somanahalli Bus configuration is shown as above. As per the reports submitted, the triggering incident was R-G fault at 220 kV Somanahalli - Harohalli line. At Somanahalli end, the fault was sensed in Z2 without receiving carrier aided trip signal due to fault not being detected at remote end and Z2 time tripped after around 430ms. During the same time the Bus-1 bus sectionaliser also tripped on EF protection (pick up 320A, TMS 0.15) as per FIR. Due to the Tripping of the only line resulted in complete outage of 220kV Harohalli, KIDAB-Harohalli and Kankapura of KPTCL.

- DR Analysis:

KIADB-HAROHALLI - 220KV

|  | KIADB-HAROHALLI - 220KV | KIADB-HAROHALLI - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | No DR uploaded. | No DR uploaded. |

KANKAPURA - 220KV

|  | KANKAPURA - 220KV | KANKAPURA - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | No DR uploaded. | No DR uploaded. |

220KV-HAROHALLI-SOMANAHALLI-1

|  | HAROHALLI - 220KV | SOMANAHALLI - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | No DR uploaded. | DR Trigger Time:31-05-2026 19:47:34.194 Relay Startup A_Phase Trip, B_Phase Trip, C_Phase Trip, 3_Phase Trip, PSB, Zone2 OPTD DI CBF C_PH DI_A/R Block, DI CBF B_PH CB Open B_Phase, CB Open C_Phase CB Open A_Phase |

HAROHALLI - 220KV

|  | HAROHALLI - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | No DR uploaded. |

- A) PMU Analysis:

From the PMU plot, R-G fault is observed during the event with delayed fau;t cleranace of around 400ms

B) SCADA Analysis:

From the SCADA data, reduction in ICT flow in Somanahalli ICTs can be observed

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| KPTCL | 1. Delayed fault clearance during the fault in 220KV-HAROHALLI-SOMANAHALLI-1 needs review 2. Tripping of BS at SOMANAHALLI during the fault in 220KV-HAROHALLI-SOMANAHALLI-1 needs review |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| KPTCL | Line inspection carried out by TLM Kanakapura, No fault found, as per the request of TLM JE Kanakapura line was test charged at 220kV Somanahalli at 20:07 Hrs. Line Immediately tripped on SOTF at 220kV Somanahalli. Load of 220kV BWSSB Harohalli was changed over to 220kV Station TK Halli at 20:08 Hrs, and 220kV KIADB Harohalli load was changed over to 220 kV Kanakapura station at 20:09 Hrs. |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

Load restored to Kanakapura, Harohalli and KIADB Harohalli at 20:09 hrs by charging 220kV TK Halli-Kanakapura line.

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | KPTCL |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | KPTCL |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) | KPTCL |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: